## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP - Watermain PVC |  |  |  |  | Yes | ITP - Watermain PVC | 32e6b2e5-b60f-4e12-88ad-ddd4a32c832c
checkpoint-group |  |  | section | 1. Pre-construction (P&G / Establishment)
checkpoint-status |  |  | checkpoint | 1.1 - Extent of Line Setout
label | 2188c8af-1b0e-5f69-b95b-5375efd86476 |  | note | Acceptance / Conformance Criteria - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Watermain drawings Identify any clashes before construction.
label | 52de05b7-2523-5da6-8f80-d5d818ab628f |  | note | Standard / Specification - Design Drawings
label | e61c2fd1-b475-5e0b-9891-8eb078397d5c |  | note | Verifying Document - ITP Sign Off
label | 4c435d60-892e-549b-ad93-35365a7448d1 |  | note | Frequency - Prior to Construction & Every Revision of IFC Drgs / Data
label | 1b47d63b-488e-5cb4-9561-a648677e6e11 |  | note | Activity - M
label | 74725284-9d13-53b3-adb8-e716dfb7ab4f |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.2 - Environmental Protection
label | 2daa111b-fb92-56cb-95f0-a0893bb7d5a7 |  | note | Acceptance / Conformance Criteria - Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events
label | 90e89d68-cdce-5951-807d-af0f8df8df9d |  | note | Standard / Specification - Project ESCP Plans
label | 0c7e2196-45e7-501f-b491-48fbc3679d4b |  | note | Verifying Document - ITP Sign Off
label | 183c9709-e340-589b-8e50-25dde0b61fe6 |  | note | Frequency - Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events
label | 58063758-ff8f-5ae4-8b2f-6df8e28b5bd3 |  | note | Activity - M
label | cb9fe534-57a2-5c13-bc53-f991d52f3827 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.3 - Stakeholder
label | 9989e892-ba99-5f46-94d1-2ad757eaa13b |  | note | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners
label | 7d849347-4c2f-51c4-9572-a3141cde43c8 |  | note | Standard / Specification - Project Stakeholder Management Plan
label | 92486058-ca48-5a73-8b08-5850dfbedada |  | note | Verifying Document - ITP Sign Off
label | e0d10c68-8f54-592b-ae3e-ce2b6314547a |  | note | Frequency - Prior to Construction with continue updates throughout the works
label | 86e0b0bb-7529-57e6-9e4e-984c639ef986 |  | note | Activity - M
label | f0b731bf-77b1-5b67-9e5f-a719015147f2 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.4 - Permits
label | 6dc1956a-3aec-55c3-ba28-fa3b08efcdc1 |  | note | Acceptance / Conformance Criteria - Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip. Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. All known services must be clearly marked on site and briefed to the workforce .
label | 37f81dcf-5bd4-55f4-acf6-85e9f7454b47 |  | note | Standard / Specification - Section 2.2.10 Project Specification
label | 858dc8ce-814c-557c-8854-687c8c26c1a9 |  | note | Verifying Document - Ground Disturbance Permit DN-ZH-FM043.1
label | 484256f6-9cf4-5e56-bc22-cd9ce8cca84f |  | note | Frequency - Prior to Construction Reviewed and Reissued weekly or when site conditions change
label | 8f71f728-3673-5fbe-9e40-0033bce41387 |  | note | Activity - H
label | c9df6b3c-5476-5a0f-a223-54b76ae6401d |  | note | By - PE
checkpoint-group |  |  | section | 2. Material, Personnel & third party approval
checkpoint-status |  |  | checkpoint | 2.1 - Pipes & Fittings
label | cb6bd198-cb74-5f66-a3a6-58ecf46e544e |  | note | Acceptance / Conformance Criteria - Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes/fittings are correct and in good condition and compliant.
label | 25841545-1c58-586f-9e80-ecf24d1107b7 |  | note | Verifying Document - Delivery Dockets
label | 0b67eb3e-77fd-5648-bc0e-f15359c84a7b |  | note | Frequency - Each Delivery to Site
label | 436ec73b-2a28-5f66-a0d0-4cacba4928ce |  | note | Activity - S
label | e86680e5-61d2-5449-9f68-97554420befe |  | note | By - PE
checkpoint-status |  |  | checkpoint | 2.2 - Bedding/Overlay
label | ac3ee39b-6f57-5478-a442-c7b907d45e1b |  | note | Acceptance / Conformance Criteria - Confirm material grading and density of pit sand or other approved material
label | 5d3234bd-54fe-55b6-b03b-87c35187af3b |  | note | Verifying Document - IANZ Lab Test Reports
label | 61ba510d-a74b-5af1-ad03-82e66121b21c |  | note | Frequency - 1 Test per 1000m3
label | f97c4424-e8b9-5ca9-a68e-bbbec2432e03 |  | note | Activity - H
label | 8057e399-7390-53b4-a075-ad6c78bb59fb |  | note | By - PE
checkpoint-status |  |  | checkpoint | 2.3 - Backfill Material Compliance
label | 0fd748e4-0fb9-504a-adf6-f623c6b4d7af |  | note | Acceptance / Conformance Criteria - Confirm material grading and density of pit sand or other approved material Use selected native soils in berm
label | 8fa15a36-e044-5740-a8a2-9311781670ef |  | note | Verifying Document - IANZ Lab Test Reports
label | 77be99f0-dc14-540f-91ce-14cf9920a5d0 |  | note | Frequency - 1 Test per 1000m3
label | c80191a8-c3bd-5a2a-bc63-9e54b7a980cc |  | note | Activity - H
label | a8b7c56f-354d-5900-86a1-235d2be3eda1 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 2.4 - Undercut Backfill Material
label | 3cb47e54-1418-5622-ab41-d615c9382364 |  | note | Acceptance / Conformance Criteria - Engineer to Specify Material to meet specifications dependant on material selected
label | 675eb2f7-2d4e-5dd8-9a6a-44367de039b6 |  | note | Verifying Document - IANZ Lab Test Reports
label | 5c0e5624-6b46-5f4e-8374-970dee1428ec |  | note | Frequency - 1 Test per 1000m3
label | 6cfa0a74-20c1-5572-80f3-2efc11be00d6 |  | note | Activity - HP
label | c075b68e-f3e8-556b-a880-b2e139659d80 |  | note | By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Geotextile/Geogrid
label | 92069664-6ed8-5673-8056-9568d2bfba26 |  | note | Acceptance / Conformance Criteria - NZTA F/07 Strength Class C & Filter Class 1 geotextile is to be used in the undercut. Geotextile or Geogrid that is used in the undercut is to be documented / marked up on drawing
label | c0adf8e0-1d1f-5027-ac8a-bae157691020 |  | note | Standard / Specification - Project Specification
label | 1217c2d7-7332-559c-b7f7-4a23ae4e0757 |  | note | Verifying Document - Certification Photos of Delivery Dockets
label | 8ae1e8ac-9cc7-5151-a8b3-88d75e34bda1 |  | note | Frequency - Material Used
label | 08f4eefd-17ae-566f-9c7a-c4931b9dc2b4 |  | note | Activity - C
label | 305ec3b4-fd80-5ba6-9290-213684fa245d |  | note | By - PE
checkpoint-status |  |  | checkpoint | 2.6 - Warning Tape
label | f1e47766-a3f3-5215-a1ce-135f9e9dbb47 |  | note | Acceptance / Conformance Criteria - Obtain Warning Tape from supplier
label | b71ee51d-495e-5b89-b505-abbfb185ea0b |  | note | Verifying Document - Delivery Dockets
label | 90b99526-3ed0-5be3-9aea-1e794c893eae |  | note | Frequency - Each Delivery to Site
label | c663b7c0-cb53-5627-ad7d-f5d83742f76e |  | note | Activity - S
label | 1121b458-64ce-5dca-b110-8108945ceb30 |  | note | By - PE
checkpoint-group |  |  | section | 3. Construction Activity
checkpoint-status |  |  | checkpoint | 3.1 - Trench Excavation
label | f12678f6-c0fd-5ed9-9d41-7545f383290c |  | note | Acceptance / Conformance Criteria - Excavate trench to design height, placing spoil in approved area and benching as required Visual Inspection to any hard stones or rocks to be removed Any archaeological finds to be reported Inspections to any formation of soft spots
label | b510b474-29a2-5d0c-81a5-9a5212a8460f |  | note | Standard / Specification - Project Specification 4.3
label | 4b59d9da-33f7-53d4-8f30-f408e131b057 |  | note | Verifying Document - Scala test result
label | cda8a064-9dfd-5a8c-8458-f1134750ce46 |  | note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
label | 78a2c85b-1eaa-5acb-bf9f-a76a82062ae1 |  | note | Activity - H
label | 46695756-bbb6-58f9-8696-bed72f90f8fd |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.2 - Foundation Compliance
label | 276d0ce0-dfa4-5bd5-a550-9580a3b5dd3e |  | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
label | cf10a023-8a94-5086-b4a7-7c0d119805d7 |  | note | Standard / Specification - Project Specification 4.3
label | f2dc0382-c218-52d7-8977-e280dd16c5b1 |  | note | Verifying Document - Scala test result
label | d4810fc8-9e04-5194-9ec3-fc30e1853e85 |  | note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
label | 06a8366a-dfc5-5baa-9e15-0b508bbbed80 |  | note | Activity - H
label | 26295be7-846f-5ad0-9afa-1dd19a084b78 |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.3 - Undercut Backfill Compliance
label | 34324fc7-d773-54db-8aeb-fc5b1c2f454a |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD
label | a38999ed-4542-576e-9f74-959326a18952 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | baf96eeb-3529-5ca7-b763-cf0dfe756ffc |  | note | Verifying Document - IANZ Lab Test Report
label | 1a703f4d-039c-5d00-ac58-61d47565037c |  | note | Frequency - Based on Undercut Section
label | 02dcf23e-0ddf-5af9-9f2f-489a85c3bd0f |  | note | Activity - H
label | 96a5d9f8-dd74-57ae-b8fd-a669eca0bac1 |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.4 - Bedding Compaction Testing
label | 08a3cf70-2b4a-517e-9869-336e34e1f911 |  | note | Acceptance / Conformance Criteria - HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD
label | cbf448d3-5bf3-5c35-be34-24363e0e426b |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | c18f590f-57f1-5d88-b849-183772593ece |  | note | Verifying Document - IANZ Lab Test Report
label | 05c60a7a-bba7-500d-bb44-44a474905a1f |  | note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
label | d3c46b89-d758-5e27-b802-1ad98e98ab2b |  | note | Activity - H
label | 1798524e-a004-51ef-af4b-104ac3f8c2da |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.5 - Overlay Compaction Testing Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed.
label | bfbf2e9a-fbc9-5fd0-973b-8095fcfb763b |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD
label | 969fa821-e653-5c9f-8897-7ec7ae2f0083 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007
label | 028a07b5-3f8a-52e8-8de4-6fba06ab734f |  | note | Verifying Document - IANZ Lab Test Report
label | 437a0105-39f6-512b-b69b-44bd64fab130 |  | note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
label | 9260299f-8ef5-52bc-bd37-83f49bdb4e74 |  | note | Activity - H
label | a5e58f80-6f41-59e1-af0d-001fe6c370e9 |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.6 - Backfill Inspection
label | 990919b2-90bb-5bf4-bc57-bdc954877ec6 |  | note | Acceptance / Conformance Criteria - Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the pipeline.
label | 106a340e-9051-54e1-89a9-15bf607d4d77 |  | note | Standard / Specification - Project Specification 4.3
label | 7ed35f7c-4b27-5ebd-8390-370abfc9f814 |  | note | Verifying Document - Photographs
label | 6b2fe735-3696-533d-bab8-16980d8f1304 |  | note | Frequency - Continuous
label | 2e70d804-bb9d-5d4f-9903-b55ab30e5653 |  | note | Activity - S
label | da1687ab-91ab-58e9-91b6-1b6e97041a12 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.7 - Install Warning Tape
label | 89ad8ee1-db8e-53c5-b079-f92974f40951 |  | note | Acceptance / Conformance Criteria - For open trenching, detector tape shall be placed approximately 200mm below final ground level and metallic ‘detector’ tape coloured blue, stipulating ‘Danger – Water Main Below’ (or similar) shall be laid.
label | d0d4470d-e0c0-5649-9097-5dea6fc91f18 |  | note | Standard / Specification - RITS
label | 21b7fcef-c235-5990-a6fd-f5e7757bfb27 |  | note | Verifying Document - Photographs
label | 30ab73b0-3683-507d-ac37-9477ae9dc08e |  | note | Frequency - Continuous
label | 1927f6e7-bf71-5f57-b600-bc4d095c4728 |  | note | Activity - S
label | ec5e7354-bd30-5124-93d6-dd96acb2018c |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.8 - Survey
label | a5d031ac-99e2-5ea8-bc94-c509b478106f |  | note | Acceptance / Conformance Criteria - All Water Mains shall be laid in a straight line or following street layout. The deviation from approved design alignment permitted either in plan or elevation shall be: Open Cut – ± 50mm on straight and 100mm in curves All pipes, fitting and thrust blocks to be as built prior to backfilling
label | 681466f1-4732-5e3b-b0ea-286d982015e0 |  | note | Standard / Specification - Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm
label | 2c0c5481-84e6-5bff-8007-7a844c38bedf |  | note | Verifying Document - Survey Data
label | 66759fe9-2a36-5335-a22c-25c4b5dd3229 |  | note | Frequency - Continuous
label | 9ba33e89-78d1-5cef-9805-8f994815413b |  | note | Activity - C
label | 69778e5c-9b81-5ce5-8d17-dd4ed98cc005 |  | note | By - SV
checkpoint-status |  |  | checkpoint | 3.9 - Backfill Compaction Testing
label | c788c146-bfb9-5a96-b95c-3518e3b3e9f7 |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
label | 931f3c70-962d-5967-b81f-1b19a97e7bf3 |  | note | Standard / Specification - RITS
label | c9458d99-170d-53ae-8103-b196f1f0fa35 |  | note | Verifying Document - IANZ Lab Test Report
label | e9547088-f957-51a1-8c0e-ee8a1f0b6997 |  | note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
label | 298dad17-495a-52c9-be43-f3bbe3b937ed |  | note | Activity - H
label | c9717a72-4c7f-5c9d-a696-26defe658e28 |  | note | By - QE
checkpoint-status |  |  | checkpoint | 3.1 - Pressure Testing
label | 5d69a420-1957-5b1c-9290-3c51d88e388b |  | note | Acceptance / Conformance Criteria - At least one working day advance notice shall be given to council for pressure testing of pipelines. All pipelines shall be pressure tested and backfilled after anchor blocks, specials and fittings are completed, but with joints and connections visible. The final tests are to be witnessed by Council prior to the pipe being connected to the ‘live’ network. No further connections will be permitted after this stage. Refer to NZS 4404 Appendix C3 for the requirements or if this not available, the pipe manufacturer’s procedure.
label | 5b2454ea-1cc6-594d-a88e-513232a2193d |  | note | Standard / Specification - 6.3.10 RITS
label | 6e90bbf9-09d4-54e5-b7e6-9a44629abfc2 |  | note | Verifying Document - Visual Inspection & Report
label | f2c3c247-ebb0-5874-a6dc-294338df015c |  | note | Frequency - Completion of Works
label | 5bde098e-eb81-5021-b0e8-32eedf795680 |  | note | Activity - S
label | 6b55841c-7a86-5f6e-a16d-f8ba94e5ce4c |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.11 - Disinfection & Flushing
label | a04ef4c3-e232-5cb6-bf4a-b48be7c1cbb3 |  | note | Acceptance / Conformance Criteria - Appendix D of NZS 4404 – Water Supply Disinfection Specification shall apply Discharge of Testing or Chlorinated Water from pipelines may require a resource consent from the regional council
label | 72e62171-3897-5595-bacf-de1ed94ce84e |  | note | Standard / Specification - 6.3.11 RITS
label | 1a077abb-5e7e-54ee-b677-bc5d79b10d96 |  | note | Verifying Document - Visual Inspection & Report
label | 012e07a0-eb0d-5930-b43a-b7ed3ebb79d4 |  | note | Frequency - Completion of Works
label | 480678f5-c94c-5bce-9be6-d7378074e353 |  | note | Activity - S
label | 80577bfd-b617-5499-b284-b5dae1307d01 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.12 - Bacteriological Test
label | ecf71ef6-9afe-54ef-b387-99bad42254b0 |  | note | Acceptance / Conformance Criteria - In commissioning new pipelines, Council shall be given 24 hours’ notice as to when sampling for bacteriological tests is to be carried out. Water in the pipeline shall be sampled between 12 hours and 48 hours after postchlorination flushing and the samples tested for the presence of E.coli, Coliforms and Heterotrophic Plate Count by a Ministry of Health Approved laboratory with IANZ accreditation for this type of test. The number of samples shall be at least one for projects involving less than 100m of pipe, two for projects up to 200m length, etc. “A satisfactory result is s <1 MPN/100ml for E.coli and Total Coliforms and less than 20 CFU/ml for Heterotrophic Plate Counts.” If E.coli is detected the pipeline shall be swabbed, flushed, disinfected, flushed again and then the bacteriological tests repeated. The process shall be repeated until such time a clear test is recorded. Note: There are high risks of test failure due to sample contamination so it is recommended that the testing laboratory is also involved in collecting the sample.
label | 8458ae3b-7797-5a0a-814d-f2e6b72268ae |  | note | Standard / Specification - 6.3.11.2 RITS
label | e3bb0c54-bcd9-5b91-92e8-cb2da86ad9a5 |  | note | Verifying Document - Visual Inspection & Report
label | 1c926b7a-e073-5363-94e9-287f94a4c5f7 |  | note | Frequency - Completion of Works
label | 1cb5f6b7-91a6-5b74-b072-c914ba3092a9 |  | note | Activity - S
label | 6a48d096-0034-56d8-868a-c78b608d8349 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.13 - Reinstatement
label | 8ec17bcc-d926-596a-8ec1-55e292b11670 |  | note | Acceptance / Conformance Criteria - Quality Check on New Works
label | 12c240a7-5851-5a10-a894-dfc1f21a71de |  | note | Standard / Specification - Reinstate and Tie into existing surrounds
label | 26665455-42e7-5cf8-af92-81a44a978efc |  | note | Verifying Document - Photographs
label | cf7cef0f-8302-5fa6-8771-1d4718d773d3 |  | note | Frequency - Continuous
label | 6b0fbabb-ce6a-568c-be52-0fa22a06b6a6 |  | note | Activity - S
label | 606b0568-359a-5ac7-a423-5451cf87de4f |  | note | By - PE
checkpoint-group |  |  | section | 4. Post-construction (Final Inspection & Handover)
checkpoint-status |  |  | checkpoint | 4.01.01 - Survey As-Builts
label | 970a77da-11d9-53d6-a1c1-82d62e20424c |  | note | Acceptance / Conformance Criteria - Quality Check on New Works based on the tolerances in RITS
label | 989fa426-033b-5cca-bab8-65ba09ef6e49 |  | note | Standard / Specification - Project Specification
label | f78817de-6c2e-573e-ac02-c1c19369129d |  | note | Verifying Document - Survey Data As Built Drawings Photographs
label | 8c5281e5-f67d-50b7-b542-966288db2b75 |  | note | Frequency - Post Works Completion
label | 45c3f513-76b5-5f0e-a367-64bc9aaa06ad |  | note | Activity - H
label | 5dc829e6-c403-5afa-9d2f-41b4948b6ec6 |  | note | By - SV
checklist-sectioned |  |  | checklist | ITP - Stormwater |  |  |  |  | Yes | ITP - Stormwater | 5bc76927-2573-4c4a-9088-318a8fd2547a
checkpoint-group |  |  | section | 1. Pre-construction (P&G / EStablishment
checkpoint-status |  |  | checkpoint | 1.1 - Extent of Line Setout
label | 447440a5-2c0a-5624-85c7-5c5695b6237d |  | note | Acceptance / Conformance Criteria - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Stormwater drawings Identify any clashes before construction.
label | c2a79509-fed9-5e36-b6c2-55161fc3b698 |  | note | Standard / Specification - Design Drawings
label | ca3ef045-41f3-51eb-926d-2360a7098b93 |  | note | Verifying Document - ITP Sign Off
label | 98ad0bfb-34bb-5a09-9755-5781e4c3ebe3 |  | note | Frequency - Prior to Construction & Every Revision of IFC Drgs / Data
label | 9f6fba78-f4fa-5da9-aba5-069ad45174ef |  | note | Activity - M
label | 8de4d596-b054-5659-bc84-16e38ba8fb5f |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.2 - Environmental Protection
label | 6612df47-d954-53c4-b894-edb8ce9af6f9 |  | note | Acceptance / Conformance Criteria - Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events
label | 062afe7b-306f-5969-b9db-f7d2dc2afc15 |  | note | Standard / Specification - Project ESCP Plans
label | 7a2cc52d-ca2a-57de-905e-1840593283b1 |  | note | Verifying Document - ITP Sign Off
label | b38eb8cb-5d9d-5cd6-aae7-aace11a0a128 |  | note | Frequency - Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events
label | de4a0ce0-290c-5f62-9d8d-6caf8dc1f487 |  | note | Activity - M
label | 052d5bf8-5a20-5976-ac01-5a2ef8b5e4f3 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.3 - Stakeholder
label | 964041ce-8f47-5f43-9ecb-4bc963a55457 |  | note | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners
label | 8b5fbeb7-f07a-5d9a-8009-c74944313641 |  | note | Standard / Specification - Project Stakeholder Management Plan
label | eb2ede20-7062-5ae6-ae42-6281a683f1fd |  | note | Verifying Document - ITP Sign Off
label | d15bcff4-95f0-5150-accf-6527317b301c |  | note | Frequency - Prior to Construction with continue updates throughout the works
label | 5ec3de2c-4b7c-5ade-a197-bd5ea77fcabe |  | note | Activity - M
label | 4c067108-806e-5e92-9370-1ad1b8a35d89 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 1.4 - Permits
label | 4c825895-8c78-55b8-b08e-a8351d233bd8 |  | note | Acceptance / Conformance Criteria - Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip. Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. All known services must be clearly marked on site and briefed to the workforce .
label | 1d27dde7-938b-501b-832f-694ad3898bab |  | note | Standard / Specification - Section 2.2.10 Project Specification
label | ebcd1d8c-89e5-5cf8-892d-b66059936aa9 |  | note | Verifying Document - Ground Disturbance Permit DN-ZH-FM043.1
label | e8bbb9a1-2854-5867-a418-82b8a8d75d70 |  | note | Frequency - Prior to Construction Reviewed and Reissued weekly or when site conditions change
label | 50b252e4-9a1b-55a1-8fcd-272b57170589 |  | note | Activity - H
label | 05b3ff20-3c01-57de-94a8-610a07e19afa |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2. Material, Personnel & third party approval
checkpoint-status |  |  | checkpoint | 2.1 - Pipes, Fittings and Pre-cast Structures
label | 8cc73743-a549-5b8a-9972-bd0ed83002b2 |  | note | Acceptance / Conformance Criteria - Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes/manholes/catchpits are correct and in good condition and compliant.
label | 99c3e5ae-e54f-5495-9913-be9258ec6a39 |  | note | Verifying Document - Delivery Dockets
label | c00daa9a-8446-5e5a-80c6-f2424b52f9d1 |  | note | Frequency - Each Delivery to site
label | a6e87c58-81fd-59d2-a37c-c5b5ea4ddfbd |  | note | Activity - S
label | 34dca5cd-53ed-5e78-9eca-2b4049551dea |  | note | By - PE
checkpoint-status |  |  | checkpoint | 2.2 - Bedding/Side & Haunch/Overlay/Backfill Material Compliance
label | 2f2b959f-0b91-593e-af76-befcf5d8037b |  | note | Acceptance / Conformance Criteria - Confirm material grading and density
label | df46ccd2-8662-5f7d-b6ba-bec7f384f640 |  | note | Verifying Document - IANZ Lab Test Report
label | 9c4db143-fb28-5f31-bc3c-43f6c7034508 |  | note | Frequency - 1 Test per 1000m3
label | 245aee90-a07b-5d58-8087-a5a14ee20ed3 |  | note | Activity - H
label | f3b05688-3c15-54c6-8fba-318cf71f63e7 |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Undercut Backfill Material
label | fe88c77f-3e70-515d-bb22-3fd140cb3a92 |  | note | Acceptance / Conformance Criteria - Engineer to Specify Material to meet specifications dependant on material selected
label | 07567e87-88a2-541c-b30e-632f15b06a13 |  | note | Verifying Document - IANZ Lab Test Report
label | 54e4e4a8-5298-504a-a852-f33bcd7d4d87 |  | note | Frequency - 1 Test per 1000m3
label | 8c66e4e0-bc8f-506b-a85f-f5d65b949fb1 |  | note | Activity - HP
label | 3d96e459-1e65-5754-b945-41afc0373867 |  | note | By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Geotextile/Geogrid
label | d07e6c50-2ff7-59c3-8fea-34e730e14a76 |  | note | Acceptance / Conformance Criteria - NZTA F/07 Strength Class C & Filter Class 1 geotextile is to be used in the undercut. Geotextile or Geogrid that is used in the undercut is to be documented / marked up on drawing
label | 6dbbe61e-6416-5303-b213-94a8c466f688 |  | note | Standard / Specification - Project Specification
label | e0bf4fe2-31b6-5f29-9c4a-9c35585633c8 |  | note | Verifying Document - Certification
label | 9db1ab35-a02a-50b0-a859-3077e8340c2f |  | note | Frequency - Material Used
label | 14c378a1-3d7d-5e88-b0b4-dc90aa22f05a |  | note | Activity - C
label | 3fd12297-a538-5970-b61b-2ca319e65cd8 |  | note | By - PE
checkpoint-group |  |  | section | 3.1 SW Pipeline Construction
checkpoint-status |  |  | checkpoint | 3.1.1 - Foundation Compliance
label | 7a04d12b-d747-5ffd-b944-2bd05ad77fc9 |  | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
label | 4f0e99a5-bfaf-5f02-a719-5a24a42d5913 |  | note | Standard / Specification - Project Specification 4.3
label | a9f17d3b-c88e-50fe-8d6f-ab8064428d69 |  | note | Verifying Document - IANZ Scala test result
label | f3841af3-80ba-5c41-8777-03f1b887719b |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | 3575732c-7133-5f5c-849a-1c506255b232 |  | note | Activity - H
label | ff25d653-974a-54e0-a0d3-32abec523435 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.2 - Undercut Backfill Compliance
label | e1ff91fe-c3fb-58ee-9e70-19bef3c46199 |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD
label | a64090ac-0958-5091-b76f-c28c35eb76a9 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | 93d8490e-c5e1-5da8-888e-c2e3ae4d55d2 |  | note | Verifying Document - IANZ Lab Test Report
label | 8b1bde27-f241-50c2-a50d-193151536635 |  | note | Frequency - Based on Undercut Section
label | 021146ef-473d-5414-88e2-ce3b10842f12 |  | note | Activity - H
label | 905f63e2-3f0e-5d40-8280-5163a1b608af |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.3 - Bedding Compaction Testing
label | e3797ba1-d525-5fd9-a978-8a5831163f09 |  | note | Acceptance / Conformance Criteria - HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD
label | a2064d5a-38c8-55fd-a7dc-82c5a0133fc2 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | 1d9d16c0-cfa7-5e49-8d48-39ef0a0d8c21 |  | note | Verifying Document - IANZ Lab Test Report
label | 499bcee3-0521-5833-b992-397bfa037601 |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | 730ed117-3d39-5268-949a-02db9efa951e |  | note | Activity - H
label | 82f85a51-88c4-5669-8e7c-07d8953148f8 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.4 - Haunch Zone Compaction Testing Haunch Zone shall extend from top of bedding to 0.3 times the outside dia of pipe
label | 943c75a0-548a-5877-b083-6d8b113d77be |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD
label | 98d9189b-0f93-5541-86a3-f57e2e828180 |  | note | Standard / Specification - HS2 backfill Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007
label | b6029590-f98f-5925-9315-855030e5fe08 |  | note | Verifying Document - IANZ Lab Test Report
label | db6a89fc-c15b-5eaf-9b4e-48577b15dbce |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | aa4f8012-e8f7-54c9-a4ac-7df2a309121b |  | note | Activity - H
label | c1462d73-a82d-5e15-9b73-6b6f3fd47075 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.5 - Side Zone Compaction Testing Side Zone shall extend from top of Haunch Zone to 0.5 times the outside dia of pipe
label | c71bafd6-9b9a-586e-a9c4-1a21adf96b38 |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD
label | 24f21671-d0d3-5a9e-bc01-b6a76b22570d |  | note | Standard / Specification - HS2 backfill Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007
label | 13b55999-794e-5122-af3b-a8aa97997815 |  | note | Verifying Document - IANZ Lab Test Report
label | 32feea1a-ae98-558d-9737-dbd1f32fab48 |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | 4a48af67-2ab9-5de9-9c40-82b43aee0a97 |  | note | Activity - H
label | fd47be6f-6c6a-5ff9-94b2-800c521a7759 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.6 - Overlay Compaction Testing Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed.
label | 05192b11-1a31-586d-905f-5659d3cebd1e |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD
label | 50b2983f-227f-536d-b0eb-3584ee19e873 |  | note | Standard / Specification - HS2 backfill Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007
label | 8a3c30b9-73dc-5a8a-838b-86b5b0bd2ed5 |  | note | Verifying Document - IANZ Lab Test Report
label | 3d025453-8849-5aed-8278-b85d2c7e3df9 |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | bea3a1ac-8116-579e-9399-b859af1663b6 |  | note | Activity - H
label | b5599516-b1eb-5110-99be-fa5c76828b21 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.1.7 - Backfill Inspection
label | 1adaab6a-26da-5cfd-b3e6-23db6fc87b44 |  | note | Acceptance / Conformance Criteria - Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the pipeline.
label | 3084c2a0-39cc-51ad-a0a2-094544a82dc1 |  | note | Standard / Specification - Project Specification 4.3
label | 57109279-457b-5e21-a601-66ebf67dfde3 |  | note | Verifying Document - Photographs
label | 191df840-3870-5720-a4de-26fffe4f3f34 |  | note | Frequency - Continuous
label | 8feee862-4ff9-5b2c-96aa-b341303a3086 |  | note | Activity - S
label | 398a1038-926f-5031-b65a-f2b2a115b4ea |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.1.8 - Survey
label | 74d6bc52-ea28-5f9e-a46e-d8a11a8a62aa |  | note | Acceptance / Conformance Criteria - Invert Levels The permissible deviation from the designated level of the invert at each manhole or structure shall be ± 50mm, provided that the fall between successive manholes or structures shall be at least 90% of that specified. Horizontal Alignment The permissible deviation of the horizontal alignment between manholes or structures shall be ± 100mm. Gradient For straight gradients, the permissible deviation from the specified gradient shall be ± 50mm from a straight line drawn between the inverts of successive manholes, provided that no point in the pipeline is lower than any downstream point.
label | 377dd711-8851-5fde-899f-26d3b19d6e49 |  | note | Standard / Specification - Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm
label | 779ac31a-8be8-5b43-a12a-7ce6784654ce |  | note | Verifying Document - Survey Data
label | 0758b277-e14d-5292-8882-bfddd9492976 |  | note | Frequency - Continuous
label | 666f3657-a9b9-5643-8c00-9d8c5e540590 |  | note | Activity - C
label | 7c5f006f-2bf8-54b5-bf65-9f6706fc2204 |  | note | By - SV
checkpoint-status |  |  | checkpoint | 3.1.9 - Backfill Compaction Testing
label | dd1b4c81-03ce-519d-86b6-a52d4bb8409b |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
label | 5a0adf60-74ff-5fe6-b4d0-bd4064d2a01e |  | note | Standard / Specification - Project Specification 4.3
label | 57b31059-a1ef-5138-ac81-a2c861002c3d |  | note | Verifying Document - IANZ Lab Test Report
label | 2ca7f613-162c-5ee2-83fc-db1a58a8a44f |  | note | Frequency - 0-5m: 2 Tests 5m-10m: 3 Tests 10m-40m: 4 Tests 40m-100m: 5 Tests 100m: 1 test per 20m
label | 3ca2a53a-d16f-538d-8f33-c2e7d8481abf |  | note | Activity - H
label | ba3f57e7-fa79-5100-999c-4e83448459c4 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.2 SW Manhole Construction
checkpoint-status |  |  | checkpoint | 3.2.1 - Foundation Compliance
label | dcec4b76-a35a-5a06-9a8d-29d8238c9847 |  | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
label | 00c8b96c-19a5-5475-912e-4316d41e6e37 |  | note | Standard / Specification - Project Specification 4.3
label | 7d677d75-abd9-53e8-b241-5dcf600e67ef |  | note | Verifying Document - IANZ Scala test result
label | 5d063390-2611-5165-8299-86528408eea5 |  | note | Frequency - 1 Test/Manhole
label | dbd0670e-e320-5db0-84a5-dd06c660d2bf |  | note | Activity - H
label | bd3b026b-9a06-55d4-bdb5-132aa5be49ca |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2.2 - Undercut Backfill Compliance
label | 39adc7b4-7c09-5d68-b4de-2afda2fef248 |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD
label | 2e017776-83f1-57c1-b446-0ea74d0331e5 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | 97f1d62b-680b-5711-ba4b-7f5b0f2b1450 |  | note | Verifying Document - IANZ Lab Test Report
label | b82b0243-c431-5bf6-bef2-54f9e9604ed4 |  | note | Frequency - 1 Test/Manhole if Undercut required
label | db6d6ab5-d974-5cc2-b57c-e9036d4fe47f |  | note | Activity - H
label | 51b8047d-5ab9-52d7-b996-5a03129f824d |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2.3 - Bedding Compaction Testing
label | 2ae700cd-cdff-561f-9c54-c990abd4899e |  | note | Acceptance / Conformance Criteria - HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD
label | 8eb8191a-61be-5741-99e3-a38fa32a2bd4 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | 15e97f48-55d1-5511-b25c-c3910dd31d24 |  | note | Verifying Document - IANZ Lab Test Report
label | 6596043b-5c4a-581d-b4bd-86665c83b1dd |  | note | Frequency - 1 Test/Manhole
label | 003075f7-e290-5eb6-a26a-9457ff57961c |  | note | Activity - H
label | 75d1fa86-4533-5a8f-b029-aec3817e6ed7 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2.4 - Backfill Inspection
label | 80e98b3b-70ee-589d-99a7-8585136c48f5 |  | note | Acceptance / Conformance Criteria - Inspection of manhole prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the manhole
label | c72fb28c-e022-5303-a650-9e008cf50310 |  | note | Standard / Specification - Project Specification 4.3
label | 87c71e3f-7a35-5568-bb19-d8524210f6d0 |  | note | Verifying Document - Photographs
label | 6e2b4e89-bad4-5a42-96c2-1a70cf38076d |  | note | Frequency - Continuous
label | c5f29725-7a10-5c82-a80d-e13fc08c62b8 |  | note | Activity - S
label | 5ea80f2a-4b35-53da-a64f-0b12bc74d1c2 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.2.5 - Survey
label | 6b93d645-4ecf-56be-a7fa-df9892ec778e |  | note | Acceptance / Conformance Criteria - Invert Levels The permissible deviation from the designated level of the invert at each manhole or structure shall be ± 50mm, provided that the fall between successive manholes or structures shall be at least 90% of that specified. Horizontal Alignment The permissible deviation of the horizontal alignment between manholes or structures shall be ± 100mm. Gradient For straight gradients, the permissible deviation from the specified gradient shall be ± 50mm from a straight line drawn between the inverts of successive manholes, provided that no point in the pipeline is lower than any downstream point.
label | 1ac3f541-1f81-5dc6-8556-14d6f56de1d6 |  | note | Standard / Specification - Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm
label | 2ef1a085-438f-59d5-b3fd-50ead3ef546b |  | note | Verifying Document - Survey Data
label | 235d4e1e-4ebb-569d-b7c5-6ef33aa85739 |  | note | Frequency - Continuous
label | 5483ddd0-7ac7-592a-bc95-d7f40b712b95 |  | note | Activity - C
label | caf7d5bb-97cc-5104-9b91-f1fdf092b1af |  | note | By - SV
checkpoint-status |  |  | checkpoint | 3.2.6 - Backfill Compaction Testing
label | 318dea9e-f21a-516d-998f-cefd11329da4 |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
label | 3fcf6580-7b80-5d37-8434-4a4bf5773b2f |  | note | Standard / Specification - Project Specification 4.3
label | 41973aa3-f55c-5b99-af6c-3e7072fe92c3 |  | note | Verifying Document - IANZ Lab Test Report
label | 085388e7-2c92-5ba2-a83e-694ebd60d6ab |  | note | Frequency - 4 Density test per layer at Quarter Points around the Structure
label | c006baea-7876-523a-b03d-5b741204d653 |  | note | Activity - H
label | 6e4a94cc-536c-56b9-9988-83741cadbbc5 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2.7 - Haunching
label | 5659e5ec-fb84-5ec0-9f8c-a5b25af378c7 |  | note | Acceptance / Conformance Criteria - All the MH's needs to be haunched as per the specifications
label | 40a23dd4-539d-586c-b1b7-6b350a9581dc |  | note | Standard / Specification - RITS
label | d9a6375d-0eef-528f-9a15-48556a44142e |  | note | Verifying Document - Photographs
label | 2799a095-3978-5051-aa95-4d0db01a222c |  | note | Frequency - Continuous
label | 6f9a12d4-fd19-5973-8db6-606ab7a73450 |  | note | Activity - S
label | 08a70049-a942-524f-91d4-b28a82d75d02 |  | note | By - PE
checkpoint-group |  |  | section | 3.3 SW Catchpit Construction
checkpoint-status |  |  | checkpoint | 3.3.1 - Foundation Compliance
label | b5bcd2e4-2d17-56bd-a5db-81d297579443 |  | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
label | 6bbdf8da-2c8e-5d2b-b460-d0096881e4c4 |  | note | Standard / Specification - Project Specification 4.3
label | 18d529ea-89eb-59fb-97f7-391b734c33f8 |  | note | Verifying Document - IANZ Scala test result
label | 87595e9e-bb05-5747-87d5-a4ed3ece4f65 |  | note | Frequency - 1 Test/Catchpit
label | e726b3b3-be6d-5a7c-a618-aa07aebbec81 |  | note | Activity - H
label | bd723658-bc76-5c1f-bc44-f3eca7d562d1 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3.2 - Undercut Backfill Compliance
label | 80cc47a7-b6e1-5136-81bd-f07069b91b8e |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD
label | c4c34550-803d-55f4-838d-e8392fdf9fd2 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | b7643824-0758-5387-ac1b-54ba81825658 |  | note | Verifying Document - IANZ Lab Test Report
label | f9947440-9d2b-53b7-832d-0d9d1f819fbb |  | note | Frequency - 1 Test/Catchpit if Undercut required
label | 11bfade2-10e4-5df8-a782-7f7e1df7d556 |  | note | Activity - H
label | ad79f347-8d68-53d4-8203-fd74f1958ad5 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3.3 - Bedding Compaction Testing
label | 648a2b95-dd00-54ea-ac31-e22564f82a91 |  | note | Acceptance / Conformance Criteria - HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD
label | 5646338b-6181-5b18-b998-28102fa4c4b3 |  | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
label | 60218604-2f09-54fd-9073-ae1aaed2a405 |  | note | Verifying Document - IANZ Lab Test Report
label | e7c00a95-6aa8-5929-87fa-96e4a3c4dde4 |  | note | Frequency - 1 Test/Catchpit
label | f0a01638-4414-5fa4-a096-f22a36e03247 |  | note | Activity - H
label | d558e9a6-05a1-54d6-9592-b7fe56f33911 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3.4 - Backfill Inspection
label | c467db57-ff4b-5807-8eee-15fae2cf0df7 |  | note | Acceptance / Conformance Criteria - Inspection of catchpit prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the catchpit
label | ffb11fbc-3b83-5abd-913a-240698c4df57 |  | note | Standard / Specification - Project Specification 4.3
label | 32b11a35-8a77-5aaa-bdb1-d7cf228e6aaf |  | note | Verifying Document - Photographs
label | b6eafff6-bdea-547a-8a04-1cb3793877d3 |  | note | Frequency - Continuous
label | a1f137a5-0c59-59e3-b70b-62dc170cc355 |  | note | Activity - S
label | c9cef0a2-1b0e-535b-8f99-d8e4d17c3ecd |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.3.5 - Survey
label | 7197b535-45c2-5809-829e-ebe391e834c7 |  | note | Acceptance / Conformance Criteria - Invert Levels The permissible deviation from the designated level of the invert at each manhole or structure shall be ± 50mm, provided that the fall between successive manholes or structures shall be at least 90% of that specified. Horizontal Alignment The permissible deviation of the horizontal alignment between manholes or structures shall be ± 100mm. Gradient For straight gradients, the permissible deviation from the specified gradient shall be ± 50mm from a straight line drawn between the inverts of successive manholes, provided that no point in the pipeline is lower than any downstream point.
label | a1ee0ca8-a47b-5917-bd54-f5214297b86b |  | note | Standard / Specification - Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm
label | 76fa5315-b0f5-58e3-acfe-56024a1d6ac4 |  | note | Verifying Document - Survey Data
label | e150227c-5e94-5830-b10d-ea0b898175bf |  | note | Frequency - Continuous
label | 5d550601-8749-5225-a5ab-5b74c1aa57c8 |  | note | Activity - C
label | 16a0960f-ef12-5ca6-ba4b-afc4551b968b |  | note | By - SV
checkpoint-status |  |  | checkpoint | 3.3.6 - Backfill Compaction Testing
label | eb686d29-26c4-5f20-adc9-e52220561e9e |  | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
label | 3e46d6be-d908-593c-b47a-2cdd80cb0094 |  | note | Standard / Specification - Project Specification 4.3
label | b1763e05-12f1-56b7-8fe0-96265442db5b |  | note | Verifying Document - IANZ Lab Test Report
label | 5bcd4b69-2adf-5059-bc82-158e8c321dbf |  | note | Frequency - 4 Density test per layer at Quarter Points around the Structure
label | a5f5cba0-c703-577a-af89-de2bad6a32ee |  | note | Activity - H
label | ebbf3c75-97de-50a0-b256-7d083ae04ea3 |  | note | By - QE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.4 Riprap & Boulders Installation
checkpoint-status |  |  | checkpoint | 3.4.1 - Rip-Rap Material
label | b321cd8c-5e46-5864-aba5-f794ff7ad43c |  | note | Acceptance / Conformance Criteria - The material shall comprise imported screened quarry blasting's and/or crushed basalt, greywacke or other angular hard rock which shall conform to Density, Crushing Resistance , Weathering Classification, Abrasion Resistance, Calcite intrusions, Grading, Shape. No rock riprap or boulders shall be placed until the Contractor has provided test results to prove compliance with the requirements and obtained approval of the Engineer.
label | b68f6a88-b769-531b-b43d-ea229b1af715 |  | note | Standard / Specification - Project Specification 4.7.1
label | 710b49eb-0085-53e1-9708-0c05bc07c290 |  | note | Verifying Document - IANZ Lab Report
label | 509fd158-cd61-5f76-9574-a828fce7ffd9 |  | note | Frequency - Prior to placement
label | c4be62b1-dd9b-5431-9751-6efbea20f7f2 |  | note | Activity - HP
label | 08dd237a-e262-5a54-9704-4d1aafdb9aa1 |  | note | By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4.2 - Soil Rip-Rap Material
label | ae586004-69f3-51f9-a2ab-3fb9c500fb06 |  | note | Acceptance / Conformance Criteria - Where soil riprap is specified on the Drawings, approved riprap rock shall be pre-mixed with topsoil from on site at a ratio of 70% riprap to 30% soil by volume.
label | 4585a3e6-61dc-5271-b76a-4db994ee98c2 |  | note | Standard / Specification - Project Specification 4.7.4
label | 5afcc23e-4686-5030-adc5-8cf217b29856 |  | note | Verifying Document - Dockets/Site Notes
label | 1b6e59a7-08e6-5461-b23a-b005331f1c91 |  | note | Frequency - Each Batch
label | 4f1355f3-bfa8-5d3e-95e0-b69bb3f6889a |  | note | Activity - R
label | e0e2ab75-0816-5f19-955a-022b76b98747 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.4.3 - Void Filling Rip-Rap Material
label | 0fb9879d-1dc8-5b88-8be9-e9d76f5bee87 |  | note | Acceptance / Conformance Criteria - Where void-filled riprap is specified on the Drawings, the riprap rock shall be premixed with well graded granular material with a maximum particle size of 40mm (GAP 40) at a ratio of 70% riprap to 30% GAP 40 by volume.
label | 4cd86cc3-8c69-5de8-943f-2ea0f7b3290f |  | note | Standard / Specification - Project Specification 4.7.5
label | 72cb2c30-925b-5688-bcae-53c504748bb8 |  | note | Verifying Document - Dockets/Site Notes
label | 2c5fc2af-b150-58a3-871e-7fda26bfac99 |  | note | Frequency - Each Batch
label | 55719c40-e0df-5036-a089-ee1c0d9c9da6 |  | note | Activity - R
label | 0dc87d3c-994a-52bd-bcde-99f769a51b07 |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.4.4 - Grouted Boulder
label | 5d119a4a-7190-56ea-a138-60a8225dc9f2 |  | note | Acceptance / Conformance Criteria - Boulders must be approved by the Engineer, prior to placement Grout used for grouted boulder structures shall meet the requirements of NZS 3109
label | e49b26c5-3d8c-535e-a12c-c23ce98772d4 |  | note | Standard / Specification - Project Specification 4.7.6
label | 79b8a383-a5a9-5a06-969f-f6aba483cb0e |  | note | Verifying Document - Site Records Data Sheet
label | b03711ab-ad6c-5f3b-b345-55a98e6258f5 |  | note | Frequency - Prior to placement
label | 1b8ab041-d166-5770-a6f6-2e79d7c9116c |  | note | Activity - HP
label | 5191a328-e62a-5de8-9966-507dbde63370 |  | note | By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4.5 - Achieving Required Depths
label | 953e1403-bb20-5da8-8128-631b97ed3482 |  | note | Acceptance / Conformance Criteria - As per IFC Drawings
label | 830943ec-076f-5cb7-bc84-87871c978dea |  | note | Standard / Specification - Project Specification
label | 4c48f30e-2955-567f-a1dd-288e00897eac |  | note | Verifying Document - Photos showing thickness/depth Each Section Labelled
label | 969c046d-ac38-5cd9-9eb3-4264be2d77bf |  | note | Frequency - After Placement
label | b22883ca-794f-5d96-a004-b5aa14482988 |  | note | Activity - H
label | dc639aaa-e29a-5d1e-a35b-050828c37bdb |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.5 CCTV & Reinstatement
checkpoint-status |  |  | checkpoint | 3.5.1 - CCTV Inspection
label | f0fab8de-949c-5ebc-a248-d79779f581c8 |  | note | Acceptance / Conformance Criteria - Quality Check on New Works
label | 18687b5c-cc85-5a1b-b730-2eb46416a2ca |  | note | Standard / Specification - Project Specification 4.4 NZ Pipe Inspection Manual
label | 63f2aecc-85a2-59a9-9b6d-adc6a21fed50 |  | note | Verifying Document - CCTV Report
label | 69d35b40-75fe-5dd2-b466-ea0d100bbaa8 |  | note | Frequency - 1 per line
label | 66432b17-ac2c-5cfd-967e-78fc98c03e74 |  | note | Activity - S
label | 488fadbe-90bf-5b0d-8b6b-8eb71925a20a |  | note | By - PE
checkpoint-status |  |  | checkpoint | 3.5.2 - Reinstatement
label | a312f052-372d-50f9-9883-57a8dbe105e1 |  | note | Acceptance / Conformance Criteria - Quality Check on New Works/All the MH Lids and Cespit Levels should align with the pavement specification in terms of level & alignment
label | 7be67543-bfaa-5a20-997e-ed431314971f |  | note | Standard / Specification - Reinstate and Tie into existing surrounds
label | d1cee765-ff68-569f-93cc-97c4f195f95c |  | note | Verifying Document - Photographs & Level Checks
label | 4d5922ad-a59f-5136-9229-4b0ba6edc19b |  | note | Frequency - Continuous
label | a287eccd-79c8-502e-9bf6-c7365abc4ed2 |  | note | Activity - S
label | 63711978-92e4-5993-a92f-a80b22d2f3bd |  | note | By - PE
checkpoint-group |  |  | section | 4. Post-construction (Final Inspection & Handover)
checkpoint-status |  |  | checkpoint | 4.1 - Survey As-Builts
label | 53857957-862a-5c02-affb-420f8bbcb2d4 |  | note | Acceptance / Conformance Criteria - Quality Check on New Works based on the tolerances in RITS
label | 0a6e7516-d189-58bf-b63f-ed3019cfa3f0 |  | note | Standard / Specification - Project Specification
label | 97975fe6-bf31-533e-aa46-c1eb07ef0da3 |  | note | Verifying Document - Survey Data As Built Drawings Photographs Red-Pen As Built
label | 64440248-836a-5ff7-84fb-19292f75fdaf |  | note | Frequency - Post works completion
label | eca96e49-ee5e-5cc0-966e-5e8083612ee8 |  | note | Activity - H
label | f0c23b4c-fd20-5916-b85f-437a97b969e5 |  | note | By - SV
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | ITP - Pavement SIL |  |  |  |  | Yes | ITP - Pavement SIL | c16731ae-3527-42b0-9337-2cc6a8485ecc
checkpoint-group |  |  | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 3.01 Site Requirements
checkpoint-status |  |  | checkpoint | 3.01.01 - Construction Pack
label | 4b26e7cb-ace0-58bb-a616-39483fc6b83d |  | note | Acceptance / Conformance Criteria - Construction Pack including a Methodology and JESA to be assembled , uploaded and transmitted on InEight before works commence
label | 39bdd60b-5a55-5725-9d44-67dc819f7e82 |  | note | Standard / Specification - Downer
label | f37b21b6-fe75-518e-99e7-441bb2e54568 |  | note | Verifying Document - Construction Pack
label | e20b4b8a-d1f3-5800-add6-1b620896d23b |  | note | Frequency - Prior to Works
label | 2c256560-e7aa-55c9-98a1-86938a36f071 |  | note | Verification Activity - H
label | 5aa00b7c-8cab-5b58-9c8a-a8ebcd4457f9 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.01.02 - Survey Setout
label | e3e94e95-7461-5602-8ae5-1f475a9a9372 |  | note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
label | a9ccfcea-23ab-5f83-98aa-01aa55f14f09 |  | note | Standard / Specification - Downer
label | bd924ba3-e98a-5a37-88f8-deb39c1915c3 |  | note | Verifying Document - Survey Records
label | 21d5543a-b500-5bb2-b23b-7150daaf8fee |  | note | Frequency - Prior to Works
label | 8155419d-e2cb-5987-8b90-4a5df3da5317 |  | note | Verification Activity - H
label | 651d4ceb-5a87-5cee-aa2f-1d5af93f48ca |  | note | Verification Activity By - SV
checkpoint-status |  |  | checkpoint | 3.01.03 - Service Location
label | beea7a1c-046b-5fb7-91cd-46b86eb7ecfd |  | note | Acceptance / Conformance Criteria - Complete the Excavation permit process to identify, locate and protect all services.
label | 8c0340ae-3f3f-57df-8af6-8836db439d12 |  | note | Standard / Specification - Downer
label | eaababd1-32a0-5323-ad8b-8e999dafd51d |  | note | Verifying Document - Excavation Permit
label | 558c19e0-5e33-5b6a-a931-c34e81e92a2c |  | note | Frequency - Prior to Excavation
label | 85387089-5afd-5a2b-974f-78eb26637df0 |  | note | Verification Activity - H
label | 33484b60-704b-5d44-8ca8-0d2f7803fb57 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 3.01.04 - Internal Permits
label | 24c5b6b2-98a4-589a-a0ad-fa73c558e90d |  | note | Acceptance / Conformance Criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
label | f1ead7c5-425d-5829-b8d1-0edd0ebada26 |  | note | Standard / Specification - Downer
label | 7bc080ae-d60d-55ed-9e48-c9efb7f6d7ce |  | note | Verifying Document - Internal Permits
label | f051067e-abc8-58c0-96b0-6932e794b31d |  | note | Frequency - Prior to activity being undertaken
label | 518ffaca-a960-5750-b6b8-c85a4e56025c |  | note | Verification Activity - H
label | cfe1cce4-c9a2-53b0-9062-99d2666b7ccb |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 3.01.05 - External Permits
label | b2e25bb1-ceae-59ce-be7a-ac0fa86efbac |  | note | Acceptance / Conformance Criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
label | 26281c77-fff7-5dd4-88f3-7e33e61e9cbf |  | note | Standard / Specification - Downer
label | fb232d0f-a63d-56c9-8cef-c489fe97494c |  | note | Verifying Document - External Permits
label | 9e657bb1-bd49-5ffa-98e1-3b2ad9d187b6 |  | note | Frequency - Prior to commencment of activity
label | 8037d5ba-0dd4-5d90-9102-4cba9dadd771 |  | note | Verification Activity - H
label | 62198747-f56f-5a64-8a05-cde299bdfa49 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.01.06 - Approved Construction Drawings
label | bb46b8a2-0124-5764-b4dd-7bdf0e69e95c |  | note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
label | f9faecd7-6ccf-5952-87fc-e7dc6b36747a |  | note | Standard / Specification - Downer
label | 030bf603-8060-5f9d-9f7a-d5e4d6516677 |  | note | Verifying Document - IFC Drawings
label | 73c5b094-94c7-5167-9ef9-037fd27c4209 |  | note | Frequency - Prior to works start
label | cefe589e-775b-5225-b22e-07aa1e40a577 |  | note | Verification Activity - H
label | 434a1998-8714-52c5-bd16-87cddbd9fb72 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.01.07 - Previous Layer QA Sign Off
label | 6983331f-cd49-553d-9d1b-2fb72a289629 |  | note | Acceptance / Conformance Criteria - All Previous layers signed off, QA complete. Including subgrade, SW, WW, WM. Ensuring everything up to the bottom of SIL is compliant.
label | 915f2668-b583-53ab-a791-7764dde86a86 |  | note | Standard / Specification - Downer
label | 77414674-0ef9-565c-bd1e-9e79630527df |  | note | Verifying Document - QA Records
label | f3a3f4b4-c411-555b-86c7-ecf46bcdf601 |  | note | Frequency - Prior to works start
label | c6466e5e-b003-544d-bb6f-6a7c079699e2 |  | note | Verification Activity - H
label | e1d16e4b-df18-54d6-933a-5129d5ba5833 |  | note | Verification Activity By - PE
checkpoint-group |  |  | section | SECTION 4 – ENGINEERS HOLD POINTS - 4.01 Engineer Nominated Hold Points (Engineer’s inspections)
checkpoint-status |  |  | checkpoint | 4.01.01 - SIL Inspection
label | 589c641a-aa63-5852-9ee0-74bb69e89f17 |  | note | Acceptance / Conformance Criteria - Prior to placing of sub-base pavement, to include proof roll, inspection of extents of works, general shape, and tidiness, free of organic or contaminated material, review of Benkelman Beaming of the SIL and final levels.
label | 63d5d160-5d5e-5d1c-8f98-de84fd1bffb8 |  | note | Standard / Specification - PS - 2.2.16
label | c3cb4613-e4f5-5cfc-b1af-22f8b68c2820 |  | note | Verifying Document - Hold Point Release
label | c154df35-5954-5684-b09e-81eb77940267 |  | note | Frequency - Min 48h Notice
label | af005a20-54f3-5277-886e-7af9e988939a |  | note | Verification Activity - HP
label | 18fb0707-f3d9-5d50-af1f-10287369254f |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.01.02 - Subgrade Inspection
label | ccdd5453-ce4a-5556-99a1-e628c9df66ef |  | note | Acceptance / Conformance Criteria - Proof roll, Scalar penetrometers, and shear vanes prior to SIL fill commencing
label | 4bc1e182-7aa8-55c3-b605-7ac285d42607 |  | note | Standard / Specification - PS - 2.2.16
label | d3d56a58-b3ff-5de8-80eb-b959f7028b02 |  | note | Verifying Document - Hold Point Release
label | daf11b30-c8b1-541a-9e0a-1f48878bd249 |  | note | Frequency - Min 48h Notice
label | 3f765b21-ec87-5fc9-b2c0-516f6ba42d38 |  | note | Verification Activity - HP
label | 54909fee-8367-537a-913e-c78a0b548259 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | SECTION 5 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - PAVEMENT AND SURFACING - 5.01 Subgrade Materials
checkpoint-status |  |  | checkpoint | 5.01.01 - Pavement Subgrade CBR
label | b3e03a0d-8900-51ac-be82-923b82921d09 |  | note | Acceptance / Conformance Criteria - The pavement design requires a soaked CBR of not less than 10 within 1.0m of the bottom of the SIL layer and 4x DCP's to a depth of 1m below subgrade level in a 1m grid around the in-situ CBR test location and 4x NDM's DT with a probe depth of 300mm in a grid around the in-situ CBR location. CBR testing of the subgrade shall be carried out by the Contractor prior to final trimming. If the soaked CBR is less than 10 the Engineer may instruct changes to the pavement design. (Push tube for Cut and Filed sample for Fill). Invitation for engineer to witness CBR testing. To be accurate representation of site
label | 8bc2d425-ceb7-5734-bb77-d28559cf4dd1 |  | note | Standard / Specification - PS 7.1
label | 7a8b0934-9135-54fb-b2a4-e6b80a154256 |  | note | Verifying Document - IANZ Lab Reports
label | 1086e7dd-eabe-514b-87d6-33b88e67f9b1 |  | note | Frequency - One test per 2,000m2, with a minimum of three tests per material type.
label | d8f0f437-a191-57db-ab63-ab5fa84405d2 |  | note | Verification Activity - HP
label | 07eb9ac4-2f53-5c6b-9ec0-d3b5327d7a95 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.02 - SIL (Clean Pit Sand)
checkpoint-status |  |  | checkpoint | 5.02.01 - SIL Conformance
label | 7b7cbf9c-e8ee-5e03-b9c4-19e9defd7ac5 |  | note | Acceptance / Conformance Criteria - The SIL shall be pit sand meeting the following requirements: · 4-day soaked CBR (NZS 4402:1986 Test 6.1.1): Shall be ≥ 30. · Organic Matter: It shall be free of organic matter. · PSD (NZS 4407:2015 Test 3.8.1): Shall be <7% passing the 75μm sieve.
label | ab9dc707-18c8-576e-aaac-433561430047 |  | note | Standard / Specification - PS - 7.2.1
label | 68faef9d-392a-59d7-bcaf-6fa1bc1f1e4f |  | note | Verifying Document - Lab Reports
label | c4fedb90-397f-5d70-8393-ddd5f80bc3ef |  | note | Frequency - CBR and PSD testing shall be completed at the rate of 1 test per 2,500m3, and being no less than 1 test every 3,000m2 (placed).
label | 2aa170d9-fa30-5034-aee7-9c13a2cf0362 |  | note | Verification Activity - HP
label | ff1df35a-76b1-5238-93f8-cfc823b7b0f1 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.02.02 - SIL Maximum Dry Density & Optimum Moisture Content
label | a27e8fb3-c719-5968-a595-666a016a330e |  | note | Acceptance / Conformance Criteria - The SIL shall be sampled and tested by an IANZ Accredited laboratory for Maximum Dry Density & Optimum Moisture Content
label | 9401944b-e210-541c-9a33-a939c9d05c3e |  | note | Standard / Specification - PS - 7.2.1
label | 008a0244-1f95-5a7a-9e8d-80305a50d1ed |  | note | Verifying Document - Lab Reports
label | 05358614-5f37-5794-981b-b6ef430b82c7 |  | note | Frequency - 1 test per material type and no less than 1 test every 5,000m³ (in place)
label | 0e569234-ac64-532c-a6a1-d7a30e8d6b76 |  | note | Verification Activity - HP
label | 73f1f2dc-3ee4-55d4-a027-2e6d2c716e44 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.02.03 - Plateau Density Test
label | 4d47d092-b781-5579-afbe-d0a041d3ac9d |  | note | Acceptance / Conformance Criteria - Compaction shall be undertaken using the higher of the two density targets. Plateau tests to be spread out evenly to be an accurate representation on what is coming into site.
label | 3646b1f1-33f8-54ed-978d-3519e10c9441 |  | note | Verifying Document - IANZ Lab Reports
label | 292f8656-46b5-5e25-9d81-b6c1be49f298 |  | note | Frequency - 5 tests per 10,000m2
label | cf700307-c8b6-5b85-8348-1951da8bab5f |  | note | Verification Activity - C
label | c2e994f8-60dc-5a5e-808d-82e1602f55ad |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 5.02.04 - NDM
label | a65fdecb-7522-5aef-8f72-c9c72775f831 |  | note | Acceptance / Conformance Criteria - Mean Value ≥ 98, and Minimum Value ≥ 95. All NDM testing shall be undertaken via Direct Transmission method at 300mm probe depth.
label | 737f32a6-ca14-58fd-aea3-8aff714c61e6 |  | note | Standard / Specification - PS - 7.3.1
label | e55891f8-d0de-516a-b9c8-54ad6ca789e9 |  | note | Verifying Document - IANZ Lab Reports
label | df80991c-456f-5a22-94b9-66aea17bf2ea |  | note | Frequency - 5 tests per layer per 1,000m2
label | ddeea918-5e1e-53c5-bdb0-567b4a7edd31 |  | note | Verification Activity - C
label | fa4e54ea-eb3c-5011-b31b-85f88f881e0f |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 5.02.05 - Benkelman Beam
label | f1e57e77-c46f-5c32-a4b7-5c36a4a04f61 |  | note | Acceptance / Conformance Criteria - Target Benkleman Beam deflections on the top of the SIL layer are 1.6mm (90th percentile) and a maximum of 1.8mm
label | 4f236964-6a78-58bb-a2ad-29ca204c836c |  | note | Standard / Specification - PS - 7.3.1
label | 9af0f383-b583-5491-8e2a-112b9bbfe9b3 |  | note | Verifying Document - IANZ Lab Reports
label | f7a61f4b-00fa-5389-858d-3782c067994b |  | note | Frequency - every 10m of each lane – staggered between left and right wheel path.
label | 70f2fcc9-b04d-51bc-a428-0e43ad15a03b |  | note | Verification Activity - C
label | e7ad119b-d74a-5d5c-b2d6-3a42d6de70a8 |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 5.02.06 - Organic Material
label | b3e67920-8037-5400-8c1c-642e5ee8991f |  | note | Acceptance / Conformance Criteria - Ongoing visual and physical inspection for any roots/organic material, photos of clean sand, and any organic material removed.
label | a0c385bf-bf9c-5c1c-ac4e-583139a2d735 |  | note | Standard / Specification - PS - 7.3.2
label | 936b6251-f4a7-5a3b-bf3c-24cba6f93080 |  | note | Verifying Document - Site Records, photos of clean sand, and any organic material removed
label | db82440f-7ec5-5382-8705-2ae2bae059b1 |  | note | Verification Activity - I
label | b5079f59-52f0-5920-ac35-007512183c86 |  | note | Verification Activity By - ENG
checkpoint-group |  |  | section | SECTION 6 – CONSTRUCTION ACTIVITY – PAVEMENT AND SURFACING - 6.01 Construction
checkpoint-status |  |  | checkpoint | 6.01.01 - Subgrade Prep
label | 3314eb0a-8401-58d3-a782-af26e847ee14 |  | note | Acceptance / Conformance Criteria - The subgrade shall be prepared in accordance with the requirements of the Geotechnical Works Specification in Appendix B, including proof rolling, Scala penetrometer and NDM testing at the specified frequencies.
label | 4832cdc2-16f0-54fb-b9f5-b13fd4db465b |  | note | Standard / Specification - PS 7.1 GWW
label | 4d5bf8ee-a1ae-53dc-83a1-b890969d9705 |  | note | Verifying Document - Completed Earthworks ITP
label | 81025f5f-e79f-5ae5-98f3-223c68ae7b80 |  | note | Frequency - Prior to Pavement Works
label | 08eae87e-fbb1-52e4-abc1-c936b9f15f93 |  | note | Verification Activity - HP
label | 531c5d6a-0940-5478-b658-d32ba101608b |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 6.02 SIL (Clean Pit Sand)
checkpoint-status |  |  | checkpoint | 6.02.01 - SIL Scala Testing
label | dcff1fcc-0468-5c64-97ec-07f5bb15626e |  | note | Acceptance / Conformance Criteria - In addition, the SIL (tested in accordance with PS Clause 7.4 below) shall achieve a Scala penetrometer blow count no less than 10 blows/100mm. Depth to be 1.5m from top of SIL.
label | 4163e9ea-e5a1-5798-9f16-4efc158777b9 |  | note | Standard / Specification - PS - 7.3.1
label | e34d2610-b9ae-5077-ba99-de1bc7d627bb |  | note | Verifying Document - Scala Results
label | 9faf4a1c-754c-5fea-ade0-407e75652614 |  | note | Frequency - 1 test per 200m2
label | 894e4cdf-7c9d-5780-a212-8b8d34c34071 |  | note | Verification Activity - I
label | 7f61f95f-4eb2-5bcd-b43f-2b57f7050d3c |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 6.02.02 - Layer thickness
label | 3f529307-5392-5a66-acbb-081265d82c69 |  | note | Acceptance / Conformance Criteria - Each layer shall be checked to ensure the required layer thickness is achieved of Maximum
label | 0fa5048b-d270-5ea1-9593-a35fc1bbadaa |  | note | Standard / Specification - PS - Table 7.2 - 2.2 NZTA B/2
label | f5c571b2-b56a-5c59-8c5f-481204083b8b |  | note | Verifying Document - As-built data
label | 5c79b190-c473-5a2d-9a81-4b6cf4384c9d |  | note | Frequency - 1 test per 20m
label | 940c333f-fade-574e-82a7-6ece487ed079 |  | note | Verification Activity - I
label | da0419c8-3af1-55d4-a644-463ad1be3e53 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.02.03 - Plateau Density Test
label | 20cea371-9a84-570b-8d74-aa280094c8ab |  | note | Acceptance / Conformance Criteria - The plateau density tests shall be undertaken at a rate of 5 tests per 10,000m2 using a variety of compaction plant typical of that to be used on site. Testing shall be at OWC. Plateau tests to be spread out evenly to be an accurate representation on what is coming into site.
label | 0aa05dd5-ffc9-504e-9a7c-60990433443a |  | note | Standard / Specification - PS - Table 7.2 - 2.2
label | 51fc55fa-f4bd-5d31-af32-b4186c256bfb |  | note | Verifying Document - Plateau Density Report
label | 0118de71-b76e-5cdf-8df4-d9032daf63dd |  | note | Frequency - 5 tests per 10,000m2
label | 24168a1d-4d75-5639-b2fc-a4cbf8e189ca |  | note | Verification Activity - I
label | d016790e-e344-529a-93dd-38a52669b805 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 6.02.04 - Sand SIL layer compaction
label | dfb1d2fa-07ef-574d-824b-bdc7ebddb7a7 |  | note | Acceptance / Conformance Criteria - Further to Figure 2 of NZTA B/2, the acceptance criteria for compaction of the sand SIL layer shall be a Mean Value ≥ 98, and Minimum Value ≥ 95.
label | 80e7f2c7-ef44-58a0-a547-4edbf52dec16 |  | note | Standard / Specification - PS - 7.3.1
label | 72f78430-a5d7-5df8-88f4-eb2aab833a7f |  | note | Verifying Document - IANZ NDMS
label | 09a46328-eb63-5bf7-b4b2-789d16cf2ce4 |  | note | Frequency - 5 tests per layer per 1,000m2 (Min per lot)
label | aac1ee29-8af1-503f-a4ab-7102ea90cd06 |  | note | Verification Activity - I
label | b6d28b73-0c57-5903-886a-50e7c7b030f5 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 6.02.05 - Proof roll
label | 07b326c3-ea68-549d-9128-c3000d49c9de |  | note | Acceptance / Conformance Criteria - The SIL shall be tested via Proof roll prior to Benkelman Beam testing. Proof roll to be under supervision of engineer and verifying document to be signed off by engineer.
label | f5e9d4dc-40e8-58cf-a4aa-b27c60255de8 |  | note | Standard / Specification - PS - Table 7.2 - 2.2
label | 564d8205-b741-54d5-b073-d48e5d67d9c6 |  | note | Verifying Document - Site Notes
label | 75ed5345-a8b0-52aa-bbc1-534c1cbcdb82 |  | note | Frequency - 1 test per 20m
label | e7f0260f-c6f5-50d7-84e5-50a351b4280e |  | note | Verification Activity - HP
label | 61899164-dfe5-5bc3-b907-b5b068e82afd |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.02.06 - SIL Benkelman Beam test
label | 1474a3bc-5812-5d34-93c3-2a76dbcbc6d8 |  | note | Acceptance / Conformance Criteria - Benkelman Beam test results shall be carried out on the top of the SIL layer at the rate specified in PS Clause 7.4 and reported to the Engineer. Target Benkleman Beam deflections on the top of the SIL layer are 1.6mm (90th percentile) and a maximum of 1.8mm. Performance verification of these target deflections shall be confirmed by the Engineer on review of results from within the pavement Stabilisation trial (PS Clause 7.3.3).
label | 04c2be5d-e694-5630-ae8f-3cd00f7c3b8f |  | note | Standard / Specification - PS - 7.3.1 PS - 2.2.16
label | b519543d-4049-5ba0-bd30-397138d05564 |  | note | Verifying Document - Benkelman Beam Report
label | 2acdff5b-4e24-5f1d-87a6-475ceff0ac5b |  | note | Frequency - every 10m of each lane – staggered between left and right wheel path. Min 48h Notice
label | e4b7f0ea-806f-538d-9a07-d162c6b4f901 |  | note | Verification Activity - HP
label | 62e03724-57d9-548c-9937-de3062eaf727 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.02.07 - SIL Inspection
label | add1780d-3465-530b-bd7c-6b3040e3182b |  | note | Acceptance / Conformance Criteria - Before laying of any pavement SIL and metal courses. SIL inspection to be carried out under supervision of engineer, verifying document to be signed off by engineer.
label | aaa691c7-ddbd-559c-b7d2-ece1f6df8a75 |  | note | Standard / Specification - PS - 2.2.16
label | 62109f41-cacd-5114-9387-f25dd7090a0b |  | note | Verifying Document - Hold Point Release
label | 53749f59-1a97-5155-aa0f-01f9dede2b1c |  | note | Frequency - Min 48h Notice
label | 8cf9b4d1-106e-5b75-8410-1d614ffa90d2 |  | note | Verification Activity - HP
label | c500ca95-c927-5ef8-8063-ff8836fab8fe |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.02.08 - Topography
label | bb8d94d0-cad7-5b1c-8c9b-72bfccbba337 |  | note | Acceptance / Conformance Criteria - Carry out level check on trimmed SIL. Survey conformance with Total Station. Tolerance = -30mm +0mm (NZTA F/2).
label | dfea0969-3fe2-5fb8-b6e2-71a12b4b8f40 |  | note | Verifying Document - Survey PDF against IFC or similar
label | c4f76caa-a1e7-5193-a040-20aa641b2936 |  | note | Frequency - every 1m across the road (avoiding islands) at 20m intervals
label | 9af73578-466b-5e6f-8458-cf20471145cb |  | note | Verification Activity - I
label | 0f251313-de06-520b-8bad-69923864004d |  | note | Verification Activity By - ENG
checkpoint-group |  |  | section | SECTION 7 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 7.02 Site Post Construction Activities
checkpoint-status |  |  | checkpoint | 7.01.01 - Construction Record Compilation
label | e33b7f2d-364e-554c-bbc9-71565eeabdcd |  | note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
label | 02cb16d6-62a9-5c07-b1fd-9212d27af6d9 |  | note | Standard / Specification - Downer
label | d5242ce2-72cf-5b1b-93ee-f2289178affc |  | note | Verifying Document - Records
label | 89f45c46-bd82-5272-9f96-7c18301858fe |  | note | Frequency - Post construction
label | e3b23594-8fa7-5800-9495-7772a6d9da38 |  | note | Verification Activity - H
label | 1f3b92d1-88f6-5192-86a8-d876bfc05b8f |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 7.01.02 - Survey Records
label | 09ede6c8-4248-52cc-ab76-a1b266afc9e7 |  | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
label | 64e2281b-04ef-5dd0-a95a-ed86a87e480f |  | note | Standard / Specification - Downer
label | c7cbca71-5e4d-5ee2-9c7e-338c155a00cc |  | note | Verifying Document - Records
label | 6bfdd8a6-0e45-5a32-b543-6abfceba1022 |  | note | Frequency - Post construction
label | b936ae2a-5b7f-575c-b00c-96f40edeb440 |  | note | Verification Activity - H
label | 239d20eb-1cda-5151-8ee0-a1a37fa759ad |  | note | Verification Activity By - SV
checkpoint-status |  |  | checkpoint | 7.01.03 - Redline Drawings
label | 4d55e902-6fc9-5949-bd90-3718360ae31b |  | note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. Red line to show any increase in SIL depth.
label | 92347465-5877-5da6-87bb-b262af7857d7 |  | note | Standard / Specification - Downer
label | 9dcd9ed1-320f-5caa-9c10-bea4580085c4 |  | note | Verifying Document - Redlines
label | 3bb64a96-941d-58a0-8054-c7df7e8a417b |  | note | Frequency - Post construction
label | 34016d76-9cb7-5f99-ac70-5ccdd07ac80a |  | note | Verification Activity - H
label | dc0a719b-c026-5d33-b5c3-421f855beb57 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 7.01.04 - Defect, Snag and Punch List
label | a813cec3-db3c-59fe-ae89-11ec57536b58 |  | note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
label | 4b87d8eb-15fe-50d6-a4c4-3d238a68c758 |  | note | Standard / Specification - Downer
label | 95b0b9db-0eec-5c01-aca1-4e4b0c7d024b |  | note | Verifying Document - Register
label | 54deb3d9-5e5c-5c40-b241-f30fadd35c16 |  | note | Frequency - Post construction
label | 98e8bc64-2444-52eb-abdc-f1fd9dccc045 |  | note | Verification Activity - H
label | ab26cea9-5803-55d8-a91d-5f75095d1303 |  | note | Verification Activity By - PE
checklist-flat |  |  | checklist | Stone Strong Wall Installation Checklist |  |  |  |  | Yes | Stone Strong Wall Installation Checklist | c6d03f27-e77e-4918-8777-b48ae7f56392
checkpoint-no-status |  |  | checkpoint | Details
text | 5c56ea41-624d-5f8b-a19d-09dc67614506 |  | textbox | Project Name:
text | 19e4224b-ed62-5e46-a533-cec42e4dac20 |  | textbox | Wall Location:
text | 6d6bf996-b548-5dd9-9ee0-d917dd2be190 |  | textbox | Block Layer:
text | e07570dd-33f5-585f-8141-e6b9b1e94af6 |  | textbox | Date:
text | 3453d87e-9319-54a9-acf6-8e0f2f4739a6 |  | textbox | Inspector:
text | 0692e518-3045-51d8-be5c-39c62e4d3b14 |  | textbox | RL of current Block/Backfill Layer:
checkpoint-status |  |  | checkpoint | Level foundation installed as per design. (Base layer only)
checkpoint-status |  |  | checkpoint | Drainage pipe wraped in filter sock to be installed along the base of the wall. (Base layer only)
checkpoint-status |  |  | checkpoint | Blocks Installed within specification tollerances & block pattern as per design drawings
label | 0dd331a6-905b-520f-85e7-1d0e1611df25 |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | 5e72637e-18b2-53de-82ca-d91284388021 |  | note | Table 4: MSE Tolerances
label | 807cb619-9421-5d28-ab8c-bf2da6ee9b5c |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | e72d7e9e-6340-547b-aadd-a6cedcd6e744 |  | note | Element ¦¦ Vertical Position ¦¦ Horizontal Position ¦¦ Vertical Alignment ¦¦ Horizontal Alignment
label | 981f8e13-85e0-5ab8-88d3-a29a943532b7 |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | 3747f6c4-c6b4-53db-b0a0-918d1038abda |  | note | Soil Surface ¦¦ ± 100mm ¦¦ N/A ¦¦ N/A ¦¦ N/A
label | 02105b15-4ea8-52aa-aa5d-d219414087e5 |  | note | Facings and wall structures ¦¦ ± 50mm ¦¦ ± 50mm ¦¦ ± 20mm in 3m ¦¦ ± 20mm in 3m
label | 7fb962c8-aa6b-57e4-980c-845ee2b51feb |  | note | Footings or supports ¦¦ ± 50mm ¦¦ ± 50mm ¦¦ ± 20mm in 3m ¦¦ ± 20mm in 3m
checkpoint-status |  |  | checkpoint | The correct number & length of parawebs are to be installed as shown on the construction drawings.
label | d1b9a8dd-3c74-5dd8-92ee-ba464e7bfa9c |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | cb25453d-184c-5806-8454-04709ba3e357 |  | note | 24SF1.1 BLOCK PARAWEB SCHEDULE
label | 917cf7ae-3f1c-5095-a6af-1e72e4cc8863 |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | 8e09984d-6f0d-50f2-abb9-cdcc9fa850cd |  | note | WALL HEIGHT (H) ¦¦ MINIMUM EMBEDMENT DEPTH (E) ¦¦ GRID LENGTH (L)* ¦¦ CONNECTIONS PER BLOCK
label | 571b4987-9d20-5db7-94d0-56578e113fa8 |  | note | – – – – – – – – – – – – – – – – – – – – – – – – – –
label | cc38ae48-88bf-57fa-ba2d-32f679a79148 |  | note | 8.0-10.0 ¦¦ 0.5 ¦¦ 9.0 ¦¦ 4
label | a0f36527-892e-5c8d-868f-3b82ab3d24a3 |  | note | 6.0 - 8.0 ¦¦ 0.5 ¦¦ 7.0 ¦¦ 4
label | bd88976d-5723-503a-aab2-1dfe67a9ad8c |  | note | 4.0 - 6.0 ¦¦ 0.5 ¦¦ 5.0 ¦¦ 4
label | 31674d68-f150-5e7a-abb3-b80d5b50c9a3 |  | note | 2.0 - 4.0 ¦¦ 0.5 ¦¦ 4.0 ¦¦ 4
label | 2ab1aa36-57c5-574a-9159-853a9471fcc3 |  | note | 0 - 2.0 ¦¦ 0.5 ¦¦ 3.0 ¦¦ 4
checkpoint-status |  |  | checkpoint | Paraweb is to be placed flat or with a 1% fall toward the rear of the wall.
label | 21d51e76-0781-5346-b566-b7bce9497e97 |  | note | ○ Paraweb must be free of wrinkles and lightly tensioned prior to and during placement of backfill. Shallow trench to be dug toward the end of the paraweb, pin to be used to pull paraweb taught prior to backfilling.
checkpoint-status |  |  | checkpoint | 150mm of fill cover is required before construction equipment can travel over the area
checkpoint-status |  |  | checkpoint | Backfill installed in max 250mm lifts
checkpoint-status |  |  | checkpoint | Proof roll completed on each layer
checkpoint-status |  |  | checkpoint | NDM testing completed
label | 313e95ff-a74a-5cd3-aca0-96fdfe23b44f |  | note | ○ Acceptance Criteria: Minimum 95% MDD
label | 18e05c73-4c1f-5444-a747-bda68ed498d4 |  | note | ○ Frequency: 1 per 500m3 with at least 1 test per 0.5m lift per 20m run of wall
checkpoint-status |  |  | checkpoint | Clegg testing completed (GAP65 only)
label | 1fa82988-8f1e-568e-9501-5d1fa85b3509 |  | note | ○ Acceptance Criteria: CIV relationship to be developed by testing alongside NDM tests
label | 6aadb3eb-b399-5f77-82e1-875f5b6abe9a |  | note | ○ Frequency: 4 tests per NDM
checkpoint-status |  |  | checkpoint | Scala testing completed (Sand only)
label | de471c65-92b2-5be9-8242-ab26586fb500 |  | note | ○ Acceptance Criteria: Minimum average value over 5 tests of 5 blows per 100mm, minimum single value of 4 blows per 100mm
label | 0d72fa89-8dc8-5a3d-9dd5-e8a34b2db867 |  | note | ○ Frequency: 1 per 500m3, 1 test per 0.5m lift per 20m run of wall
checkpoint-no-status |  |  | checkpoint | ADDITIONAL NOTES:
text | 81dd5416-d172-51ad-8781-a20c3ac7e029 |  | textbox
checklist-sectioned |  |  | checklist | ITP - Earthworks |  |  |  |  | Yes | ITP - Earthworks | c81579b7-fafa-4f2f-8de6-dd90cc97d798
checkpoint-group |  |  | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 3.04 Site Requirements
checkpoint-status |  |  | checkpoint | 3.04.01 - Construction Pack
label | bfee9e2d-a6b7-5f70-91c0-be5382ad9749 |  | note | Acceptance / Conformance Criteria - Submit a Construction Pack including a Methodology and JESA to the Engineer before works
label | 73019707-9e2c-534c-a05b-3fcde5672553 |  | note | Standard / Specification - Downer
label | fc46177b-d6da-5e5f-b473-8975092b2048 |  | note | Verifying Document - Construction Pack
label | cf028689-ebb3-5192-9152-61a6781b2e1b |  | note | Frequency - Submit 10 days prior to commencement of works
label | 1053d10a-8bc4-5c7e-b34e-717289b9bdf0 |  | note | Verification Activity - H
label | 769b19e6-25c2-51ef-b6c5-d49c93eb7c7b |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.04.02 - Survey Setout
label | cf831fa4-9e72-5f6f-93bc-7b92ee6d3e7a |  | note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
label | 51686e4f-ea10-57de-b465-280fbf293317 |  | note | Standard / Specification - Downer
label | a56c6f04-de46-5fb8-aa75-7917dc94c8f6 |  | note | Verifying Document - Survey Records
label | 77d6aa06-edd2-51e5-b4d1-f50385252962 |  | note | Frequency - Prior to Works
label | e9e2ae26-142d-55ca-80ae-2a4d6a362454 |  | note | Verification Activity - H
label | 5ac007ba-46a3-5bdd-84ea-5f8829d48733 |  | note | Verification Activity By - SV
checkpoint-status |  |  | checkpoint | 3.04.03 - Approved Construction Drawings
label | adac429a-f7e2-5e63-80d0-730d50cbd484 |  | note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
label | 3b02b1a1-aed9-5211-a134-9a04eeffc8ce |  | note | Standard / Specification - Downer
label | 3fdf891e-3ead-5017-b89f-18cf138d101c |  | note | Verifying Document - IFC Drawings
label | 4173a28d-0312-5795-9c8c-5dbbcc1476d8 |  | note | Frequency - Prior to works start
label | cfa53cbe-96bf-5d97-a692-51a01ce4fd25 |  | note | Verification Activity - H
label | 457bb499-0401-57d1-a2a5-f9335bba738f |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.04.05 - Topographic surveys for measurement
label | b0ac2514-a724-594e-9ebc-d4a1ce86bf41 |  | note | Acceptance / Conformance Criteria - The Contractor shall provide topographic survey reports and electronic survey models (in a dxf or dwg format) to enable the Engineer to verify quantities.
label | aa70e3c8-aabb-5a4e-bbe9-5a344f485278 |  | note | Standard / Specification - PS 2.2.12
label | f4e73635-e745-53ec-9c27-42e5b3f88ffa |  | note | Verifying Document - As-built
label | c95d9ef2-4b07-5466-a47b-37893c42864a |  | note | Frequency - Prior to works and Post Works
label | e0c41ef4-e1d7-542e-b948-53432b22e03a |  | note | Verification Activity - H
label | 666286b2-083d-59cc-9c48-2306a176d1d0 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 3.04.06 - Permits
label | 1086a7b0-b8fe-576d-8430-21b79737c40c |  | note | Acceptance / Conformance Criteria - The contractor shall complete internal and external permits for construction requirements
label | 5795d95a-16ee-5ff4-9521-bbea691dbe15 |  | note | Standard / Specification - ITP Register
label | abf5a4ad-1f5e-5db4-adc9-de90fce74b16 |  | note | Verifying Document - ITP Sign Off
label | d59d5929-0aa7-5d0b-89cb-e4bd1357d609 |  | note | Frequency - Prior to commencement of construction activity
label | 4c981c6f-8b77-5d6e-8556-3aabf085e93c |  | note | Verification Activity - R
label | 412821e0-a96c-5a47-92ad-7cf6c94f8d6b |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 3.04.07 - Stakeholder Management
label | 07f0300b-dee9-5f28-9128-a0d9daf1509f |  | note | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners
label | 66cd92a6-7a53-540f-9e88-afdef00c9aed |  | note | Standard / Specification - Project Stakeholder Management Plan
label | e422661f-e345-5a54-8688-d7cd237acb92 |  | note | Verifying Document - ITP Sign Off
label | 4b556bcf-42b1-56a5-bfdf-aff9f8fc919d |  | note | Frequency - Prior to Construction with continue updates throughout the works
label | b486a5da-ac9f-5a37-89a1-e4205d6f2fb7 |  | note | Verification Activity - R
label | f1c12282-a223-563a-b4af-025210d3be65 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | 3.05 Engineer Nominated Hold Points (Engineer’s inspections)
checkpoint-status |  |  | checkpoint | 3.05.01 - Environmental Controls Inspection
label | 220fb01b-d745-5045-be14-134205e9c4ca |  | note | Acceptance / Conformance Criteria - After installing measures to meet environmental requirements, before any earthworks begin.
label | 12810a36-7076-5fa3-9309-fa15bd838414 |  | note | Standard / Specification - PS 2.2.16
label | b6e38161-1c28-58dd-8003-e06fc54c07b5 |  | note | Verifying Document - Site Records
label | 2468b7fa-2b30-5143-9a17-d0cf723c63b6 |  | note | Frequency - Min 48h Notice
label | 82fc3266-7242-50e7-adfc-5b87a9456b0a |  | note | Verification Activity - HP
label | 6fe76645-582f-5023-93da-ab8501b34efd |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.02 - Bulk Fill Inspection
label | 39705f9c-e934-5b3b-8800-e537f4d47d3c |  | note | Acceptance / Conformance Criteria - Prior to beginning bulk filling operations.
label | bd28e4f6-5513-5ca5-b0b9-8f398af9b0bf |  | note | Standard / Specification - PS 2.2.16
label | 7f620750-7037-5f90-b423-8458b93e4bfd |  | note | Verifying Document - Site Records
label | 4cc87978-3af0-54f2-a37c-2861c60b4f3f |  | note | Frequency - Min 48h Notice
label | bcaf12cf-0efa-51ad-9ded-5b8f62c0353f |  | note | Verification Activity - HP
label | 4c8ec7d8-3e90-5a24-957b-45c963ead5e2 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.03 - Service Ducting Bedding Inspection
label | 57a8445d-fd38-5977-b749-a3db5394a8c6 |  | note | Acceptance / Conformance Criteria - Prior to laying any service duct, drainage/water/sewer pipeline and associated pits, fittings and structures
label | 0bd2a218-cf77-58c3-be8b-00842a9fa36c |  | note | Standard / Specification - PS 2.2.16
label | 241bcb23-ff2f-5e2e-bd32-1b66435db087 |  | note | Verifying Document - Site Records/ Refer to Services ITP for testing requirements
label | 305f24c2-0703-584a-9e40-ce3157339d1e |  | note | Frequency - Min 48h Notice
label | 1bc05559-a503-5c5f-8fd1-27d0207c0609 |  | note | Verification Activity - W
label | f5ac7004-e040-5094-b259-35cbbf4b3574 |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 3.05.04 - Service Ducting Backfill Inspection
label | 7e4a7988-03c3-5c7e-87af-ed5a4d520a43 |  | note | Acceptance / Conformance Criteria - After laying, before backfilling any service duct, drainage/water/sewer pipeline and associated pits, fittings and structures.
label | 5397b13e-25a0-53f7-90e6-21d21174ffa1 |  | note | Standard / Specification - PS 2.2.16
label | 38f7b901-ce61-5b82-ba86-2c9d95552aab |  | note | Verifying Document - Site Records/ Refer to Services ITP for testing requirements
label | e019faaf-8fe0-58e4-a4b1-8950d688b682 |  | note | Frequency - Min 48h Notice
label | d6a597bf-c1ae-5f05-a332-0e409159e8ac |  | note | Verification Activity - W
label | 9abd5920-382a-5c80-a2b5-d604334cd91e |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 3.05.05 - Geotextile Inspection
label | 30235357-ba2a-5d0d-bf32-e108465a9ab7 |  | note | Acceptance / Conformance Criteria - Before placement of any geotextile.
label | af850139-ab11-59d3-8d6a-5ded512dd2e8 |  | note | Standard / Specification - PS 2.2.16
label | 0ce6ff77-7be6-5200-8852-5d53e2272e01 |  | note | Verifying Document - Site Records
label | 5cc966d5-e906-56ef-8ad4-2635435e73de |  | note | Frequency - Min 48h Notice
label | 2e6fd158-bfe1-590a-9fbb-55341e4c9b58 |  | note | Verification Activity - HP
label | f63cd949-8628-5163-86d2-5e2ab51aae46 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.06 - Subgrade Inspection
label | bea3bd3e-1a67-59b3-b150-ca5c3595fab9 |  | note | Acceptance / Conformance Criteria - Subgrade inspection/stripped surface inspection, to include proof roll, scalar penetrometer and/or shear vanes.
label | 70fc358c-d354-5c6c-8df9-908d48a52f10 |  | note | Standard / Specification - PS 2.2.16
label | 714db9ad-f46f-52ef-a07e-a27fc0f7ea8d |  | note | Verifying Document - Site Records/ Test Results
label | 089e3007-f9b2-53da-8767-6fb0c3a01dd8 |  | note | Frequency - After surface is stripped
label | 40c00e8f-59e9-50f6-b11f-195e2cab0563 |  | note | Verification Activity - HP
label | fb26b3b6-d7be-55a5-b920-f8455c493cc5 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.07 - Undercut Inspection
label | 205f430b-1d40-5338-820a-fc895c69c6b2 |  | note | Acceptance / Conformance Criteria - Undercut (if required) inspection, to include proof roll, scalar penetrometer and/or shear vanes.
label | 04d27b24-5e7b-5476-a7ea-cd82483eb3f5 |  | note | Standard / Specification - PS 2.2.16
label | 65d11e86-28dd-584c-80fe-f09a9af7f41b |  | note | Verifying Document - Site Records/ Test Results
label | 3ff38dd2-5471-58e4-ae4a-e9a347932bd0 |  | note | Frequency - Prior to Subgrade Fill
label | cc051a3c-b0ae-58ed-85a3-2f3963327f46 |  | note | Verification Activity - HP
label | 1feae0c2-2658-5f77-98b9-3f71b3aea196 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.08 - Settlement Monitoring
label | 977450d1-fc9f-55e5-817a-1b9283275032 |  | note | Acceptance / Conformance Criteria - Settlement monitoring (Settlement pins & Targets) to be assessed by Geotechnical Engineer.
label | 6d2a8eb6-7a7b-5db6-b4f9-6b3941313504 |  | note | Standard / Specification - Drawing 5200
label | 70cf0c56-fdd1-5590-bef1-518c0f108a8c |  | note | Verifying Document - Site Records
label | 1a1b650a-d510-553b-b01c-32e36162d83f |  | note | Frequency - Prior to constructing pavement and wall
label | f7da49b3-2c9b-5dd0-bd85-3aeaf35709bb |  | note | Verification Activity - HP
label | 111c8e86-e703-5fd2-8eb8-e9bc46da9b4a |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 3.05.09 - Subgrade Fill
label | 3b6d39e4-aded-5525-9a05-2f3ba7d4111b |  | note | Acceptance / Conformance Criteria - Inspection of completion of sub grade fill prior to placing SIL, to include proof roll.
label | 1e9e7ca8-b008-5387-b5a7-47972e295356 |  | note | Standard / Specification - PS 2.2.16
label | 53267922-2588-5542-83ec-dcce3f7fd14f |  | note | Verifying Document - Site Records
label | 9c59b01f-1e26-5caf-bc10-e68acc082366 |  | note | Frequency - Prior to placing SIL
label | c72eeff7-163c-5f7e-80c2-3f277204adcb |  | note | Verification Activity - HP
label | a33638a4-2802-5015-8b04-2758f810735c |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-group |  |  | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - Earthworks General Materials
checkpoint-status |  |  | checkpoint | Imported Fill Approval
label | 45fd01c7-e910-54d4-bec7-c51dc5e869fb |  | note | Acceptance / Conformance Criteria - Due to the fill-deficit on this project, imported fill will be required and should be discussed with and approved by the Engineer to verify its appropriateness and quality control testing requirements prior to use.
label | 00224ad9-b44c-5c64-925b-0bdf2c3ad0b9 |  | note | Standard / Specification - GWS 2.4.1
label | 034eb994-bff4-5dce-a8f5-5ca2e39e8efb |  | note | Verifying Document - Lab Tests
label | 7bda6704-2e88-5a6c-903a-5abc136f5367 |  | note | Frequency - At least 2 days prior to placement and compaction.
label | be698d53-8e18-584e-b59e-5008a430fece |  | note | Verification Activity - HP
label | 1b3a4554-bdab-544a-b0fe-2f429c05b292 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | Re-Use Suitability Approval
label | 41060b61-19fa-58c6-8795-3e53e1d8ca7d |  | note | Acceptance / Conformance Criteria - The Contractor shall test representative samples of the site-won material to be used as Bulk Fill and Subgrade Fill and the results are to be sent to the Engineer for approval.
label | 71239f25-057a-5495-a65b-8059f502eb40 |  | note | Standard / Specification - GWS 2.4.2.1
label | 91ac6848-60d0-5318-9a00-ed4c631f5ddb |  | note | Verifying Document - MDD, OMC, Shear Vane, PSD
label | 51318647-1fc0-5090-a5bb-df5e632715e4 |  | note | Frequency - At least 2 days prior to placement and compaction.
label | 4017e19b-6c59-58e0-a358-c2fb46c5bd2f |  | note | Verification Activity - HP
label | 2738daad-13e6-56e2-850b-dbfe698f6491 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | Eastern Gully Weir Fill - Cohesive (Imported silt/clay)
label | 13cb71d6-c1af-54a6-b7bd-21510996a303 |  | note | Standard / Specification - GWS
checkpoint-status |  |  | checkpoint | Eastern Gully Weir Cohesive Fill Material Testing
label | 7e475385-e59b-545a-a386-0317f85d7e4f |  | note | Acceptance / Conformance Criteria - Eastern Gully Weir Fill shall be tested for Standard Compaction, Solid Density, Plasticity Index (PI), Particle Size Distribution, and Liquid Limit for
label | 5599aacf-9b19-556b-8071-03ee88a79288 |  | note | Standard / Specification - GWS 2.9.4
label | 291d7143-24d1-5bea-a541-b52e6e678f66 |  | note | Verifying Document - Test Results
label | c80900c5-6f26-514c-925c-08033d42fde0 |  | note | Frequency - At least 2 days prior to placement and compaction.
label | 5e1dd57d-db29-5032-93c2-fc611966f113 |  | note | Verification Activity - I
label | 2acb792c-7756-591a-9291-3d52f360c47d |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Subsoil Drainage
checkpoint-status |  |  | checkpoint | Subsoil Pipes
label | 3f94bf73-bf5b-5437-9da8-17e3ae97576d |  | note | Acceptance / Conformance Criteria - Drainage pipes used in subsoil drainage shall be smooth bore perforated corrugated 160mm diameter complying with NZTA F5 unless otherwise stated on the drawings. Pipes shall not have a geofabric filter sock unless requested by the Engineer.
label | f9a94957-2d43-5bcb-b341-3538bb894ea7 |  | note | Standard / Specification - GWS 3.2.1
label | b629c8f6-6dfd-5ea2-b72e-17917646bbc1 |  | note | Verifying Document - Datasheet
label | f4e1f338-8fa7-504b-a4cb-56b41896398e |  | note | Frequency - Prior to installation
label | 1a71e582-8f83-564e-92ab-12f86985a0e1 |  | note | Verification Activity - C
label | 33c9ad80-23dd-5d83-a970-60e5f6105c12 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | Subsoil Drainage Aggregate
label | 157dd5fd-3914-5a7d-b6cd-82a7e9a4aafb |  | note | Acceptance / Conformance Criteria - When placing geotextile wrapped drainage aggregate, the drainage material shall be in accordance with TNZ F/6 including gradings
label | aa2baf26-c5d7-5049-ab44-ef2f743b3ebe |  | note | Standard / Specification - GWS 3.2.2 & 3.4
label | 1248aa8d-7bc1-58cb-a514-3c47b2467f19 |  | note | Verifying Document - PSD, CR
label | 7a23c5b4-57d0-5aa9-9f7e-07c02b92409f |  | note | Frequency - Prior to installation
label | 5e0a201a-911e-5ee8-b97a-d9332fbdcfe8 |  | note | Verification Activity - C
label | 506f0618-6e1c-5102-87bc-d361e1022c7b |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | Filter Cloth
label | 40786ed1-1abb-5eab-b26d-821b1c62bf75 |  | note | Acceptance / Conformance Criteria - Any filter cloth surround specified on the drawings shall meet the requirements of Transit Specification TNZ/F7, Filtration Class 2 and Strength Class B unless otherwise specified on the drawings.
label | a0219122-25d9-528f-ae9a-22dbaf87c7a8 |  | note | Standard / Specification - GWS 3.2.3
label | f610f319-f379-53fa-8154-8b4d5bca6c13 |  | note | Verifying Document - Datasheet
label | 2e3e366f-ba60-5836-9a55-28f1ba3a5d70 |  | note | Frequency - Every 1,000m3. At least two weeks prior to works.
label | 951ef335-8d62-5c06-be73-7eec18ac3d1f |  | note | Verification Activity - C
label | fe3a95d8-88a3-576f-aa42-613286c0653d |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Geotextile and Geogrid
checkpoint-status |  |  | checkpoint | Geotextile Approval
label | 9a3d2597-ebe2-539a-aa42-61368c2611c3 |  | note | Acceptance / Conformance Criteria - The Contractor shall submit to the Engineer for approval the details of the filter fabric they propose to use at least two weeks prior to commencement of works, including compliance certificates.
label | a79a093a-64b5-5be4-812d-9f9f7aa9450c |  | note | Standard / Specification - GWS 4.1
label | 561e97cf-103c-5838-ac55-be14acc86d5e |  | note | Verifying Document - Compliance certificates
label | 79bd7770-6037-5577-8954-1c2bdc4582d9 |  | note | Frequency - At least two weeks prior to works
label | 067be5b6-4d6d-5483-92ea-3e46a124d9a9 |  | note | Verification Activity - HP
label | 967372ea-a3a3-54c8-9a64-18ddb723d059 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | Uniaxial, Biaxial and Triaxial Geogrid
label | 20af9f1b-6c10-5787-a2c6-f3c6221c2cc6 |  | note | Acceptance / Conformance Criteria - All uniaxial, biaxial and triaxial geogrid shall be manufactured in accordance with a management system that complies with BS EN ISO 9001 and BS 14001 and shall submit to the Engineer for approval.
label | ef41addc-1cbe-5c0d-9ca5-8d1ef6fdbe67 |  | note | Standard / Specification - GWS 4.2
label | 0c7958a6-3ee8-5743-b5ce-19e007a5a8f6 |  | note | Verifying Document - Datasheet
label | 913b2d66-4c18-5767-a5e9-17b67944114f |  | note | Frequency - At least two weeks prior to works.
label | aea6a083-cef0-5f4f-85d7-58111f8e5b2e |  | note | Verification Activity - HP
label | 2fb75c33-4757-5988-8eb9-2f85068131e8 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-group |  |  | section | Settlement Monitoring
checkpoint-status |  |  | checkpoint | Settlement Baseplate Design
label | b2e13714-0793-5134-9aba-dff3f3e49e11 |  | note | Acceptance / Conformance Criteria - Equipment shall consist of 600mm x 600mm base plate (typically 20mm thickness),150mm PVC duct, 32mm diameter threaded bar with couplers for extensions at 1m intervals and waratahs and coloured flagging for protection following installation.
label | ab58a620-29e1-5cd5-9913-2c7857009c45 |  | note | Standard / Specification - GWS 6.2
label | 9dc5bee6-37ba-5834-afe8-f7ef22fcf6eb |  | note | Verifying Document - Datasheet
label | 177044c2-7b5a-56d8-b467-6a11c2a05f8d |  | note | Frequency - Prior to installation
label | 38c7b763-7106-5ffc-9cab-8f619cc54550 |  | note | Verification Activity - I
label | 9d733ae1-3eec-549d-8aba-40c2e14e2c81 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | Settlement Pin Design
label | 4993c9e1-6514-5af4-8698-bf4bb1ef0f04 |  | note | Acceptance / Conformance Criteria - Settlement pins are to comprise 32mm diameter Reidbar rods driven a minimum depth of 0.5m into the ground surface. The top of the pin shall be domed to ensure repeatable survey measurements.
label | 8280e55b-aaec-5527-b3ea-2bd24da7ac4e |  | note | Standard / Specification - GWS 6.3
label | 6a86ff42-72c4-56ff-9fe0-eff5fd9492fd |  | note | Verifying Document - Datasheet
label | f069dae9-7360-5fcb-a785-701687cc1afc |  | note | Frequency - Installed within 24 hours of reaching design subgrade level
label | c73ca30a-597f-5a40-b41f-829e4cedbddd |  | note | Verification Activity - I
label | 33be6f18-8792-5920-bf9d-de4009c5069b |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | Settlement Pin Bedding
label | 2e1cfb65-6bc6-5474-a42d-b8ec2e0429ff |  | note | Acceptance / Conformance Criteria - Installation of the settlement markers shall occur at the base of the fill embankment, prior to placement of any fill. They shall be installed on a 100mm thick sand layer to form an even and smooth foundation which will be levelled using a spirit level.
label | 2e80c0cf-b430-5cf6-8078-e90a77e6de23 |  | note | Standard / Specification - GWS 6.2
label | bb88f167-2eac-5ea1-a07a-4edb43311454 |  | note | Verifying Document - Site Record
label | 433e324e-7e70-5607-946b-81fc02328d45 |  | note | Frequency - Prior to placement of fill
label | f0211247-806a-5652-b84e-408b2ce9da48 |  | note | Verification Activity - I
label | 8c69d77c-c146-5a3b-9c0b-2d63827771a2 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | SECTION 5 – CONSTRUCTION ACTIVITY – CLEARING - 5.01 Demolition / Site Clearance
checkpoint-status |  |  | checkpoint | 5.01.01 - Clearing
label | 78082b3a-e12b-5c21-a358-53d24b788896 |  | note | Acceptance / Conformance Criteria - All surface objects including fences, gates, debris, wood, dumped rubbish, concrete and other protruding obstructions shall be cleared and disposed of
label | 9da1e544-eed3-519d-91c1-83240462c755 |  | note | Standard / Specification - PS 3.1
label | b50dac47-4fde-59b0-813f-56d6371997cc |  | note | Verifying Document - Site Records
label | a64d2405-c9fc-5811-a16d-dfcafa596de9 |  | note | Frequency - Prior to earthworks
label | 1ca5d8fa-084f-53ca-b716-8880263ff1fd |  | note | Verification Activity - C
label | 783b14cd-f41b-5af2-ab9a-9cdee83f416d |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 5.01.02 - Demolition
label | 898e6b66-9ffd-5630-8dcf-66d7cdd5cb4e |  | note | Acceptance / Conformance Criteria - Remove all buildings from the site including foundations, buried services and any other remnants.
label | 1e4b5000-6877-5ca4-84b0-743bc492ac42 |  | note | Standard / Specification - PS 3.2
label | 24b04cf3-b6ce-5360-8034-99e455efb90d |  | note | Verifying Document - Site Records
label | 0f5cac53-5c09-5007-b349-9f02b07fb230 |  | note | Frequency - Prior to earthworks
label | 676ec549-3b82-5463-b42f-70db12e7831d |  | note | Verification Activity - C
label | 0937604e-d956-5db1-bf39-00d54c56fc50 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 5.01.03 - Septic tanks
label | f8c973f8-deef-5746-94a7-f251b5a2a71d |  | note | Acceptance / Conformance Criteria - Septic tanks shall be pumped out prior to removal and backfilling
label | b49d37c8-cb6e-501b-a4fc-a478b803a512 |  | note | Standard / Specification - PS 3.2
label | df2c9c6a-22a3-5041-8d6d-32a328bfb5ce |  | note | Verifying Document - Site Records
label | c6bf3dbd-30cf-5317-9142-90b0a2dd1c2d |  | note | Frequency - Prior to earthworks
label | f5499a7d-03ba-57c9-b1ef-2012a2864ca5 |  | note | Verification Activity - C
label | c011ed82-15bf-5f55-9f4c-d8313d37f9ce |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 5.01.04 - Plant Clearance
label | 6d4d6e9c-4028-5c04-8cc4-6787c37ba964 |  | note | Acceptance / Conformance Criteria - Vegetation, Tree stumps, shrubs, plants, logs, including any roots greater than 25mm in diameter shall be cleared and disposed of
label | e513f065-fdac-5f75-a44b-2e4108a6638a |  | note | Standard / Specification - GWS 2.5
label | 89f3f0b4-9bed-5b89-9ee8-bc47e57cad46 |  | note | Verifying Document - Site Records
label | dfdf7fa0-228d-51d6-a8d7-2b99f126969c |  | note | Frequency - Prior to earthworks
label | 705917af-f81b-547e-848b-02cbfb8e0005 |  | note | Verification Activity - C
label | 88634bea-cf7c-5452-9202-e6787e9c447d |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | SECTION 6 – CONSTRUCTION ACTIVITY – EARTHWORKS - Earthworks General
checkpoint-status |  |  | checkpoint | 6.1.1 - Groundwater Management
label | eb0e86e5-e733-5223-bbb9-927510d23d9b |  | note | Acceptance / Conformance Criteria - The Contractor shall provide all pumping plant and drainage systems required to ensure excavations are always free from water.
label | 7e7617fa-fae5-5875-b604-3d92f1ae9a02 |  | note | Standard / Specification - PS 3.4
label | e28a6666-2864-58ac-b2be-d03fe009182d |  | note | Verifying Document - Correspondence
label | 3c59ca22-9750-56f4-9528-71508147a1a2 |  | note | Frequency - Prior to excavation
label | 963a9310-1758-5ef2-b107-9ca62263c7a2 |  | note | Verification Activity - W
label | 6dad533d-9d56-562d-a873-7ac544b09ff9 |  | note | Verification Activity By - ENG
checkpoint-status |  |  | checkpoint | 6.1.2 - Cut to Waste Approval
label | 4d18e52c-8158-562d-a166-7fae841d5a02 |  | note | Acceptance / Conformance Criteria - The Contractor shall obtain written approval from the Engineer prior to cutting any material to waste. To include evidence and extents of cut to waste. Topography survey data of all material to leave site, photographs of material and any material test reports.
label | e1a13489-9a5d-55a8-902e-237a7c4a31e1 |  | note | Standard / Specification - GWS 2.4.3
label | f68f05fa-aac4-5343-bc89-5a71a59747d5 |  | note | Verifying Document - Correspondence/Photos/Survey
label | db47406d-a14b-5988-af96-e4bde7d4b0ae |  | note | Frequency - Prior to cut to waste
label | 1f8dfc8b-94b1-5db0-91bf-802c87634719 |  | note | Verification Activity - HP
label | d1e607a9-75e4-5ccc-9495-77974ca634ce |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 6.1.3 - Foundation Suitability
label | 8f52a174-1f14-5d9c-8f84-53832a38af69 |  | note | Acceptance / Conformance Criteria - The foundation on which filling is to be placed must be observed by the Engineer following clearing and prior to the placement of any filling to confirm the strength of the underlying soils is sufficient.
label | 403a8560-3fe5-5d70-8ba0-4889dd83f554 |  | note | Standard / Specification - GWS 2.7
label | 190f3aa6-7334-5f5f-a3ee-8d073c6c01ad |  | note | Verifying Document - Site Record
label | 9fe9f93a-da52-5774-aa98-f6a1d17205aa |  | note | Frequency - Prior to the placement of any filling
label | 49c4a9bc-2a33-58b4-aa32-18d9c49e9425 |  | note | Verification Activity - HP
label | 55a75d49-9d4c-53ae-b04c-d26ae7dc6395 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 6.1.4 - Unsuitable ground
label | f74e983f-b3f1-52d2-a6da-8feacdfc6948 |  | note | Acceptance / Conformance Criteria - Unsuitable ground shall be defined as any pre-existing uncertified filling or natural silts/clays having an undrained shear strength of less than 70kPa or natural sands having less than 3 blows per 100mm penetration when tested with a Scala penetrometer. The contractor shall obtain instruction from Engineer around extent and depth of undercut.
label | 72b8a517-2c2f-576c-ab22-8a5927e27db0 |  | note | Standard / Specification - GWS 2.7
label | 20f3605a-ef82-5349-8b91-838106d91174 |  | note | Verifying Document - Shear Vane / Scala penetrometer
label | 6e495bf5-1e22-523d-9860-9240145d4445 |  | note | Frequency - Prior to the placement of any filling
label | b650b8b5-6206-5b56-9962-d2e1a99ce04e |  | note | Verification Activity - I
label | 5bd7b186-b7b2-5740-b0cd-6b7cd6829b31 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.1.5 - Preparation for Filling
label | a6040fbd-88ee-5361-8734-01f4b7fd8f51 |  | note | Acceptance / Conformance Criteria - Preparation of the firm to stiff / medium dense subgrade beneath the proposed fill areas should comprise stripping of all vegetation, topsoil, any pre-existing fill materials or weak alluvium followed by benching of the exposed subgrade where natural slopes beneath the fill exceed gradients of nominally 1:5 (vertical to horizontal).
label | 7c91a7c3-4bf8-5b9f-be81-ab10b9428ed3 |  | note | Standard / Specification - GWS 2.9.2
label | fc234cf2-875c-50a9-bd15-e27556849159 |  | note | Verifying Document - Site Record
label | 22f53065-82e3-5ab6-ae5a-39840a6267b4 |  | note | Frequency - Prior to placement and compaction of fill
label | 239279e4-1553-5a57-b7d5-a078fa61cec6 |  | note | Verification Activity - I
label | aa3d6ba2-bde8-57a5-aefa-e21d85e5b1ea |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.1.6 - Subgrade Conditioning and Proof Rolling
label | bd14a369-a5e5-53fe-af67-b8de5e4943c4 |  | note | Acceptance / Conformance Criteria - The subgrade shall be scarified and moisture conditioned where necessary and then proof rolled to verify the subgrade stiffness and consistency.
label | c9327137-4cde-584e-9d31-f301eced2c4f |  | note | Standard / Specification - GWS 2.9.2
label | 5a215d15-4350-5e0a-b384-5db64abf102b |  | note | Verifying Document - Proof Rolling Sheet
label | 437a76a4-fcbb-5fb8-b9c0-dba79aa678b3 |  | note | Frequency - Prior to the placement of any filling
label | 5e876cd9-e4c1-583b-bce3-5c43af9e35ff |  | note | Verification Activity - V
label | 51ccb122-fc8c-5e98-9471-2075d87f0242 |  | note | Verification Activity By - SE/QE/ENG
checkpoint-status |  |  | checkpoint | 6.1.7 - Undercut Backill Compliance
label | 34b385b3-2355-59e7-876f-ff44ad010bdd |  | note | Acceptance / Conformance Criteria - Test results for undercut backfill prior to bulk fill commencing, NDM, scala penetrometer, shear vane or cleggs, material dependant. TBC instruction from engineer. Undercut backfill QA to be filed/captured separately from bulk earthworks fill QA.
label | f2d5b609-ffe3-5060-90eb-b2aeb2b22cc6 |  | note | Standard / Specification - GWS 2.9.2
label | 2a5ceae4-6204-56b2-af74-f7b852dc82ec |  | note | Verifying Document - Test Results
label | 3d85fe98-17a1-5ba1-8548-1faff69eb73f |  | note | Frequency - Prior to bulk fill commencing
label | ec2b9ddc-86b4-5199-a84a-b585302e0d67 |  | note | Verification Activity - R
label | f06ec382-6ae1-5540-b7b0-49c345564686 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.1.8 - Topographic Survey
label | a5561c5b-ca9e-5395-be42-bdfcd8eb8c4f |  | note | Acceptance / Conformance Criteria - All subgrades and undercuts to be captured via topographic survey (GPS)
label | 972f635b-ad00-5e9d-a764-3df28e80d140 |  | note | Standard / Specification - PS 2.2.12
label | 67096b30-70fa-568b-8ca7-5c4476661a15 |  | note | Verifying Document - Survey Results
label | f665dbf1-e4ae-555a-a155-8f872335b31f |  | note | Frequency - Prior to cutting or filling.
label | 4e3075c0-3f73-5c5e-acea-53b9ff9dc3aa |  | note | Verification Activity - R
label | 0dd85854-02b3-5db4-9210-0eb8f56a5c43 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Stockpiles
checkpoint-status |  |  | checkpoint | 6.2.1 - Stockpiles
label | bef39443-7d85-52f7-8d0c-66f2e56b1f58 |  | note | Acceptance / Conformance Criteria - The location of all temporary stockpiles must be approved by the Engineer prior to placement. Where stockpiles cannot be avoided above sloping ground, they should be placed over a wide area with the height restricted under the direction of the Engineer.
label | 25ca6fa2-218e-58ee-bfc3-2c5a7c30c9df |  | note | Standard / Specification - GWS 2.9.3
label | 0234ee50-2cac-5b79-8bc4-e97d89f84622 |  | note | Verifying Document - Stockpile Map
label | db7cde91-35c2-5185-9e3b-b29a79f2176d |  | note | Frequency - Prior to placement.
label | 48298222-1d4e-5d30-932c-06dd5fa4628d |  | note | Verification Activity - HP
label | 1497dad8-abb9-5023-a8ca-f94c8ff694a8 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-group |  |  | section | Earthfill
checkpoint-status |  |  | checkpoint | 6.3.1 - Earthfill Placement and Compaction
label | 286ede01-a444-59af-8320-caa3012c88cc |  | note | Acceptance / Conformance Criteria - Earthfill must be placed, spread and compacted in controlled lifts under the direction of the Engineer. All earthfill must be placed to ensure adequate knitting of successive fill lifts by ripping any surfaces that have become dry prior to placing the following fill lift.
label | b3cf298a-4b4e-50e8-92bc-e06a06b5c243 |  | note | Standard / Specification - GWS 2.9.4
label | 0ba917b5-eebf-5035-abc0-0e37abe8cbed |  | note | Verifying Document - Site Record
label | 0e81b6c5-9757-515a-b91b-e69f20515b83 |  | note | Frequency - Per lift
label | d3f4f4d1-826c-579d-b32f-e6b543e41cf7 |  | note | Verification Activity - HP
label | 4406eb78-5b4b-5bc2-ac14-4fb5ba61d892 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-group |  |  | section | Bulk Fill - Granular (Hinuera Sands or Imported Sand/Gravel)
checkpoint-status |  |  | checkpoint | 6.4.1 - Proof roll Testing
label | 81e47988-85b7-532a-bae1-1a12e72c1d69 |  | note | Acceptance / Conformance Criteria - Each layer shall be tested via Proof roll to: 7mm maximum impression
label | 881f0569-d51a-5ef7-8ef0-d3678621cee8 |  | note | Standard / Specification - GWS 2.9.4
label | 71c058e2-0e0e-5335-9f4a-00d696132c0b |  | note | Verifying Document - Proof Rolling Sheet
label | d2cdd97d-44a2-54ec-8461-90172cb8a3be |  | note | Frequency - 100% of each layer
label | a3cf788c-318e-5cbc-adc4-8104048747c7 |  | note | Verification Activity - I
label | a6b88ab0-b9d8-5dd7-8d79-5c1cdfb29ad2 |  | note | Verification Activity By - SE/ENG
checkpoint-status |  |  | checkpoint | 6.4.2 - Compaction Testing
label | 0361ad6d-e77a-5d58-81fe-394dbecd915c |  | note | Acceptance / Conformance Criteria - Bulk fill shall be tested by DT at 300mm probe depth 95% MDD. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick.
label | 702d3671-8874-54ae-904e-c2b546422874 |  | note | Standard / Specification - GWS 2.9.4
label | 84133fc7-b8f9-55b3-a993-09885b7c8b41 |  | note | Verifying Document - Test Results
label | 9d017020-3c0e-553d-b800-f863103cd6c3 |  | note | Frequency - 1 set / 500m3 (1 set to include 1 x 0.5m deep Scala and 1 x DT within a 3m radius)
label | e73f6f4f-173e-5265-a670-bd32cc5dbb1d |  | note | Verification Activity - R
label | 2c57898f-d1f2-505a-abc6-d6dda53bcda1 |  | note | Verification Activity By - SE/ENG
checkpoint-status |  |  | checkpoint | 6.4.3 - Scala Penetrometer Testing
label | f1331738-3f66-562e-aab4-9f1c14cd166a |  | note | Acceptance / Conformance Criteria - Bulk fill shall be tested by Scala Penetrometer every 500m3 to: 4 blows per 100mm. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick.
label | 3ecfb16a-a9fc-5056-9e5c-bed455d0694e |  | note | Standard / Specification - GWS 2.9.4
label | e7df00a3-4bb3-5329-b09e-c11d8a7e7f46 |  | note | Verifying Document - Test Results
label | c5a4782b-328c-5561-92b4-2ad8f96d9ddf |  | note | Frequency - 1 set / 500m3 (1 set to include 1 x 0.5m deep Scala and 1 x NDM within a 3m radius)
label | 3b2bf319-1640-5979-bca2-736dc8f5952c |  | note | Verification Activity - R
label | 11826f75-4718-5556-89d7-4887d9c2d9d7 |  | note | Verification Activity By - SE/ENG
checkpoint-group |  |  | section | Bulk Fill - Cohesive (Imported Silt/Clay and Sand/Silt Blend)
checkpoint-status |  |  | checkpoint | 6.5.1 - Vane Shear Strength Testing
label | dbbc0a18-ae6a-5cf7-9ce0-18ec7a7ed771 |  | note | Acceptance / Conformance Criteria - Bulk fill shall be tested for Vane Shear Strength to: Minimum average 120kPa over 10 tests, minimum single value 110kPa. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick. NDM direct transmission with probe depth of 300mm.
label | 36bcc3d7-db98-5639-af85-741172812629 |  | note | Standard / Specification - GWS 2.9.4
label | 251ea5e9-0ef2-5550-9457-1743ce45a70b |  | note | Verifying Document - Test Results
label | 1d857961-37ac-5b77-a66c-91f514f529e0 |  | note | Frequency - 1 set / 500m3 (1 set to include 5 x shear vanes and 1 x air voids within a 3m radius)
label | 56d13354-9e3c-5cfb-91f0-04b5ea52b5e7 |  | note | Verification Activity - R
label | 2f5aef00-2b4f-5282-a689-66479c32e70b |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.5.2 - Air Voids Testing
label | 9901dfd8-8abf-5c33-9555-ffa623f92f70 |  | note | Acceptance / Conformance Criteria - Bulk fill shall be tested for Air Voids to: Maximum average 10% over 10 tests, maximum single value 12%. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick. NDM direct transmission with probe depth of 300mm.
label | f3da272a-2c60-5787-9a8d-72ddfd15ed6c |  | note | Standard / Specification - GWS 2.9.4
label | 36bf09f3-2f3e-56ec-8617-e97bc6b90620 |  | note | Verifying Document - Test Results
label | 0a4d47d7-3840-5c0a-a55d-504f47de1df7 |  | note | Frequency - 1 set / 500m3 (1 set to include 5 x shear vanes and 1 x air voids within a 3m radius)
label | c3c6cc28-d947-5fc1-bac2-97a43d11f29e |  | note | Verification Activity - R
label | 8267f1ef-1ee0-56f7-bf44-85d36163dbe2 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Subgrade Fill - Granular (Hinuera Sands or Imported Sand/Gravel)
checkpoint-status |  |  | checkpoint | 6.6.1 - Proof roll Testing
label | b633fc11-6f49-5738-ae16-b70fd989c7e5 |  | note | Acceptance / Conformance Criteria - Each layer shall be tested via Proof roll to: 5mm maximum impression
label | bde7cd76-353a-543d-81ea-5b47ef0877e2 |  | note | Standard / Specification - GWS 2.9.4
label | 2f034ce5-f965-53c1-9f07-ab3c43bb4201 |  | note | Verifying Document - Proof Rolling Sheet
label | bbc95283-876f-534a-a57e-454ecf07ca08 |  | note | Frequency - 100% of each layer
label | b884386a-1912-518f-82fa-88e7ffc3a8ab |  | note | Verification Activity - I
label | a9e47c7c-12af-5d6a-a677-b116b4721333 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.6.2 - Compaction Testing
label | 72f4e1d4-2714-5bad-b61b-a89df2751088 |  | note | Acceptance / Conformance Criteria - Subgrade fill shall be tested by DT every 500m3 to: 98% MDD. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick. NDM direct transmission with probe depth of 300mm.
label | 90c5da6a-fd57-519a-af68-7f03ff4eeae2 |  | note | Standard / Specification - GWS 2.9.4
label | 65582f1c-08a9-5ed4-9cca-7ae57b6fd2b2 |  | note | Verifying Document - Test Results
label | 7d1f3f80-e554-5f08-8f36-5f61dd240c55 |  | note | Frequency - 1 set / 400m3 (1 set to include 1 x 0.5m deep Scala and 1 x NDM within a 3m radius)
label | fb7d72f3-6266-5d2f-a84a-b8ef5a9bfb43 |  | note | Verification Activity - I
label | abf82fab-4d37-580d-834e-df632b56edbd |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.6.3 - Scala Penetrometer Testing
label | fa73c0bd-67ed-5c81-b9f6-bcf874f36e76 |  | note | Acceptance / Conformance Criteria - Subgrade fill shall be tested by Scala Penetrometer every 500m3 to: 5 blows per 100mm. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick.
label | b52aed14-7a5f-5c32-b592-ad178c6a4ba8 |  | note | Standard / Specification - GWS 2.9.4
label | cbf75fa7-f933-50e9-81ab-d8fe0557bba2 |  | note | Verifying Document - Test Results
label | 7c9d20af-a460-54be-8d2d-db9494b4edc4 |  | note | Frequency - 1 set / 400m3 (1 set to include 1 x 0.5m deep Scala and 1 x NDM within a 3m radius)
label | d6175d17-dc53-576e-92fe-4c625f891373 |  | note | Verification Activity - I
label | b98e763c-d8e0-5357-ab9e-fbe30cc17c2e |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Eastern Gully Weir Fill - Cohesive (Imported silt/clay)
checkpoint-status |  |  | checkpoint | 6.7.1 - Shear Vane Testing
label | 97b9b3e5-db79-59b2-b466-0b008ccff789 |  | note | Acceptance / Conformance Criteria - The Cohesive Fill shall be tested by Vane shear strength to: Minimum average 140kPa over 10 tests, minimum single value 120kPa
label | 5caf5c28-8adb-5986-ac40-117c055eb178 |  | note | Standard / Specification - GWS 2.9.4
label | 08babd25-b5e1-5a0e-ab73-99303ff9fc43 |  | note | Verifying Document - Test Results
label | e2d0c240-a3cd-5182-a990-b731d77ba303 |  | note | Frequency - set / 500m3 and every 0.5m lift (1 set comprises 4 x shear vanes and 1 x air voids within 3m radius)
label | 76397b3a-dd0b-59ae-b0c7-b18f4785fcd5 |  | note | Verification Activity - I
label | cb0b7c5b-f49c-59af-ab6f-04fa7cf3847b |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.7.2 - Air Voids Testing
label | 4db17005-7815-5b97-af65-a2d559d0b55c |  | note | Acceptance / Conformance Criteria - The Cohesive Fill shall be tested for Air Voids to: Maximum average 5% over 10 tests, maximum single value 6%. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick. NDM direct transmission with probe depth of 300mm.
label | 9e4e2f34-58e8-5cba-8f25-809593f7e3b4 |  | note | Standard / Specification - GWS 2.9.4
label | b94e47d1-f994-5e12-9c5a-ca666b8a440e |  | note | Verifying Document - Test Results
label | 33c1e730-fd7a-5790-b721-486d1a8144f6 |  | note | Frequency - set / 500m3 and every 0.5m lift (1 set comprises 4 x shear vanes and 1 x air voids within 3m radius)
label | 8f1e6d8b-95ee-55cc-ab21-e7ba2bff47aa |  | note | Verification Activity - I
label | b2000c16-2302-5b4f-a14b-e4c0f973756c |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.7.3 - Water Content Testing
label | 5a8fb55b-62f9-5e81-87cf-23c8f3f5f47e |  | note | Acceptance / Conformance Criteria - The Cohesive Fill shall be tested for Water Content to: Minimum 2% dry and maximum 6% wet of optimum water content. Survey shot at each test location, point ID to be agreed upon by contractor/sub-contractor to match test number, each test lift not to exceed 500mm thick. NDM direct transmission with probe depth of 300mm.
label | 04845150-aafd-5748-987d-ec3e37a628f5 |  | note | Standard / Specification - GWS 2.9.4
label | a24404f7-d7be-5b60-acf0-37f389166146 |  | note | Verifying Document - Test Results
label | b4089446-2691-5cae-af41-2c84000040ba |  | note | Frequency - set / 500m3 and every 0.5m lift (1 set comprises 4 x shear vanes and 1 x air voids within 3m radius)
label | 607ffd22-9ae7-5e38-92d4-cdfc2d60fd38 |  | note | Verification Activity - I
label | 0eb417e8-c6f3-58b8-9ce6-33a9fbcc8a53 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Cut Batter
checkpoint-status |  |  | checkpoint | 6.8.1 - Cut Batter Inspections
label | 4d324204-dd12-5e34-b757-a5805d8ba4ae |  | note | Acceptance / Conformance Criteria - The Contractor will need to regularly inspect the exposed soils and check for any seepages that may occur due to the layered profile of the natural soils. All inspection records are to be submitted to the Engineer within 24 hours.
label | 2759f9f1-0521-5f18-9d18-423ac5f16661 |  | note | Standard / Specification - GWS 2.9.6
label | ce5cab41-2c26-5482-96c2-3d22d43139ce |  | note | Verifying Document - Inspection Programme and Records
label | 5c505c18-e993-51f7-949a-5b47156856cc |  | note | Frequency - Submitted to the Engineer within 24 hours.
label | a43347cf-95d7-5b0a-9e04-e6157f5a29d0 |  | note | Verification Activity - H
label | eb00df9a-b10b-5382-9e6b-464ee4e94717 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | Cut Batters- temporary cut
label | 82b32635-e0da-5dbe-96c9-9eb5a24df6f3 |  | note | Acceptance / Conformance Criteria - The temporary cut buffer shall be maintained for 2 weeks to see if the seepage drains out, after which it may be cut to the final profile or additional drainage measures installed subject to review by the Engineer.
label | 73e4728b-5fd1-5e00-a3de-757a7f39c0e9 |  | note | Standard / Specification - GWS 2.9.6
label | d4b60330-816d-503d-8f99-630ff7c072c6 |  | note | Verifying Document - Site Record
label | f141fdc1-eaa1-5721-93e2-10a3bf9531bd |  | note | Frequency - Each Cut Batter
label | 08a7b0a1-3bd6-52cb-a687-8fd6eec5a3ed |  | note | Verification Activity - I
label | b7d155b5-2a16-51db-b7e9-418daa45c1cb |  | note | Verification Activity By - SE/ENG
checkpoint-group |  |  | section | Surcharge Fill
checkpoint-status |  |  | checkpoint | 6.9.1 - Surcharge Fill Installation
label | f8d6420c-f10e-5e92-8f1b-1938b79fc563 |  | note | Acceptance / Conformance Criteria - Surcharge filling shall be placed, spread and track rolled in 300mm layers. Surcharge fill will only be required if the settlement monitoring results exceed what was anticipated in the design. Under Engineer’s direction.
label | bea58f9c-832b-54dd-91d1-7738ce2a1847 |  | note | Standard / Specification - GWS 2.9.7
label | 11e1b7c8-63f1-5b19-b041-37ef1a1a8150 |  | note | Verifying Document - Site Record
label | be46eeb9-b88f-5e12-adb3-e15853fa82ea |  | note | Frequency - Per 300mm layer
label | 89c48506-43db-5c3d-aa52-bf114025d184 |  | note | Verification Activity - I
label | ac13cdb7-dc86-52f2-b78a-f98e874d68bc |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Respread Topsoil
checkpoint-status |  |  | checkpoint | 6.10.1 - Topsoil Respread on Steep Ground
label | 612645e2-276d-5142-9b35-0c856ea5d03c |  | note | Acceptance / Conformance Criteria - On ground steeper than 1V:3H the surface should be roughened under the supervision of the Engineer prior to topsoil placement.
label | 6e7f7b5a-7ed7-5cf2-9964-ab15f2fd2dfc |  | note | Standard / Specification - GWS 2.9.9
label | f6c2c4c1-e3aa-52d0-b069-b8bfb728a650 |  | note | Verifying Document - Site Record
label | 28b6f014-6695-5478-a0ab-d75596c438bf |  | note | Frequency - Prior to topsoil placement
label | 27f50561-beb4-53c0-85fd-f9ca434bb6ec |  | note | Verification Activity - HP
label | b0f3ff82-752c-51a9-aaa9-99a25793f796 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-group |  |  | section | Subsoil Drainage
checkpoint-status |  |  | checkpoint | 6.11.1 - Filter Cloth Wrap Inspection
label | e85fb9f6-7d2b-513a-bd83-0e4c00c9f8d7 |  | note | Acceptance / Conformance Criteria - Observation of the cloth wrap should form an inspection hold point prior to backfilling over the drain.
label | 246d901e-41b6-508b-a982-d57b285d48f6 |  | note | Standard / Specification - GWS 3.2.2
label | 14272c52-0910-574a-8e68-1a008caaea01 |  | note | Verifying Document - Site Record
label | 4b416b83-4d74-5080-9f4a-780e2dd7ea80 |  | note | Frequency - prior to backfilling
label | b07a666c-cab0-5dc9-b74a-e8928840c5da |  | note | Verification Activity - HP
label | 2a503a6b-ecda-532e-8198-34ada9d17cca |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 6.11.2 - Trench Backfill
label | 9be62d94-669d-56c5-98df-f0655e525d22 |  | note | Acceptance / Conformance Criteria - Backfilling of all trenches should be to the fill standard above
label | 9943da35-02d8-5462-9871-d8df0642290e |  | note | Standard / Specification - GWS 3.3
label | 14fbb3eb-8b9a-5333-af1a-fb278cb4f91d |  | note | Verifying Document - Site Record
label | 71250cca-3f46-5d4d-8b23-78956c6b7201 |  | note | Frequency - Each trench
label | 63f9d961-89a4-582b-8e63-ba924b5a4aa5 |  | note | Verification Activity - I
label | e9ff29db-9280-5bcb-8127-113818b5c8f5 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.11.3 - Drainage Outlets and Inspection Points
label | e249ae11-1c7d-5447-bc71-995f46050380 |  | note | Acceptance / Conformance Criteria - At least one temporary flush point is required for each subsoil drainage system to enable flushing of the system once the earthworks are complete.
label | e46ceacf-cb8b-505d-8b15-1dc555be327f |  | note | Standard / Specification - GWS 3.6
label | 85052b17-54d4-5a95-9cbb-ef0d6c71f674 |  | note | Verifying Document - Site Records
label | 5ba4c355-4959-5072-8fd9-0aaf4250d5fb |  | note | Frequency - Each Subsoil Line
label | 8a2d0f43-d8cf-5b99-be4a-77de64ccae73 |  | note | Verification Activity - I
label | ee8b451c-21ab-5f86-ba49-8c33a487de18 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.11.4 - Subsoil Flushing
label | ac40c030-449b-542a-af1b-0220426fe171 |  | note | Acceptance / Conformance Criteria - On completion of earthworks the Contractor shall flush the subsoil drainage system. This must be witnessed by the Engineer.
label | b407e655-141b-5767-955c-3c2aa89b6d64 |  | note | Standard / Specification - GWS 3.6
label | e23d0fc8-d955-5bdd-9a2e-739dea834f0e |  | note | Verifying Document - Site Records
label | 08a98415-27ac-5d92-accf-d6f9681783cf |  | note | Frequency - On completion of earthworks
label | 8c87024e-7a19-523d-9d24-d7539bbdb6c3 |  | note | Verification Activity - HP
label | 4f23f32d-52cd-557e-8dc4-002c5a2eda2c |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 6.11.5 - Survey
label | 157333d0-9f65-58aa-be41-2fc45a3a2cdd |  | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
label | 1b3f7c5e-1e01-5a0e-a9e7-06bc3b3a5f3a |  | note | Standard / Specification - Downer
label | a335245c-0a90-5993-a7e9-27775cd90fca |  | note | Verifying Document - Records
label | ef32fdb5-96c4-5a3f-8230-c5c1f956c7f7 |  | note | Frequency - Post construction
label | 343e4729-0a43-541b-963c-5e036c02f45f |  | note | Verification Activity - H
label | 74b2f7ff-37a5-576d-8c7d-82789d0323f5 |  | note | Verification Activity By - SV
checkpoint-group |  |  | section | Geotextile and Geogrid
checkpoint-status |  |  | checkpoint | 6.12.1 - Geotextile Installation and Lap Length
label | 76225046-1c0e-5471-957a-bb64165abba8 |  | note | Acceptance / Conformance Criteria - All geotextiles shall be placed in accordance with the Manufacturer’s instructions and installed as specified on the drawings. A minimum overlap of 500mm is required between sheets.
label | 66d8fa5b-a442-549a-bea5-c3cb7452c2ad |  | note | Standard / Specification - GWS 4.1
label | de2fd70a-1a13-5c27-a39c-70f8eed0732e |  | note | Verifying Document - Site Records
label | c2acaba6-1ca8-5cac-8371-503ab5be89c7 |  | note | Frequency - Between each sheet
label | 0067de7e-b9fc-5b67-8136-0342c39ff969 |  | note | Verification Activity - I
label | f5d827bb-f426-5371-a150-e95a31726758 |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.12.2 - Geotextile Inspection
label | 5fce79e7-daa5-53c5-ad32-308b9a5bc3c4 |  | note | Acceptance / Conformance Criteria - Before placement of any geotextile should form an Engineers inspection hold point
label | b95f0b90-c3e4-514b-835d-2f189a655d86 |  | note | Standard / Specification - PS 2.2.16
label | f3c2b170-0327-54e3-b456-bc5cc93ab321 |  | note | Verifying Document - Site Records
label | b2d0e962-99a2-5b14-8134-5a715d35b1d2 |  | note | Frequency - Min 48h Notice
label | 4ca5ca69-f231-5784-abee-83eeca3a889b |  | note | Verification Activity - HP
label | a8b167fb-fa63-5a5a-a9b8-2948ec01afe8 |  | note | Verification Activity By - ENG
holdpoint |  |  | signoff | Hold Point (Engineer)
checkpoint-status |  |  | checkpoint | 6.12.3 - Geogrid Prep Inspection
label | 08108f8c-c97e-553e-9698-ffa2ad50e42c |  | note | Acceptance / Conformance Criteria - Prior to placement of the geogrid, verification of the grade, length, orientation and layout is required against the drawings.
label | 5123368d-8f9e-559a-b60f-86578ebb8743 |  | note | Standard / Specification - GWS 4.2
label | 80170ccc-66d3-58b2-b5d7-f14349acad85 |  | note | Verifying Document - Checksheet / Survey
label | 0a1db885-bc81-5f42-85ea-012546cd27bf |  | note | Frequency - Prior to placement
label | d17f58fa-a7fc-5a1b-a210-e9612db174c1 |  | note | Verification Activity - I
label | b5070777-cb7a-5829-bc76-2a395a322d46 |  | note | Verification Activity By - SE
checkpoint-group |  |  | section | Settlement Monitoring
checkpoint-status |  |  | checkpoint | 6.13.1 - Settlement Pin Installation
label | 99a3f15f-8fc2-5bf6-9524-d6389239a71b |  | note | Acceptance / Conformance Criteria - Protective waratahs and coloured flagging shall be installed around all settlement pins for protection. Settlement pins shall be installed within 24 hours of reaching design subgrade level.
label | 2f1d0c7e-7ded-524d-9789-d329ecdea150 |  | note | Standard / Specification - GWS 6.3
label | 7a072403-7d6d-584f-b3d8-2d79756c7e87 |  | note | Verifying Document - Checksheet
label | 248f1536-fe7a-5a91-887f-1bd1ed65900a |  | note | Frequency - within 24 hours of reaching design subgrade level.
label | b4f59ffe-eb6b-5ea4-80c8-cf2ba8ab3538 |  | note | Verification Activity - C
label | 0cef5e12-9dee-51e8-b40d-6b3fb1589e5d |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 6.13.2 - Settlement Survey
label | 112e7f80-767f-5636-946f-3932d2c8e479 |  | note | Acceptance / Conformance Criteria - Survey measurements are to be undertaken regularly by the Contractor as specified on the drawings, to within an accuracy of 2mm. Results must be provided to the Engineer within 24 hours of each reading.
label | 212ea4ee-e52a-546b-808c-745bac8d928a |  | note | Standard / Specification - GWS 6.3
label | f1489eab-003c-5a56-a03f-13ad0877b9b2 |  | note | Verifying Document - Both paper and electronic formats
label | 571d823b-77b5-53aa-8f3b-cc51567a9717 |  | note | Frequency - within 24 hours of each reading.
label | d4b9d21a-a50a-5a45-8ad8-0771fa0b609e |  | note | Verification Activity - H
label | 539fae9f-0f46-5cb7-ac3e-84c6f799cda3 |  | note | Verification Activity By - SV/SE
checkpoint-status |  |  | checkpoint | 6.13.3 - Retaining Wall Settlement Targets
label | b493ddef-686b-59cb-a6fa-20ce8a77e630 |  | note | Acceptance / Conformance Criteria - Targets shall be fixed immediately after completion of the first row of retaining wall blocks at each location and the initial baseline survey reading made prior to the subsequent row of retaining wall blocks placed.
label | 3eeed169-5910-546d-849f-0c6770ded3bc |  | note | Standard / Specification - GWS 6.4
label | 4fa0ca17-2e43-50c7-8881-fe23558af58b |  | note | Verifying Document - Checksheet
label | 90ae0198-a4e3-5455-90ed-a258561cd1fc |  | note | Frequency - prior & after completion of first row of retaining blocks
label | be7c7a7f-d127-535b-ad98-78270c9a6907 |  | note | Verification Activity - I
label | a8e6571c-2ea6-520b-b643-50014469a9b8 |  | note | Verification Activity By - SV/SE
checkpoint-group |  |  | section | SECTION 8 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - Site Post Construction Activities
checkpoint-status |  |  | checkpoint | 8.1.1 - Construction Record Compilation
label | 9e865959-c88a-5190-9f5f-9aead8c19ce6 |  | note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
label | f4dfd5a4-d771-5aff-a69f-4c87ca9911bb |  | note | Standard / Specification - Downer
label | 89b72ad1-0a2c-5e13-a797-a0d4a5b77ccf |  | note | Verifying Document - Records
label | 855af0eb-08d2-530f-a975-5f08114d94c3 |  | note | Frequency - Post construction
label | 0c644f99-c56e-54d0-b27f-54f286afe727 |  | note | Verification Activity - H
label | 271d3bf3-544b-50e2-a020-72c91450dfda |  | note | Verification Activity By - SE
checkpoint-status |  |  | checkpoint | 8.1.2 - Survey Records
label | e04a5f03-809c-5321-856b-6c14bbe078c7 |  | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting including, initial subgrade level, all undercuts, all test location points, and final level
label | ea054228-80af-5478-8e11-c723f5ec1539 |  | note | Standard / Specification - Downer
label | fcc41489-f8ba-5261-96c6-b0f25fa9d847 |  | note | Verifying Document - Records
label | 0e8d161d-391b-5bc0-a9cf-621caa90b000 |  | note | Frequency - Post construction
label | 606b5e65-7591-5355-8b6f-2c9e2ee4738f |  | note | Verification Activity - H
label | a10d33be-0636-5363-b915-0104e692bbbe |  | note | Verification Activity By - SV
checkpoint-status |  |  | checkpoint | 8.1.3 - Redline Drawings
label | c8dc263f-8b1e-52a7-beee-97d562069bee |  | note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
label | e3d9d811-9f48-50aa-ad2d-fbcb143b84ad |  | note | Standard / Specification - Downer
label | c8d3d189-33f3-5e6e-a349-a2f6a1c86fce |  | note | Verifying Document - Redlines
label | bb6a84e8-3c2f-500a-8396-acf0711ef71f |  | note | Frequency - Post construction
label | fbb1edf2-dd6f-53ab-abb0-02caa90ae961 |  | note | Verification Activity - H
label | c8c2a577-65bf-5aed-9279-6ba112957dfc |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 8.1.4 - Defect, Snag and Punch List
label | cabd4ab6-3f8c-56a6-85c9-b1978f83c065 |  | note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
label | 10adea13-6583-56cf-a47a-74e52be060f2 |  | note | Standard / Specification - Downer
label | ff84c247-59ba-58d6-ab15-87cde05db7b7 |  | note | Verifying Document - Register
label | 7c100c2c-f6d9-5eb5-8a7c-7402ea3850ee |  | note | Frequency - Post construction
label | a81e1351-5432-54e8-9e31-499cb6261f99 |  | note | Verification Activity - H
label | 6924f01b-f7f3-51bf-a1e7-f2c5e75d1ab0 |  | note | Verification Activity By - PE
checkpoint-status |  |  | checkpoint | 8.1.5 - Photos
label | 94e37964-f4ea-55f7-843c-d9cff1cab647 |  | note | Acceptance / Conformance Criteria - Minimum subgrade, undercuts, all service ducting/pipe lines immediately before backfill, warning tape / mag slabs immediately before backfill.
label | 4bbb697c-8d21-5a96-8dda-190c8bb6e3e5 |  | note | Standard / Specification - Downer
label | 613458d8-44b8-5f7b-aa36-ddd3ce4f2886 |  | note | Verifying Document - Photo Records
label | 706b1d90-4936-5f76-ab5e-a6ac12da6b19 |  | note | Frequency - Post construction
label | 88958877-a040-53a7-a425-18f857a2b216 |  | note | Verification Activity - H
label | b80fc67a-8a18-5aef-addc-224f7da47377 |  | note | Verification Activity By - SE