## Master
|  |  |  | Project: | Project Kuiper |  |  | Lot Number
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
1 | Project Start Up
1.1 | Contract Agreement | H | Signed contract agreement | A copy of the contract agreement has been reviewed, agreed and signed by both parties | Once | Documents | Signed Agreement | Construction services Schedule | Cedric Senkel
1.2 | Contract Management Plan | H | Approved Contract Management Plan | An approved copy of the contract specific management plan is received and kept on site | Once and updated as required | Documents | Approved CMP | Construction services Schedule | Cedric Senkel
1.3 | Construction Drawings | H | Full set of FOR CONSTRUCTION Drawings | A full and final set of For Construction drawing is received and entered into project drawing register. Register is updated as required | Once | Documents | Construction Drawings | Construction services Schedule | Cedric Senkel
1.4 | Resource Consent | H | Approved Resource Consent | An approved resource consent has been received from the relevant regulatory authority for the construction of the contract works | Once | Documents | Approved Consent | Construction services Schedule | Michael Harley
1.5 | Electronic design data | H | current and up to date electronic design data | A full set of design data files are supplied to allow for set out and machine control models to be created | Once | File Transfer | Design Data Files | N/A | Michael Harley
1.6 | Insurances | H | Insurance Certificates | A set of current and in date insurance certificates are supplied. | Once | Documents | Current Insurance Certs | Construction services Schedule | Cedric Senkel
1.7 | Construction Program | H | Construction program | An accepted construction program has been supplied showing start and finished dates, duration and critical path for the contract works | Once and updated weekly | Documents | Approved Construction Program | Construction services Schedule | Cedric Senkel
1.8 | Pre-Construction Photos | H | Photograph the site | Photograph the site prior to construction starting | Once | Inspection | Photos | Construction services Schedule | Michael Harley
1.9 | Daily Reporting | W | Provide daily progress reports | Provide daily progress reports showing % complete, weather conditions, photos and descriptions of the work, number of workers on site, type and number of plant items on site, problems encountered and any other relevant data | On-Going | Capture all info on DJR's | DJR | Construction services Schedule | Michael Harley
2 | Site Establishment
2.1 | Erosion and sediment control installation | H | Install effective silt and sediment controls | Install silt fencing and water diversion bund as per contract erosion and sediment control plan | Once | Inspection | Photos | Contract drawings - 0350 & 0351 | Chad Ellis
2.2 | Erosion and sediment control maintenance | M | Monitor effectiveness of, and repair damage to silt control measures | Prior to, during and after rain fall exceeding 25mm/day, check silt control measures and monitor effectiveness of the controls. Carry out any repairs/modification as required | On-going | Inspection | Photos | Contract drawings - 0350 & 0351 | Chad Ellis
2.3 | Site security | H | Security Fencing | Set up security fencing 1.8m high to provide a secure compound to store plant and materials. | Once | Inspection | Photos | N/A | Chad Ellis
3 | Site Survey
3.1 | Levels check | H | Check existing ground levels and control points | Check existing or install new survey control points. Survey existing ground levels and compare to design levels | Once | Measure | Survey Data | Design Data | Michael Harley
3.2 | Site control and set out | H | Setout Contract works | Setout key points of the contract works to allow for accurate levels and positions of all elements | Once | Measure | Survey Data | Design Data | Michael Harley
3.3 | Machine control model | W | IF REQUIRED - Build machine control model for the contract works | Build a model of design surfaces that can be utilised with machine control plant (excavator, grader) | Once | Measure | Survey Data | Design Data | Michael Harley
3.4 | As-built Pick-up | M | Record all construction works | Pickup all elements as constructed - finished levels, ducting, concrete foundations, fencing etc | On-Going | Measure | Survey Data | Construction services Schedule | Michael Harley
3.5 | As-built drawings and data | H | Produce as-built drawing set | Provide a set of as-built drawings and data as required by client | Once | File Transfer | Survey Data | Construction services Schedule | Michael Harley
4 | Compound Earthworks
4.1 | Site grading | H | Site is to be graded so water falls away from compound | Grade surrounding ground level so water flows away from compound | Once | Measure | Survey Pickup | Construction services Schedule | Michael Harley
4.2 | Subgrade CBR | H | Test Subgrade CBR | Subgrade must be a minimum CBR value of 3% The subgrade is to be proof rolled and any deflection greater than 25mm should be rectified | Once | Test | Test report | Contract Drawing - 0460 GGT Hosting Spec Section 1.6 | Cedric Senkel
4.3 | Geotextile | H | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Supplier Dockets | Contract Drawing - 0460 | Michael Harley
4.4 | GAP65 Basecourse | W | Grading | Aggregate must be graded as a GAP65 | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.5 | GAP65 Basecourse | W | MDD and OMC | Lab test to determine the MDD and OMC of the GAP65 Aggregate | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.6 | GAP65 Basecourse | H | Layer surface | Top of GAP65 surface should be 100mm below FL | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
4.7 | GAP65 Basecourse | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Mean 95%, Min 92% | 1 test per 20m2 | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.8 | AP20 Running Course | W | Grading | Aggregate must be graded as a AP20 | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.9 | AP20 Running Course | W | MDD and OMC | Lab test to determine the MDD and OMC of the AP20 Aggregate | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.1 | AP20 Running Course | H | Layer surface | Top surface should be at FL | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
4.11 | AP20 Running Course | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Mean 98%, Min 92% | 1 test per 20m2 | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.12 | Compound extents | W | Gravel compound size and batter slops | Top surface of compound must extend minimum 500mm past fence location and slope 1:3 to existing ground level | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
5 | Trenching, Ducts and Cable Trays
5.1 | Trench locations | H | Trench and ducting routes, Concrete protrusions | The trenching an cable routes are to be marked out on site and checked. Protrusions into concrete slab foundations are to be set out | Once | Measure | Survey Pickup | Contract Drawing - 0602 | Michael Harley
5.2 | Trench depth | H | Trench to be excavated to required depth | trenches are to be 850mm deep from design FL and 300mm wide | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.3 | Duct installation | W | Power and fibre duct installation depth | Power ducts to be 800mm and fibre ducts to be 600mm minimum below design FL | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.4 | Warning Tape | W | Warning tape location | Warning tape is to be 450mm below design FL | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.5 | TUDS Pits - Size and lid rating | W | Correct size and ratings | Power and fibre pits to be a minimum of 0.59m2 (750x1200) and security pit to be a minimum of 0.45m2 (450x450) and all lids to be class D and bolted down | Once | Documents | Supplier dockets | Contract Drawing - 0463 | Michael Harley
5.6 | TUDS Pits - Locations | H | Locations are correct | Setout pit locations prior to trenching | Once | Measure | Survey Pickup | Contract Drawing - 0602 | Chad Ellis
5.7 | H-Frame Foundations - Depth | H | Foundations are to the correct depth and size | Augered holes need to be a depth of 1220mm and a diameter of 460mm | Once | Measure | Photos | Contract Drawing - 0463 | Chad Ellis
5.8 | H-Frame Foundations - Concrete | H | Concrete strength | Holes to be backfilled with 25MPa concrete, poles are to be spaced 100mm from the base of the excavation | Once | Test | Delivery Docket and Lab Testing | Contract Drawing - 0463 | Chad Ellis
6 | Antenna Foundations
6.1 | Excavation Depth and Size | H | Excavation must be deep and large enough. | Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.2 | Geotextile | W | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Delivery docket | Contract Drawing - 0450 | Michael Harley
6.3 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.4 | Gap40 Basecourse | H | MDD and OMC | Lab test to determine the MDD and OMC of the GAP40 Aggregate | Once | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.5 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 300mm thick, extend 600mm around the foundation of all side and lift 400mm above base of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.6 | Gap40 Basecourse | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Min 98% MDD | 2 tests per foundation | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.7 | Reinforcing Steel | H | Size and Grade | HD20 (Grade 500) for top and bottom bars, HD10 (Grade 500) for link legs | Once | Inspection | Delivery Dockets | Contract Drawing - 0450 | Michael Harley
6.8 | Reinforcing Steel | H | Spacing and Cover | 200mm centres for top and bottom bars, and 400mm centres for link legs 75mm cover, top, sides and bottom | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0450 | Cedric Senkel
6.9 | Duct Protrusions | H | Location for Protrusions | Ducts for KAA Power and Communications must protrude on the left side of bolt 7 and stay between bolts 6&7. Ducts must protrude outside of the 600mm keep out zone. | Once | Measure | Survey Pickup and photos | Contract Drawing - 0450 & 0602 | Chad Ellis
6.1 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0450 | Michael Harley
6.11 | Concrete | W | Strength | 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders per load delivered | 2 cylinders per load | Lab Test | Test reports, delivery dockets | Contract Drawing - 0450 GGT Hosting Spec GGT-1501 | Cedric Senkel
6.12 | Concrete | W | Finish | Finish surface to be U3, Broom finish with a 25mm chamfer on all exposed edges | Once | Inspection | Photos | Contract Drawing - 0450 | Chad Ellis
6.13 | Anchor Bolt Kits | H | Alignment | Bolts to be numbers 1 to 8 clockwise around foundation. Bolts 1 and 5 must be aligned with long fence azimuth | Once | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.14 | Anchor Bolt Kits | H | Embedment Depth | Anchor bolts must be embedded a minimum of 265mm and protrude from the top surface by a minimum of 120mm | once | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
7 | GWSE Foundation Slab
7.1 | Excavation Depth and Size | H | Excavation must be deep and large enough. | Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.2 | Geotextile | W | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Delivery docket | Contract Drawing - 0463 | Michael Harley
7.3 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0463 | Cedric Senkel
7.4 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad | Once | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.5 | Reinforcing Steel | H | Size and Grade | HD16 (Grade 500) for top and bottom bars | Once | Inspection | Delivery Dockets | Contract Drawing - 0463 | Michael Harley
7.6 | Reinforcing Steel | H | Spacing and Cover | 200mm centres for top and bottom bars both ways 75mm cover, top, sides and bottom | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0463 | Cedric Senkel
7.7 | Duct Protrusions | H | Location for Protrusions | There are 8 duct protrusions detailed in the contract drawings, 3 x power, 3 x fibre, 1 x generator controls and 1 x earth | Once | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.8 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0463 | Michael Harley
7.9 | Concrete | W | Strength | 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery | 2 cylinders | Lab Test | Test reports, delivery dockets | Contract Drawing - 0463 GGT Hosting Spec GGT-1501 | Cedric Senkel
7.1 | Concrete | W | Finish | Finish surface to be U3, Broom finish on all exposed concrete, trowel finish for area under cabinet. There must be a 25mm chamfer on all exposed edges and 1% fall away from concrete of pad. | Once | Inspection | Photos | Contract Drawing - 0463 | Chad Ellis
8 | Generator and Fibre Enclosure Pads
8.1 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0460 | Cedric Senkel
8.2 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
8.3 | Reinforcing Steel | H | Size and Grade | SE72 Mesh | Once | Inspection | Delivery Dockets | Contract Drawing - 0460 | Michael Harley
8.4 | Reinforcing Steel | H | Spacing and Cover | Two layers of Mesh for generator pad, single layer for fibre enclosure. 75mm cover from bottom, 50mm cover from top | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0460 | Cedric Senkel
8.5 | Duct Protrusions | H | Location for Protrusions | TBC | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
8.6 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0460 GGT Hosting Spec GGT-1501 | Michael Harley
8.7 | Concrete | W | Strength | 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery | 2 cylinders | Lab Test | Test reports, delivery dockets | Contract Drawing - 0460 GGT Hosting Spec GGT-1501 | Cedric Senkel
8.8 | Concrete | W | Finish | Finish surface to be U3, Broom finish. There must be a 25mm chamfer on all exposed edges. | Once | Inspection | Photos | Contract Drawing - 0460 | Chad Ellis
9 | Security and Acoustic Fence
9.1 | Fence Placement | H | Fence must be in correct location | Fence line will be set out by survey prior to post hole excavation | Once | Measure | Survey Pickup and photos | Contract drawings - 0401, 0405 & 0800-0808 | Michael Harley
9.2 | Post Hole | H | Diameter and Depth | All Post Holes are to be 450mm diameter Gate posts, corner posts and the first two posts in from each corner post must be 1.8m deep. All other intermediate posts and timer fence posts must be 1.2m deep | Once | Measure | Survey Pickup and photos | Contract drawings - 0405, 0464 & 0800-0809 | Chad Ellis
9.3 | Post Hole | H | Spacing | Security Fence post holes to be 2.5m apart Acoustic Fence posts to be 1.2m apart | Once | Measure | Survey Pickup and photos | Contract drawings - 0405, 0464 & 0800-0809 | Chad Ellis
9.4 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery Docket | GGT Hosting Spec GGT-1501 | Michael Harley
9.5 | Concrete | W | Strength | 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from each delivery load | 2 Cylinders from each load | Test | Lab Test Report | GGT Hosting Spec GGT-1501 | Cedric Senkel
9.6 | Timber | H | Size and treatment of timber | Posts - 90x90 H4 Rails - 90x70 H2.3 Vertical Boards - 240x25 H2.3 | Once | Inspection | Delivery Dockets | Contract Drawing - 0464 | Chad Ellis
9.7 | Fence Alignment | W | Post and Fence Alignment | Fence posts must be vertical and in a straight line | Once | Inspection | Survey Pickup and photos | Contract drawings - 0401, 0405, 0464 & 0800-0809 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 1.0.0 Establishment and Survey
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 1.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
2 | Site Establishment
2.1 | Erosion and sediment control installation | H | Install effective silt and sediment controls | Install silt fencing and water diversion bund as per contract erosion and sediment control plan | Once | Inspection | Photos | Contract drawings - 0350 & 0351 | Chad Ellis
2.2 | Erosion and sediment control maintenance | M | Monitor effectiveness of, and repair damage to silt control measures | Prior to, during and after rain fall exceeding 25mm/day, check silt control measures and monitor effectiveness of the controls. Carry out any repairs/modification as required | On-going | Inspection | Photos | Contract drawings - 0350 & 0351 | Chad Ellis
2.3 | Site security | H | Security Fencing | Set up security fencing 1.8m high to provide a secure compound to store plant and materials. | Once | Inspection | Photos | N/A | Chad Ellis
3 | Site Survey
3.1 | Levels check | H | Check existing ground levels and control points | Check existing or install new survey control points. Survey existing ground levels and compare to design levels | Once | Measure | Survey Data | Design Data | Michael Harley
3.2 | Site control and set out | H | Setout Contract works | Setout key points of the contract works to allow for accurate levels and positions of all elements | Once | Measure | Survey Data | Design Data | Michael Harley
3.3 | Machine control model | W | IF REQUIRED - Build machine control model for the contract works | Build a model of design surfaces that can be utilised with machine control plant (excavator, grader) | Once | Measure | Survey Data | Design Data | Michael Harley
3.4 | As-built Pick-up | M | Record all construction works | Pickup all elements as constructed - finished levels, ducting, concrete foundations, fencing etc | On-Going | Measure | Survey Data | Construction services Schedule | Michael Harley
3.5 | As-built drawings and data | H | Produce as-built drawing set | Provide a set of as-built drawings and data as required by client | Once | File Transfer | Survey Data | Construction services Schedule | Michael Harley
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 2.0.0 Compound Earthworks
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 2.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
4 | Compound Earthworks
4.1 | Site grading | H | Site is to be graded so water falls away from compound | Grade surrounding ground level so water flows away from compound | Once | Measure | Survey Pickup | Construction services Schedule | Michael Harley
4.2 | Subgrade CBR | H | Test Subgrade CBR | Subgrade must be a minimum CBR value of 3% The subgrade is to be proof rolled and any deflection greater than 25mm should be rectified | Once | Test | Test report | Contract Drawing - 0460 GGT Hosting Spec Section 1.6 | Cedric Senkel
4.3 | Geotextile | H | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Supplier Dockets | Contract Drawing - 0460 | Michael Harley
4.4 | GAP65 Basecourse | W | Grading | Aggregate must be graded as a GAP65 | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.5 | GAP65 Basecourse | W | MDD and OMC | Lab test to determine the MDD and OMC of the GAP65 Aggregate | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.6 | GAP65 Basecourse | H | Layer surface | Top of GAP65 surface should be 100mm below FL | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
4.7 | GAP65 Basecourse | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Mean 95%, Min 92% | 1 test per 20m2 | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.8 | AP20 Running Course | W | Grading | Aggregate must be graded as a AP20 | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.9 | AP20 Running Course | W | MDD and OMC | Lab test to determine the MDD and OMC of the AP20 Aggregate | Once | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.1 | AP20 Running Course | H | Layer surface | Top surface should be at FL | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
4.11 | AP20 Running Course | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Mean 98%, Min 92% | 1 test per 20m2 | Test | Lab Test Report | Contract Drawing - 0460 | Cedric Senkel
4.12 | Compound extents | W | Gravel compound size and batter slops | Top surface of compound must extend minimum 500mm past fence location and slope 1:3 to existing ground level | Once | Measure | Survey Pickup | Contract Drawing - 0460 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 3.0.0 Trenching and Ducts
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 3.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
5 | Trenching, Ducts and Cable Trays
5.1 | Trench locations | H | Trench and ducting routes, Concrete protrusions | The trenching an cable routes are to be marked out on site and checked. Protrusions into concrete slab foundations are to be set out | Once | Measure | Survey Pickup | Contract Drawing - 0602 | Michael Harley
5.2 | Trench depth | H | Trench to be excavated to required depth | trenches are to be 850mm deep from design FL and 300mm wide | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.3 | Duct installation | W | Power and fibre duct installation depth | Power ducts to be 800mm and fibre ducts to be 600mm minimum below design FL | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.4 | Warning Tape | W | Warning tape location | Warning tape is to be 450mm below design FL | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
5.5 | TUDS Pits - Size and lid rating | W | Correct size and ratings | Power and fibre pits to be a minimum of 0.59m2 (750x1200) and security pit to be a minimum of 0.45m2 (450x450) and all lids to be class D and bolted down | Once | Documents | Supplier dockets | Contract Drawing - 0463 | Michael Harley
5.6 | TUDS Pits - Locations | H | Locations are correct | Setout pit locations prior to trenching | Once | Measure | Survey Pickup | Contract Drawing - 0602 | Chad Ellis
5.7 | H-Frame Foundations - Depth | H | Foundations are to the correct depth and size | Augered holes need to be a depth of 1220mm and a diameter of 460mm | Once | Measure | Photos | Contract Drawing - 0463 | Chad Ellis
5.8 | H-Frame Foundations - Concrete | H | Concrete strength | Holes to be backfilled with 25MPa concrete, poles are to be spaced 100mm from the base of the excavation | Once | Test | Delivery Docket and Lab Testing | Contract Drawing - 0463 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 4.0.0 Antenna Foundations
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 4.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
6 | Antenna Foundations
6.1 | Excavation Depth and Size | H | Excavation must be deep and large enough. | Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.2 | Geotextile | W | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Delivery docket | Contract Drawing - 0450 | Michael Harley
6.3 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.4 | Gap40 Basecourse | H | MDD and OMC | Lab test to determine the MDD and OMC of the GAP40 Aggregate | Once | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.5 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 300mm thick, extend 600mm around the foundation of all side and lift 400mm above base of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.6 | Gap40 Basecourse | H | NDM Testing | Compaction testing using a NDM to confirm degree of compaction - Min 98% MDD | 2 tests per foundation | Lab Test | Testing report | Contract Drawing - 0450 | Cedric Senkel
6.7 | Reinforcing Steel | H | Size and Grade | HD20 (Grade 500) for top and bottom bars, HD10 (Grade 500) for link legs | Once | Inspection | Delivery Dockets | Contract Drawing - 0450 | Michael Harley
6.8 | Reinforcing Steel | H | Spacing and Cover | 200mm centres for top and bottom bars, and 400mm centres for link legs 75mm cover, top, sides and bottom | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0450 | Cedric Senkel
6.9 | Duct Protrusions | H | Location for Protrusions | Ducts for KAA Power and Communications must protrude on the left side of bolt 7 and stay between bolts 6&7. Ducts must protrude outside of the 600mm keep out zone. | Once | Measure | Survey Pickup and photos | Contract Drawing - 0450 & 0602 | Chad Ellis
6.1 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0450 | Michael Harley
6.11 | Concrete | W | Strength | 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders per load delivered | 2 cylinders per load | Lab Test | Test reports, delivery dockets | Contract Drawing - 0450 GGT Hosting Spec GGT-1501 | Cedric Senkel
6.12 | Concrete | W | Finish | Finish surface to be U3, Broom finish with a 25mm chamfer on all exposed edges | Once | Inspection | Photos | Contract Drawing - 0450 | Chad Ellis
6.13 | Anchor Bolt Kits | H | Alignment | Bolts to be numbers 1 to 8 clockwise around foundation. Bolts 1 and 5 must be aligned with long fence azimuth | Once | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
6.14 | Anchor Bolt Kits | H | Embedment Depth | Anchor bolts must be embedded a minimum of 265mm and protrude from the top surface by a minimum of 120mm | once | Measure | Survey Pickup and photos | Contract Drawing - 0450 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 5.0.0 GWSE Foundation
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 5.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
7 | GWSE Foundation Slab
7.1 | Excavation Depth and Size | H | Excavation must be deep and large enough. | Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides | once for each foundation | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.2 | Geotextile | W | Geotextile Strength Class | Geotextile must be a minimum of strength class D | Once | Inspection | Delivery docket | Contract Drawing - 0463 | Michael Harley
7.3 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0463 | Cedric Senkel
7.4 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad | Once | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.5 | Reinforcing Steel | H | Size and Grade | HD16 (Grade 500) for top and bottom bars | Once | Inspection | Delivery Dockets | Contract Drawing - 0463 | Michael Harley
7.6 | Reinforcing Steel | H | Spacing and Cover | 200mm centres for top and bottom bars both ways 75mm cover, top, sides and bottom | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0463 | Cedric Senkel
7.7 | Duct Protrusions | H | Location for Protrusions | There are 8 duct protrusions detailed in the contract drawings, 3 x power, 3 x fibre, 1 x generator controls and 1 x earth | Once | Measure | Survey Pickup and photos | Contract Drawing - 0463 | Chad Ellis
7.8 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0463 | Michael Harley
7.9 | Concrete | W | Strength | 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery | 2 cylinders | Lab Test | Test reports, delivery dockets | Contract Drawing - 0463 GGT Hosting Spec GGT-1501 | Cedric Senkel
7.1 | Concrete | W | Finish | Finish surface to be U3, Broom finish on all exposed concrete, trowel finish for area under cabinet. There must be a 25mm chamfer on all exposed edges and 1% fall away from concrete of pad. | Once | Inspection | Photos | Contract Drawing - 0463 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 6.0.0 Generator Pad
|  |  |  | Project: | Project Kuiper |  |  | Lot Number |  | 6.0.0
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
8 | Generator and Fibre Enclosure Pads
8.1 | Gap40 Basecourse | W | Grading | Aggregate must be graded as a GAP40 | Once | Lab Test | Testing report | Contract Drawing - 0460 | Cedric Senkel
8.2 | Gap40 Basecourse | W | Layer thickness | AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
8.3 | Reinforcing Steel | H | Size and Grade | SE72 Mesh | Once | Inspection | Delivery Dockets | Contract Drawing - 0460 | Michael Harley
8.4 | Reinforcing Steel | H | Spacing and Cover | Two layers of Mesh for generator pad, single layer for fibre enclosure. 75mm cover from bottom, 50mm cover from top | Once | Inspection | Pre-pour Checklist, Photos | Contract Drawing - 0460 | Cedric Senkel
8.5 | Duct Protrusions | H | Location for Protrusions | TBC | Once | Measure | Survey Pickup and photos | Contract Drawing - 0460 | Chad Ellis
8.6 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery docket | Contract Drawing - 0460 GGT Hosting Spec GGT-1501 | Michael Harley
8.7 | Concrete | W | Strength | 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery | 2 cylinders | Lab Test | Test reports, delivery dockets | Contract Drawing - 0460 GGT Hosting Spec GGT-1501 | Cedric Senkel
8.8 | Concrete | W | Finish | Finish surface to be U3, Broom finish. There must be a 25mm chamfer on all exposed edges. | Once | Inspection | Photos | Contract Drawing - 0460 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________

## 7.0.0 Fencing
|  |  |  | Project: | Project Kuiper |  |  | Lot Number
|  |  |  | Project Location | 9-17 Boxman Place |  |  | Scope Of ITP |  | Project QA Requirements
|  |  |  | Job # | 4405127 |  |  | Sub Contractor
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Supervisor |  | Chad Ellis
| Action | W | Witness | Requiring Designer Representative |  | Project Engineer |  | Cedric Senkel
|  | H | Hold Point | Requiring Sub-contractor Representative |  | Sub-Contractor Representative |  | N/A
|  | M | Monitor | Requiring Fulton Hogan Manager Representative |  | FH Job Manager |  | Michael Harley
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | CSS/IDS/ASNZS Standard | Signatory | Date(s) | Signature
9 | Security and Acoustic Fence
9.1 | Fence Placement | H | Fence must be in correct location | Fence line will be set out by survey prior to post hole excavation | Once | Measure | Survey Pickup and photos | Contract drawings - 0401, 0405 & 0800-0808 | Michael Harley
9.2 | Post Hole | H | Diameter and Depth | All Post Holes are to be 450mm diameter Gate posts, corner posts and the first two posts in from each corner post must be 1.8m deep. All other intermediate posts and timer fence posts must be 1.2m deep | Once | Measure | Survey Pickup and photos | Contract drawings - 0405, 0464 & 0800-0809 | Chad Ellis
9.3 | Post Hole | H | Spacing | Security Fence post holes to be 2.5m apart Acoustic Fence posts to be 1.2m apart | Once | Measure | Survey Pickup and photos | Contract drawings - 0405, 0464 & 0800-0809 | Chad Ellis
9.4 | Concrete | W | Mix | Maximum aggregate size of 19mm | Once | Inspection | Delivery Docket | GGT Hosting Spec GGT-1501 | Michael Harley
9.5 | Concrete | W | Strength | 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from each delivery load | 2 Cylinders from each load | Test | Lab Test Report | GGT Hosting Spec GGT-1501 | Cedric Senkel
9.6 | Timber | H | Size and treatment of timber | Posts - 90x90 H4 Rails - 90x70 H2.3 Vertical Boards - 240x25 H2.3 | Once | Inspection | Delivery Dockets | Contract Drawing - 0464 | Chad Ellis
9.7 | Fence Alignment | W | Post and Fence Alignment | Fence posts must be vertical and in a straight line | Once | Inspection | Survey Pickup and photos | Contract drawings - 0401, 0405, 0464 & 0800-0809 | Chad Ellis
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________