## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Project Start Up | itp |  |  |  |  | ITP - Project Start Up
section | 1.0 - Project Start Up
checkpoint | 1.1 - Contract Agreement
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Signed contract agreement
label | DETAIL - A copy of the contract agreement has been reviewed, agreed and signed by both parties
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Signed Agreement
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Contract Management Plan
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Approved Contract Management Plan
label | DETAIL - An approved copy of the contract specific management plan is received and kept on site
label | FREQUENCY - Once and updated as required
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Approved CMP
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Construction Drawings
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Full set of FOR CONSTRUCTION Drawings
label | DETAIL - A full and final set of For Construction drawing is received and entered into project drawing register. Register is updated as required
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Construction Drawings
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Resource Consent
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Approved Resource Consent
label | DETAIL - An approved resource consent has been received from the relevant regulatory authority for the construction of the contract works
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Approved Consent
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Electronic design data
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - current and up to date electronic design data
label | DETAIL - A full set of design data files are supplied to allow for set out and machine control models to be created
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - File Transfer
label | VERIFICATION RECORDS - Design Data Files
label | CSS/IDS/ASNZS STANDARD - N/A
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Insurances
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Insurance Certificates
label | DETAIL - A set of current and in date insurance certificates are supplied.
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Current Insurance Certs
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Construction Program
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Construction program
label | DETAIL - An accepted construction program has been supplied showing start and finished dates, duration and critical path for the contract works
label | FREQUENCY - Once and updated weekly
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Approved Construction Program
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.8 - Pre-Construction Photos
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Photograph the site
label | DETAIL - Photograph the site prior to construction starting
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.9 - Daily Reporting
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Provide daily progress reports
label | DETAIL - Provide daily progress reports showing % complete, weather conditions, photos and descriptions of the work, number of workers on site, type and number of plant items on site, problems encountered and any other relevant data
label | FREQUENCY - On-Going
label | INSPECTION / TEST METHOD - Capture all info on DJR's
label | VERIFICATION RECORDS - DJR
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
checklist | ITP - 1.0.0 Establishment and Survey | itp |  |  |  |  | ITP - 1.0.0 Establishment and Survey
section | 2.0 - Site Establishment
checkpoint | 2.1 - Erosion and sediment control installation
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Install effective silt and sediment controls
label | DETAIL - Install silt fencing and water diversion bund as per contract erosion and sediment control plan
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0350 & 0351
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Erosion and sediment control maintenance
label | ACTION (W, M, H) - M
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Monitor effectiveness of, and repair damage to silt control measures
label | DETAIL - Prior to, during and after rain fall exceeding 25mm/day, check silt control measures and monitor effectiveness of the controls. Carry out any repairs/modification as required
label | FREQUENCY - On-going
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0350 & 0351
label | SIGNATORY - Chad Ellis
checkpoint | 2.3 - Site security
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Security Fencing
label | DETAIL - Set up security fencing 1.8m high to provide a secure compound to store plant and materials.
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - N/A
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 - Site Survey
checkpoint | 3.1 - Levels check
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Check existing ground levels and control points
label | DETAIL - Check existing or install new survey control points. Survey existing ground levels and compare to design levels
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Data
label | CSS/IDS/ASNZS STANDARD - Design Data
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Site control and set out
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Setout Contract works
label | DETAIL - Setout key points of the contract works to allow for accurate levels and positions of all elements
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Data
label | CSS/IDS/ASNZS STANDARD - Design Data
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Machine control model
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - IF REQUIRED - Build machine control model for the contract works
label | DETAIL - Build a model of design surfaces that can be utilised with machine control plant (excavator, grader)
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Data
label | CSS/IDS/ASNZS STANDARD - Design Data
label | SIGNATORY - Michael Harley
checkpoint | 3.4 - As-built Pick-up
label | ACTION (W, M, H) - M
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Record all construction works
label | DETAIL - Pickup all elements as constructed - finished levels, ducting, concrete foundations, fencing etc
label | FREQUENCY - On-Going
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Data
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
checkpoint | 3.5 - As-built drawings and data
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Produce as-built drawing set
label | DETAIL - Provide a set of as-built drawings and data as required by client
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - File Transfer
label | VERIFICATION RECORDS - Survey Data
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 2.0.0 Compound Earthworks | itp |  |  |  |  | ITP - 2.0.0 Compound Earthworks
section | 4.0 - Compound Earthworks
checkpoint | 4.1 - Site grading
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Site is to be graded so water falls away from compound
label | DETAIL - Grade surrounding ground level so water flows away from compound
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Construction services Schedule
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Subgrade CBR
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Test Subgrade CBR
label | DETAIL - Subgrade must be a minimum CBR value of 3%
label | ○ The subgrade is to be proof rolled and any deflection greater than 25mm should be rectified
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Test report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460, GGT Hosting Spec Section 1.6
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Geotextile
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Geotextile Strength Class
label | DETAIL - Geotextile must be a minimum of strength class D
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Supplier Dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - GAP65 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Grading
label | DETAIL - Aggregate must be graded as a GAP65
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
checkpoint | 4.5 - GAP65 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - MDD and OMC
label | DETAIL - Lab test to determine the MDD and OMC of the GAP65 Aggregate
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
checkpoint | 4.6 - GAP65 Basecourse
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Layer surface
label | DETAIL - Top of GAP65 surface should be 100mm below FL
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.7 - GAP65 Basecourse
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - NDM Testing
label | DETAIL - Compaction testing using a NDM to confirm degree of compaction - Mean 95%, Min 92%
label | FREQUENCY - 1 test per 20m2
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.8 - AP20 Running Course
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Grading
label | DETAIL - Aggregate must be graded as a AP20
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
checkpoint | 4.9 - AP20 Running Course
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - MDD and OMC
label | DETAIL - Lab test to determine the MDD and OMC of the AP20 Aggregate
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
checkpoint | 4.10 - AP20 Running Course
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Layer surface
label | DETAIL - Top surface should be at FL
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.11 - AP20 Running Course
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - NDM Testing
label | DETAIL - Compaction testing using a NDM to confirm degree of compaction - Mean 98%, Min 92%
label | FREQUENCY - 1 test per 20m2
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.12 - Compound extents
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Gravel compound size and batter slops
label | DETAIL - Top surface of compound must extend minimum 500mm past fence location and slope 1:3 to existing ground level
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 3.0.0 Trenching and Ducts | itp |  |  |  |  | ITP - 3.0.0 Trenching and Ducts
section | 5.0 - Trenching, Ducts and Cable Trays
checkpoint | 5.1 - Trench locations
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Trench and ducting routes, Concrete protrusions
label | DETAIL - The trenching an cable routes are to be marked out on site and checked. Protrusions into concrete slab foundations are to be set out
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0602
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Trench depth
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Trench to be excavated to required depth
label | DETAIL - trenches are to be 850mm deep from design FL and 300mm wide
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Duct installation
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Power and fibre duct installation depth
label | DETAIL - Power ducts to be 800mm and fibre ducts to be 600mm minimum below design FL
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
checkpoint | 5.4 - Warning Tape
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Warning tape location
label | DETAIL - Warning tape is to be 450mm below design FL
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
checkpoint | 5.5 - TUDS Pits - Size and lid rating
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Correct size and ratings
label | DETAIL - Power and fibre pits to be a minimum of 0.59m2 (750x1200) and security pit to be a minimum of 0.45m2 (450x450) and all lids to be class D and bolted down
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Documents
label | VERIFICATION RECORDS - Supplier dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Michael Harley
checkpoint | 5.6 - TUDS Pits - Locations
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Locations are correct
label | DETAIL - Setout pit locations prior to trenching
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0602
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.7 - H-Frame Foundations - Depth
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Foundations are to the correct depth and size
label | DETAIL - Augered holes need to be a depth of 1220mm and a diameter of 460mm
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.8 - H-Frame Foundations - Concrete
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Concrete strength
label | DETAIL - Holes to be backfilled with 25MPa concrete, poles are to be spaced 100mm from the base of the excavation
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Delivery Docket and Lab Testing
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 4.0.0 Antenna Foundations | itp |  |  |  |  | ITP - 4.0.0 Antenna Foundations
section | 6.0 - Antenna Foundations
checkpoint | 6.1 - Excavation Depth and Size
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Excavation must be deep and large enough.
label | DETAIL - Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides
label | FREQUENCY - once for each foundation
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Geotextile
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Geotextile Strength Class
label | DETAIL - Geotextile must be a minimum of strength class D
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery docket
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Michael Harley
checkpoint | 6.3 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Grading
label | DETAIL - Aggregate must be graded as a GAP40
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Testing report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Cedric Senkel
checkpoint | 6.4 - Gap40 Basecourse
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - MDD and OMC
label | DETAIL - Lab test to determine the MDD and OMC of the GAP40 Aggregate
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Testing report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.5 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Layer thickness
label | DETAIL - AP40 layer below foundation should be a minimum of 300mm thick, extend 600mm around the foundation of all side and lift 400mm above base of foundation on all sides
label | FREQUENCY - once for each foundation
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Chad Ellis
checkpoint | 6.6 - Gap40 Basecourse
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - NDM Testing
label | DETAIL - Compaction testing using a NDM to confirm degree of compaction - Min 98% MDD
label | FREQUENCY - 2 tests per foundation
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Testing report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.7 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Size and Grade
label | DETAIL - HD20 (Grade 500) for top and bottom bars, HD10 (Grade 500) for link legs
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery Dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.8 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Spacing and Cover
label | DETAIL - 200mm centres for top and bottom bars, and 400mm centres for link legs
label | ○ 75mm cover, top, sides and bottom
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Pre-pour Checklist, Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.9 - Duct Protrusions
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Location for Protrusions
label | DETAIL - Ducts for KAA Power and Communications must protrude on the left side of bolt 7 and stay between bolts 6&7. Ducts must protrude outside of the 600mm keep out zone.
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450 & 0602
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.10 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Mix
label | DETAIL - Maximum aggregate size of 19mm
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery docket
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Michael Harley
checkpoint | 6.11 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Strength
label | DETAIL - 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders per load delivered
label | FREQUENCY - 2 cylinders per load
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Test reports, delivery dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450, GGT Hosting Spec GGT-1501
label | SIGNATORY - Cedric Senkel
checkpoint | 6.12 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Finish
label | DETAIL - Finish surface to be U3, Broom finish with a 25mm chamfer on all exposed edges
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Chad Ellis
checkpoint | 6.13 - Anchor Bolt Kits
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Alignment
label | DETAIL - Bolts to be numbers 1 to 8 clockwise around foundation. Bolts 1 and 5 must be aligned with long fence azimuth
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.14 - Anchor Bolt Kits
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Embedment Depth
label | DETAIL - Anchor bolts must be embedded a minimum of 265mm and protrude from the top surface by a minimum of 120mm
label | FREQUENCY - once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0450
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 5.0.0 GWSE Foundation | itp |  |  |  |  | ITP - 5.0.0 GWSE Foundation
section | 7.0 - GWSE Foundation Slab
checkpoint | 7.1 - Excavation Depth and Size
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Excavation must be deep and large enough.
label | DETAIL - Must allow for 300mm of AP40 Basecourse and extend 600mm past face of foundation on all sides
label | FREQUENCY - once for each foundation
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.2 - Geotextile
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Geotextile Strength Class
label | DETAIL - Geotextile must be a minimum of strength class D
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery docket
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Michael Harley
checkpoint | 7.3 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Grading
label | DETAIL - Aggregate must be graded as a GAP40
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Testing report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Cedric Senkel
checkpoint | 7.4 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Layer thickness
label | DETAIL - AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
checkpoint | 7.5 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Size and Grade
label | DETAIL - HD16 (Grade 500) for top and bottom bars
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery Dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.6 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Spacing and Cover
label | DETAIL - 200mm centres for top and bottom bars both ways 75mm cover, top, sides and bottom
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Pre-pour Checklist, Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.7 - Duct Protrusions
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Location for Protrusions
label | DETAIL - There are 8 duct protrusions detailed in the contract drawings, 3 x power, 3 x fibre, 1 x generator controls and 1 x earth
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.8 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Mix
label | DETAIL - Maximum aggregate size of 19mm
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery docket
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Michael Harley
checkpoint | 7.9 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Strength
label | DETAIL - 30MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery
label | FREQUENCY - 2 cylinders
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Test reports, delivery dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463, GGT Hosting Spec GGT-1501
label | SIGNATORY - Cedric Senkel
checkpoint | 7.10 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Finish
label | DETAIL - Finish surface to be U3, Broom finish on all exposed concrete, trowel finish for area under cabinet. There must be a 25mm chamfer on all exposed edges and 1% fall away from concrete of pad.
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0463
label | SIGNATORY - Chad Ellis
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 6.0.0 Generator Pad | itp |  |  |  |  | ITP - 6.0.0 Generator Pad
section | 8.0 - Generator and Fibre Enclosure Pads
checkpoint | 8.1 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Grading
label | DETAIL - Aggregate must be graded as a GAP40
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Testing report
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
checkpoint | 8.2 - Gap40 Basecourse
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Layer thickness
label | DETAIL - AP40 layer below foundation should be a minimum of 150mm thick and be the same dimensions as the concrete pad
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
checkpoint | 8.3 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Size and Grade
label | DETAIL - SE72 Mesh
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery Dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8.4 - Reinforcing Steel
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Spacing and Cover
label | DETAIL - Two layers of Mesh for generator pad, single layer for fibre enclosure. 75mm cover from bottom, 50mm cover from top
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Pre-pour Checklist, Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Cedric Senkel
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8.5 - Duct Protrusions
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Location for Protrusions
label | DETAIL - TBC
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8.6 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Mix
label | DETAIL - Maximum aggregate size of 19mm
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery docket
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460, GGT Hosting Spec GGT-1501
label | SIGNATORY - Michael Harley
checkpoint | 8.7 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Strength
label | DETAIL - 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from delivery
label | FREQUENCY - 2 cylinders
label | INSPECTION / TEST METHOD - Lab Test
label | VERIFICATION RECORDS - Test reports, delivery dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460, GGT Hosting Spec GGT-1501
label | SIGNATORY - Cedric Senkel
checkpoint | 8.8 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Finish
label | DETAIL - Finish surface to be U3, Broom finish. There must be a 25mm chamfer on all exposed edges.
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Photos
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0460
label | SIGNATORY - Chad Ellis
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP
checklist | ITP - 7.0.0 Fencing | itp |  |  |  |  | ITP - 7.0.0 Fencing
section | 9.0 - Security and Acoustic Fence
checkpoint | 9.1 - Fence Placement
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Fence must be in correct location
label | DETAIL - Fence line will be set out by survey prior to post hole excavation
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0401, 0405 & 0800-0808
label | SIGNATORY - Michael Harley
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.2 - Post Hole
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Diameter and Depth
label | DETAIL - All Post Holes are to be 450mm diameter
label | ○ Gate posts, corner posts and the first two posts in from each corner post must be 1.8m deep.
label | ○ All other intermediate posts and timer fence posts must be 1.2m deep
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0405, 0464 & 0800-0809
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.3 - Post Hole
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Spacing
label | DETAIL - Security Fence post holes to be 2.5m apart
label | ○ Acoustic Fence posts to be 1.2m apart
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Measure
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0405, 0464 & 0800-0809
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.4 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Mix
label | DETAIL - Maximum aggregate size of 19mm
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery Docket
label | CSS/IDS/ASNZS STANDARD - GGT Hosting Spec GGT-1501
label | SIGNATORY - Michael Harley
checkpoint | 9.5 - Concrete
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Strength
label | DETAIL - 25MPa Concrete must be used. Concrete cylinder must be tested at 28 days, take 2 cylinders from each delivery load
label | FREQUENCY - 2 Cylinders from each load
label | INSPECTION / TEST METHOD - Test
label | VERIFICATION RECORDS - Lab Test Report
label | CSS/IDS/ASNZS STANDARD - GGT Hosting Spec GGT-1501
label | SIGNATORY - Cedric Senkel
checkpoint | 9.6 - Timber
label | ACTION (W, M, H) - H
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Size and treatment of timber
label | DETAIL - Posts - 90x90 H4
label | ○ Rails - 90x70 H2.3
label | ○ Vertical Boards - 240x25 H2.3
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Delivery Dockets
label | CSS/IDS/ASNZS STANDARD - Contract Drawing - 0464
label | SIGNATORY - Chad Ellis
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.7 - Fence Alignment
label | ACTION (W, M, H) - W
label | CONFORMANCE CRITERIA (WHAT'S REQUIRED) - Post and Fence Alignment
label | DETAIL - Fence posts must be vertical and in a straight line
label | FREQUENCY - Once
label | INSPECTION / TEST METHOD - Inspection
label | VERIFICATION RECORDS - Survey Pickup and photos
label | CSS/IDS/ASNZS STANDARD - Contract drawings - 0401, 0405, 0464 & 0800-0809
label | SIGNATORY - Chad Ellis
checkpoint | Final Inspection
textbox | Accepted By: Sub-contractor
textbox | Accepted By: Project Manager
textbox | Accepted By: Quality Manager
signoff | Sign ITP