## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 089ba6be-8b55-44b5-a0b1-0ebb7c677f16 |  | checklist | Incident Report - Checklist |  |  |  |  | Yes | Incident Report - Checklist | 0077ebaf-2e22-4d82-affe-bbbbcaeaa256
checkpoint-group | 95f431dc-6c04-47a5-ada1-ff59c7aa6a2f |  | section | Injured Workers Details
checkpoint-status | f6f11460-abcf-4f93-a18a-7819b1fc2384 |  | checkpoint | Injured Worker
text | 00e31074-2039-5360-b60f-fe52f0e53657 |  | textbox | Name of Employer of injured Person(s) (If any):
text | c695726b-6337-5087-88c7-e0fb338763ac |  | textbox | Business address of Person/Organisation in charge of the equipment:
text | eb0072e5-9a54-53c0-a7d6-bd648eb073e6 |  | textbox | Full name of Employee:
text | a669153e-66ac-50a2-8359-61c94d523efc |  | textbox | Date of Birth:
button | aa6993a4-07e3-50fd-80fd-d35f50ef34e8 |  | button | Sex: | Female, Male
text | 6ac94fb6-2b02-5354-abdc-93932d5906ee |  | textbox | Residential address and telephone number (if known):
text | e94d128a-ac80-5a58-8a79-b2d7241b894a |  | textbox | Occupation of Employee:
checkpoint-group | 42fdad4e-95e2-4551-b44c-7c65b1b50a31 |  | section | Incident Details
checkpoint-status | 462beb60-19a5-4ec7-b957-cfdc2a60b46f |  | checkpoint | Incident
text | 765c42b2-fdca-56a0-b7df-5551194fd6ea |  | textbox | Date of Birth:
text | 278ed11a-e5c0-58d8-bb81-b12a959f5bca |  | textbox | Place/Location where incident occurred:
text | 181c8c95-1506-553c-8955-780fcbd4b8e7 |  | textbox | Work/activity being performed at time of incident and equipment being used:
text | 336b796d-2775-521f-9e78-f17380203837 |  | textbox | Brief description of incident:
text | 8d4814dc-a9d9-5517-a480-7b9c195a94ed |  | textbox | Treatment given/action taken at the time of the incident: (Attach Statements below)
text | 07786379-e1ba-59b8-afdc-a95b61f137fa |  | textbox | Name of Witnesses or Name of Person(s) who first attended the scene: (Attach Statements below)
text | 5423e500-ba21-580e-a22c-72a833fcf7c1 |  | textbox | Action taken/intended, if any, to prevent recurrence of the incident:
label | a892df1f-979f-5bdf-b056-525b54efa311 |  | note | Add diagram or picture of incident below
checkpoint-group | 119905d9-e4dd-4740-bd5f-62e5adb3830f |  | section | Treatment Details
checkpoint-status | 85c23cc1-118e-44ed-b10e-8c60e6e39b90 |  | checkpoint | Details
button | 925bbbcf-69f7-5672-a117-d05ebdfab877 |  | button | Did the injury necessitate loss of time? | No, Yes
label | 184e6a1f-d12c-56ce-a901-ca094a85f372 |  | note | If "Yes" selected
text | 30776262-997d-5040-ac11-8d3def1ffc3c |  | textbox | Name the clinic/medical centre attended:
label | 6ad991a2-2b59-5cd5-8822-04203d53cf4f |  | note | Attach WorkCover Certificate of Capacity (Attach below)
button | 234d0e1d-8cf6-57dd-9176-62ca31c71e04 |  | button | Was an ambulance required? | No, Yes
button | 137eb5da-2402-5412-af23-98a7a71c5855 |  | button | Was the incident reported to WorkSafe Victoria? | No, Yes
label | 792ed534-2dab-5005-8bba-6b742f596488 |  | note | If "Yes" selected
text | a47ff3c7-03ac-5ac2-b423-e53828ed83bb |  | textbox | WorkSafe Incident notification number is:
checkpoint-group | 92674a90-c124-4046-8b31-c03ef33f0d97 |  | section | Form Details
checkpoint-status | 38d6c489-aa57-46cb-b661-c71e8d0af3c5 |  | checkpoint | Details of Person submitting this form
text | 790ce84b-23ba-5727-ba27-22dca24a522e |  | textbox | Name:
text | c42616aa-2dd3-5325-b1cc-58cf3690800b |  | textbox | Position/Title:
text | 24e45b1f-4ccd-5390-9bb8-ec748594f5bf |  | textbox | Date:
button | e13b5396-f12e-53a6-8672-935025160bea |  | button | Type of Injury (Filled out by OHS Manager): | LTI, MTI, FAI
checklist-flat | 0b738d53-50bc-4b85-8240-7128a2784dba |  | checklist | Variation (21/05/2020) |  |  |  |  | Yes | Variation (21/05/2020) | 196ea0bd-9587-4adc-97c5-367da2b9db52
checkpoint-status | 7a77cb08-517f-4955-9733-0753608c97d4 |  | checkpoint | Variation Details Complete (Pass once inputted)
text | 206997c7-9700-5cac-9ec8-864710c683a3 |  | textbox | Variation Name
text | 15fd0f77-1283-51d7-b773-062b3923b8ac |  | textbox | Variation Description
text | 8407f4f9-c250-5511-9f19-fe9ac9eef13e |  | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
text | d5249ab2-12fa-59fe-9599-ec511fd9c74c |  | textbox | Acknowledgement (Who requested the work to be done)
text | 0c27cd13-4618-5c10-b949-1a97a557ac4a |  | textbox | Signature/Reference Mail (Who to send the variation too)
checkpoint-status | 838ad0bb-f046-4b77-a057-4fd55db691f6 |  | checkpoint | Supporting Documentation (Attached or Referenced)
label | cc1436e2-044b-5a7b-831a-bdd5e7bc6df7 |  | note | Add Photos/Comments of variation work below
checkpoint-status | 9de917a1-429b-4ac6-8652-219d8a507203 |  | checkpoint | Variation Sign-Off - Click to Add signatures below
button | 68a1b9f9-518a-5a5b-8af6-b07735122003 |  | button | Broad Air Representative Signature Added below | Yes, No
button | 8538d351-0ad4-531a-bc4e-db5814952a83 |  | button | Builder Representative Signature Added below | Yes, No
holdpoint | 00b163bd-b594-48e7-9522-95ffe1846973 |  | signoff | Click to Add Signatures of Wilson & Builder's Representative
checklist-flat | f22c7575-96ad-4b12-a926-a8de61ea5b59 |  | checklist | Common Area Fit-Off Checklist [D] |  |  |  |  | Yes | Common Area Fit-Off Checklist [D] | 1c1e141c-c693-4864-b848-99f3e0dbfacc
checkpoint-status | a36e7315-e8d6-43e2-a253-f8ef2494b6ca |  | checkpoint | Lobby supply grilles fitted
checkpoint-status | 4ffef9ec-b767-4295-92e4-e34c0f581bed |  | checkpoint | Lobby Relief VCD is installed and the motirised actuator is fitted of and wired
checkpoint-status | 0f859653-9a4b-4a74-ad7f-5ddaed9ec71e |  | checkpoint | Lobby relief grilles fitted
checkpoint-status | 54141aa5-fba5-4fec-90df-0f576bc9c064 |  | checkpoint | Stair pressurisation grilles in the stair shaft fitted
checkpoint-status | 9dbcda7d-18d8-40cd-b58a-d972a673c67d |  | checkpoint | Stair pressurization VCD / OBD is installed
checkpoint-status | 3dd4b3d2-126f-456b-b0d7-85fd4d80945d |  | checkpoint | Carpark supply grilles fitted
checkpoint-status | 88bb80ce-5159-4364-a8d4-a99cf91d4164 |  | checkpoint | Carpark supply VCD / OBD is installed and the motirised acutator is fitted of and wired (if applicable)
checkpoint-status | 8a0fb42b-d3cf-48c5-9985-e7da77fc60a2 |  | checkpoint | Carpark Exhaust grilles fitted
checkpoint-status | a1986ed7-8b91-4c4b-9c8f-fca07b325269 |  | checkpoint | Carpark Exhaust VCD / OBD is installed and the motirised acutator is fitted of and wired (if applicable)
checkpoint-status | 786ea575-736b-4754-b29c-ccc40daf048f |  | checkpoint | Garbage Exhaust grilles fitted
checkpoint-status | 223cf93f-4cb1-4bd2-802c-554fc7dc4d0a |  | checkpoint | Garbage Exhaust VCD / OBD is installed
checkpoint-status | 8e1ae5f0-7daa-4416-b355-e967f42586b1 |  | checkpoint | General Exhaust grilles fitted
checkpoint-status | 80ae4d31-2cf6-431f-860b-d3b444a710de |  | checkpoint | General Exhaust VCD / OBD is installed
checkpoint-status | 43950ae2-ad1f-4072-aae1-72bf834efb37 |  | checkpoint | Loading Dock grilles fitted
checkpoint-status | 1cf57b8c-81dd-46d7-92e5-e932d077f06a |  | checkpoint | Loading Dock VCD / OBD is installed
checkpoint-status | 79f6e9ea-b2c2-42b8-8428-397b6de4ddff |  | checkpoint | Pump Room supply grillies fitted
checkpoint-status | 22fd4056-514e-4d28-b859-e44cf8246e9c |  | checkpoint | Pump room supply VCD / OBD is installed
checkpoint-status | 072b004e-3280-4619-be18-263fc32dc2c3 |  | checkpoint | Toilet Exhaust grilles fitted c/w OBD
checkpoint-status | dba44850-ab04-4aa1-a5c7-a62f15f53c81 |  | checkpoint | Bike room grilles fitted
checkpoint-status | 81c5f229-ca64-4dc3-abb9-7936ee6e79c4 |  | checkpoint | Bike room VCD / OBD installed
checkpoint-status | cc8ed32b-0a02-47ea-a381-911683a410e0 |  | checkpoint | Comms room supply grilles fitted
checkpoint-status | d0585a99-6584-471f-82bb-530ff28e2d6b |  | checkpoint | Comms room VCD / OBD installed
checkpoint-status | dd9c47a1-38b5-4930-9d39-6600c334cf6b |  | checkpoint | Main Switch room Supply grilles fitted
checkpoint-status | 9e82146a-1139-4cfe-a65c-5e7e157a8d7b |  | checkpoint | Main Switch room Supply VCD / OBD installed
checkpoint-status | 0d92e174-cc82-4ba0-8be1-27a35a78c535 |  | checkpoint | Storage room Supply grilles fitted
checkpoint-status | fa0b2f89-3955-4174-bae1-463472f3715c |  | checkpoint | Storage room Supply VCD/ OBD installed
checkpoint-status | b95a6c0e-b817-42a6-aff2-739e4ca48620 |  | checkpoint | Bin room grilles fitted
checkpoint-status | 4a3f22c6-76cc-41f1-ae4e-17211ebee108 |  | checkpoint | Bin room VCD / OBD installed
checkpoint-status | b59c7f24-01bb-46c3-8be1-c5520b3d1838 |  | checkpoint | All fire dampers provided with an access panel as per mechanical drawings
checklist-flat | beb4f0dc-5f99-45a0-8b6a-3dc22943e8e5 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | 336e13cb-03b5-45ee-b086-74f7026921f0
checkpoint-status | d313887f-7d91-4a09-b34e-294f5a693534 |  | checkpoint | Toolbox meeting completed & Specific Document(s) attached
text | b2dea265-0125-5bbb-ac60-c19553d177d4 |  | textbox | Date
text | 0cd2e618-9d1d-5c62-a6e7-cb6709301b34 |  | textbox | Site Address
text | f5afc738-e731-57f7-af5d-07d6b5dd8976 |  | textbox | Toolbox meeting topic
text | d2690777-9c2e-5658-8830-455f11fa69ce |  | textbox | Toolbox Item 1 - (Add any resolutions below item)
text | d15d75ee-2910-52be-ba40-d327be180a46 |  | textbox | Toolbox Item 2 - (Add any resolutions below item)
text | d3c7eed7-f4e8-5812-ac36-8b5072e72ae9 |  | textbox | Toolbox Item 3 - (Add any resolutions below item)
text | f96d9c14-29bd-5f45-8a8d-cdce17ca415e |  | textbox | Toolbox Item 4 - (Add any resolutions below item)
checkpoint-status | 8e334a21-6e1a-4dcf-9c74-8856bfb9cbba |  | checkpoint | Toolbox meeting pdf attached (Add below)
label | 9dca7fb7-88b9-5b52-adf8-d55f07604ef7 |  | note | Broad Air takes safety seriously and we encourage all persons representing the company to speak up if something is not right. If you find yourself unsure about something when it comes to safety, ASK! There is no such thing as a stupid question.
checkpoint-status | 65bba8c7-8710-4d0a-8618-3e903595feea |  | checkpoint | Sign Off – By signing this page you acknowledge your attendance of this toolbox meeting and your co-operation with our policies & procedures
holdpoint | 5963583f-3586-4de0-b1c0-7a771083f147 |  | signoff | Click to 'Add' signature's of each attendee
checklist-flat | 68316b5b-017a-423c-a8ef-acd8c53ba64e |  | checklist | A/C Checklist Commissioning [F] |  |  |  |  | Yes | A/C Checklist Commissioning [F] | 3815f1a7-d679-458f-9425-83e36dc5abac
checkpoint-status | c1e528c2-605a-469b-aef8-5ae5d259424e |  | checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs?
checkpoint-status | 02201044-919c-41dc-952f-b114b004789a |  | checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum?
checkpoint-status | f8e86a12-7bbc-4413-b0fc-e089bfd84729 |  | checkpoint | Indoor unit drains have been terminated to the tundish point?
checkpoint-status | 5751542c-ab85-4e87-aea3-8068e005d086 |  | checkpoint | Outdoor unit drains have been terminated to the tundish point?
checkpoint-status | 72b42206-129b-457a-ab6d-c279a323b6d5 |  | checkpoint | Indoor unit flare connection has been properly insulated with specified insulation?
checkpoint-status | 65303761-85d1-4b16-b06d-68d31fe039ee |  | checkpoint | Indoor unit drain connection point has been securely fastened and sealed?
checkpoint-status | 59e060f8-331d-47ae-a8cb-b9601ce27d37 |  | checkpoint | A/C System Flows checked as per mechanical drawings
checklist-flat | 824e9a92-7e79-4d6b-a88c-e58a7343912b |  | checklist | Apartment Fit-Off Checklist [E] |  |  |  |  | Yes | Apartment Fit-Off Checklist [E] | 4995732e-751c-45a0-8b11-9409634cf424
checkpoint-status | a9ebd7dd-724e-4e66-b5cb-d9b15ecf0dc4 |  | checkpoint | AC grille to living room installed with no defect
checkpoint-status | 6a573d07-35ae-4c7f-8a5c-2eb16c75c149 |  | checkpoint | AC grille to bedroom installed with no defect
checkpoint-status | e70af270-42b4-451b-9b37-8a16d8cf7b5d |  | checkpoint | Return Air grille installed as per RCP drawings
checkpoint-status | 50a2ac33-2c40-4598-b065-ed28d8a8b800 |  | checkpoint | Range hood duct connected and taped to ensure air tight
checkpoint-status | e76025a6-2ad0-4844-9f1d-70f80a80d69d |  | checkpoint | AC Controller installed as per RCP drawings
checkpoint-status | 78ab3dbe-f9aa-4b14-9637-0a488309bb8a |  | checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point
checkpoint-status | 10d10135-d38e-4abe-8aab-1e3407442d02 |  | checkpoint | Ensuite Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-status | 1bc65bbd-986e-4bb5-8ce8-3f162c89d1dc |  | checkpoint | Toielt Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-status | 7c344c4c-7ddc-496b-8ff3-0b096de225d1 |  | checkpoint | Ensuite exhaust grilles installed
checkpoint-status | 0cc7f97a-6a04-434a-8c39-efe9becbb5ab |  | checkpoint | Toilet exhaust grilles installed
checkpoint-status | eea321d0-27f4-45e9-855c-5a2c339138ca |  | checkpoint | Laundry Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-status | 9f614b3b-1f44-43b1-81c9-1b1afffa29fa |  | checkpoint | Laundry exhaust grilles installed
checkpoint-status | a9ec6d09-dfb1-4081-a733-68bd36013728 |  | checkpoint | Access panels placed as per drawings
checkpoint-status | 0478c9b8-f846-4c50-858e-f396f0d69746 |  | checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked
checkpoint-status | 4e0b8bad-c074-479f-b1a0-48276770fa95 |  | checkpoint | External louvers installed all gaps sealed between plenum box and wall/ louver flange to wall , photo evidence provided for below 1.Box sealed internally and the gap between the box and wall is sealed 2.Louver flanges sealed to the external box
checklist-flat | 3a15d89d-ea7b-4894-b84c-ecaf7b86e67a |  | checklist | Delivery Dockets |  |  |  |  | Yes | Add Delivery Dockets | 71ff8a27-1067-495f-bd16-b81cdce3fe6d
checkpoint-no-status | 1b484281-4d61-44c2-8653-1ad0f4374101 |  | checkpoint | Attach Delivery Dockets
checklist-flat | ec327f7a-3b76-4e52-b804-e79c58635fe6 |  | checklist | Sign Off |  |  |  |  | Yes | Sign Off (Fire Damper) | 96cad709-9393-4781-b17b-d0f4b619c68e
checkpoint-status | 229fdb5b-51c6-4fa6-bcc3-ecf24f98fd6d |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 6820a7d6-5b9e-443e-9b1b-f4ab1a970493 |  | checkpoint | Pictures/Comments attached below
checkpoint-no-status | 565f7c40-7b8e-4b5d-9787-424bbabec0cb |  | checkpoint | Notes/Additional Comments
checkpoint-status | bd915c9d-977f-46e4-999b-e218b069872a |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 51c01fbb-c759-43c2-adc4-8ecd3b3f1799 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | ed54e8a3-2dea-41fb-9e7b-915a8bcaad12 |  | checkpoint | Builder Representative Sign Off
holdpoint | 150e67ef-e1e4-43c7-98b4-ca8cc2e32954 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | f68b262c-f021-4034-9df1-a1b7fdc474b7 |  | checklist | Ducting-Common Area [K] |  |  |  |  | Yes | Ducting-Common Area [K] | 9f3ed4e2-33f4-4b59-9050-619cddeb9e48
checkpoint-status | 17b144d8-bc94-4311-9a4d-a9337ee327ef |  | checkpoint | Riser
checkpoint-status | 361d5f54-5206-4791-9c79-c4e108a2e48b |  | checkpoint | Are drawings on site the latest issue
checkpoint-status | a1b81cbe-7134-4743-9ef9-5382812c04d3 |  | checkpoint | Are plant and equipment location correct
checkpoint-status | daeb92b5-37d4-4783-bb05-54b7566c287a |  | checkpoint | Duct size and location correct
checkpoint-status | 8cedcd17-e959-484a-969e-a53b2171bd9f |  | checkpoint | Material and gauge correct
checkpoint-status | bef1872f-ab70-48a8-8530-4a34b2ad43e6 |  | checkpoint | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method
checkpoint-status | 0797d87e-e91f-499f-86e9-55349f69654b |  | checkpoint | Is correct Joining method being used
checkpoint-status | 5ed60400-4436-47a0-b60d-3e11e553c627 |  | checkpoint | Are joints completed and cleated installed on flanges
checkpoint-status | e0046574-9221-4b52-8796-0dd9c3ca2f1c |  | checkpoint | Is correct joint sealant being used
checkpoint-status | 57c60a39-5e6b-48b6-b538-1e5bd65c4404 |  | checkpoint | Is ductwork installation complete
checklist-flat | d940186f-4a6d-40f6-ab41-29cb766e7440 |  | checklist | Job Details |  |  |  |  | Yes | Job Details | ad0d9fc5-6d55-4ef5-9f86-af0ba1dc8647
checkpoint-status | 07fd746d-4f67-45a7-9ced-f753a712b3e8 |  | checkpoint | Site Info
text | abb3b7f6-6af4-51ac-897f-1b2a05ae41c0 |  | textbox | Site Address
text | 2e307e01-7d9c-5b5f-b0bf-8dbe818b5557 |  | textbox | Builders Details
text | 4a404e52-6a18-5133-89a4-cee4b7e2858d |  | textbox | Project Managers Details
text | e3ad6643-faa5-50a2-bff1-d73c6cd7a81e |  | textbox | Site Managers Details
checkpoint-status | 61f4e93b-9cde-458e-a4c9-0446b5d7f993 |  | checkpoint | latest drawings (attached or referenced)
checkpoint-status | cfabc1f9-e4cc-4b67-b4b8-eb9c7a856ef0 |  | checkpoint | Scope of Works Attached
checkpoint-status | 59a44ec3-a4ee-4c2f-8604-d7e12ac69d2a |  | checkpoint | Additional Pre-Start Docs (attached or referenced)
checklist-flat | d739526b-9d43-44ee-a57e-97c9da6da62e |  | checklist | Jet Fans [L] |  |  |  |  | Yes | Jet Fans [L] | b69346c4-ff38-4750-9bb7-b95a73112838
checkpoint-status | dc12c27a-150e-4cd6-8ec6-4607f6d15722 |  | checkpoint | Are drawings on site the latest issue?
checkpoint-status | e4a5c2f0-888a-4055-9578-24ab0da30548 |  | checkpoint | Are plant and equipment location installed correctly as per drawings?
checkpoint-status | ec5f1584-9e0a-462c-9fd3-a2b01464dc68 |  | checkpoint | Model of the fan is correct as per latest Fan Schedule?
checkpoint-status | 4ab85bc6-fe8e-4eea-8e92-5b1efd1fc760 |  | checkpoint | Is the fan attached to the ceiling structure of the carpark with hardware appropriate to the size and weight of the units (Typically 8mm fasteners)?
checkpoint-status | 0de87791-b901-4079-a62d-e42f96d586ac |  | checkpoint | Are the correct anti-vibration mounts being used ?
checkpoint-status | 7d684226-7b77-4a1c-b731-d152205cae13 |  | checkpoint | Is the Fan discharge parallel to beams?
checkpoint-status | 9eeb9d58-5e10-4ce1-9996-2665b8218915 |  | checkpoint | Do we have sufficient Clearance?
checkpoint-status | 8125271f-c1d6-4fa5-893a-29ac9caedcce |  | checkpoint | Is the obstruction too close?
checkpoint-status | 397dc1ff-d2d5-4d25-b010-f36aaf21676d |  | checkpoint | Is the fan installation site coordinated between trades to avoid clashes with pipe work, signage and other obstructions?
checklist-flat | 90c7b42d-f998-4b9f-9529-f8a83aab7aaa |  | checklist | Fire Damper Checklist -IBD-FS-A [H] |  |  |  |  | Yes | Fire Damper Checklist -IBD-FS-A [H] | b87a35ce-e6e9-4818-aa53-455afd374a93
checkpoint-status | c0b7f65a-8fa1-493a-a44f-dce118631155 |  | checkpoint | Penetration details have been captured
checkpoint-status | 5e15f674-c144-4aa2-8478-2039e40de671 |  | checkpoint | Gaps between the fire damper and wall no greater than 25mm and is filled with Lorient Intumescent Sealant with no cracking visible
checkpoint-status | 854ca0f5-9fe0-4b2d-a75a-199cca2f2ef0 |  | checkpoint | Lorient fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint-status | b4f4aed0-6fb7-4b98-be5a-55c2092fdeca |  | checkpoint | Casing perimeter is sealed with Lorient intumescent sealant. No evidence of cracking.
checkpoint-status | 68227094-98cb-4c4e-a9d2-ad338debf2ed |  | checkpoint | Mechanically fix the branch to the vertical riser with steel screws or pop rivets
checkpoint-status | b1db16c4-4a48-42dc-9890-4928a0ae07ea |  | checkpoint | Sheet metal thickness is 0.7mm or greater.
checkpoint-status | 25a12ee4-8cb9-4fd5-956e-f387b1ef4120 |  | checkpoint | Ductwork is connected to either side of the casing with nylon bolts on the flanges as per the AS1682.2 break away joint method. Bolts do not exceed an 8mm diameter.
checkpoint-status | 016ddefa-fb2e-4063-b9f4-c4610ecd1896 |  | checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
checkpoint-status | 2ec8f315-1cbc-4382-95a0-be5104210f07 |  | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint-status | ab482d32-5df1-49c6-9eae-b86717eda119 |  | checkpoint | Pictures attached
checkpoint-status | eb8c6561-3ae6-4353-a769-50be5129ae3f |  | checkpoint | Signature (Contract/Subcontractor Assessor)
checkpoint-status | f1f4eced-ac62-4ebf-a68b-6f7122f844d4 |  | checkpoint | Signature (Builder Representative)
checklist-flat | 39480e29-a8b7-4746-984f-ed17a3c14ee2 |  | checklist | Duct Installation Check List [C] |  |  |  |  | Yes | Duct Installation Check List [C] | b8bc58a1-0344-4419-bbf7-417bfbcd76e6
checkpoint-status | e3017edb-a15c-470a-88bf-57809645f660 |  | checkpoint | Are drawings on site the latest issue
checkpoint-status | 97241eb8-20d9-4164-b6d6-ea8a20db4b9f |  | checkpoint | Are plant and equipment location correct
checkpoint-status | 1d55bbc5-1109-4f3d-86b7-10f18380e90a |  | checkpoint | Fan in the duct run has been installed
checkpoint-status | c6ba9b35-131f-4b9f-82d0-5ba2d077b8f8 |  | checkpoint | Model of the fan is correct as per latest Fan Schedule
checkpoint-status | 430bf207-aa34-4c5d-9ca0-e8985a4a8b2c |  | checkpoint | Duct size and location correct
checkpoint-status | c1108547-309e-4361-8321-bdccd64ea203 |  | checkpoint | Material and gauge correct
checkpoint-status | f5249219-b7bb-48d7-8da4-24f199259db0 |  | checkpoint | Is correct support method being used - Risers are supported at each level.
checkpoint-status | ba83a4c9-93ac-4dc5-beb3-f511eca6b40b |  | checkpoint | Is correct jointing method being used
checkpoint-status | 9bc76ccd-05ec-4ffc-8d35-165b6ee81a23 |  | checkpoint | Are joints completed and cleated installed on flanges
checkpoint-status | 7653f40d-a7cc-483b-b0bd-7002d6656055 |  | checkpoint | Is correct joint sealant being used
checkpoint-status | 07a22d21-0bf2-4f94-9595-88c260d01357 |  | checkpoint | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
checkpoint-status | d0143c93-5d84-47cb-9631-0dc3df5842c3 |  | checkpoint | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
checkpoint-status | e3ec33e8-a387-4cec-927e-529eedac209d |  | checkpoint | Is adequate distance between attenuator and fans been maintained?
checkpoint-status | d455d355-4e68-4caf-b11e-c365bad05700 |  | checkpoint | Are the attenuator splitters in the plane of the bend ?
checkpoint-status | 2b8a8c8b-7ac9-4b88-a792-245d4f95ae2c |  | checkpoint | Are transitions close to attenuators gradual?
checkpoint-status | 6023d33e-bbff-4c42-849b-2fa448c889a6 |  | checkpoint | Is a settling duct between volume control dampers and attenuators allowed?
checkpoint-status | a92817d7-e466-4e0e-a110-ed317a31693f |  | checkpoint | Are fire dampers installed and break away joint complete
checkpoint-status | d4025b7c-519f-49d4-902f-babfae078e51 |  | checkpoint | Are flexible ducts installed, supported and connected to spigot by approved mthod using duct tape on internal core and cable tie on outer core
checkpoint-status | c7e312a2-7b33-4209-9b2b-4800bca517a6 |  | checkpoint | Are flexible connections to equipment sealed and aligned
checkpoint-status | 47510d01-2f38-4e4b-86f7-8a5737264b64 |  | checkpoint | Is ductwork insulation as per drawings
checkpoint-status | a7e25885-32fa-4cee-bef3-17f57602d4dd |  | checkpoint | Is ductwork fire rating complete
checkpoint-status | b27d92c9-287b-45fb-84c0-eacb70329a51 |  | checkpoint | Are all spigots installed and dampers fully open
checkpoint-status | 50b66697-937f-461f-9838-c8167abd86ce |  | checkpoint | Are all access panels for fire damper access installed and closed
checkpoint-status | 3e65cf41-2b74-4ea3-845b-929cf55289c9 |  | checkpoint | Is ductwork installation complete
checklist-flat | fd5cf43f-e3bb-4bc7-992d-35fb2e12df3f |  | checklist | Ceiling Closure Checklist 1 Rough In [B] |  |  |  |  | Yes | Ceiling Closure Checklist 1 Rough In [B] | b8f2186f-9318-4c81-a054-d88081668227
checkpoint-no-status | 67317795-5b7e-48ea-907a-b8809e3e35d8 |  | checkpoint | Air Conditioning
text | a1692f13-449f-56da-b32c-fdedf8762ab5 |  | textbox | Inspection Date:
text | 4729cbe4-e451-5b85-b650-3f8bacf9dc20 |  | textbox | Air Conditioning:
checkpoint-status | 35114ad5-3abe-49d4-bec8-089ed60944c0 |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status | d6899954-260c-4b65-8a17-f78f487f6ecd |  | checkpoint | Units all hung with isolation mounts and with 5% fall to drain point
checkpoint-status | 0c2dba62-4b20-4c90-b22d-5cc0012ce0f8 |  | checkpoint | Other services installed are not impeding access to fan coil
checkpoint-status | edffb6f1-f8a8-4480-a8a3-13de991f6239 |  | checkpoint | Wiring connected to indoor unit electrical box
checkpoint-status | dbea07ca-3941-4cdd-8c4d-31f4795ae5c0 |  | checkpoint | Condensate drainage is in correct location & height
checkpoint-status | 344076cc-84f3-4310-a2f7-9a2f17552691 |  | checkpoint | Filter Track for return air have been installed at the back of unit
checkpoint-status | f8d6627e-4c1f-4dd9-862b-f197fb48131e |  | checkpoint | All flexible ducts connections to air terminlas and spigots have been air tight by using duct tape
checkpoint-status | 23dfd4cb-e04e-4920-a436-72263cedf923 |  | checkpoint | All flexible ducts connections to air terminlas and spigots have been secured by using fixing ties/cables ties
checkpoint-status | 9a5a708f-d979-4643-abcc-1d1395f613e5 |  | checkpoint | Fresh air to apartment
checkpoint-no-status | e814280f-45ee-49ff-8438-47d6817f7e1f |  | checkpoint | Ventilation
text | 87bbe5c0-b649-5add-9a91-93a20adbe8c7 |  | textbox | Ventilation:
text | f4ca08c4-725e-5336-8601-0aadf2b4eaed |  | textbox | Inspection Date:
checkpoint-status | 609eae1e-c5d0-4853-ba57-262b3de9bde1 |  | checkpoint | Fans installed within ceiling areas are in the correct location as per Mechanical Drawings
checkpoint-status | aa9ded96-67a4-4ded-b448-b050b8be1bce |  | checkpoint | Fans Installed correctly with rubber isolation pads
checkpoint-status | 4bfad2fe-f47b-481d-8b1c-30479c63c6dd |  | checkpoint | All Flex has been run to correct location
checkpoint-status | 7bd738e8-a5e5-4abd-b4ca-fe50b44a0efb |  | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint-status | cbd0404c-f2f0-4c89-b8b4-7ee3a4b467e0 |  | checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties
checkpoint-status | f98972f4-6d28-4380-97c5-72e748e76e2b |  | checkpoint | Butterfly dampers are installed on the PODs grille neck and they are in a fully opened position and air tight sealed
checkpoint-status | 4d1db50f-71ee-48b4-95f7-2d0b39644a1b |  | checkpoint | PVC sleeves has been installed in wet area walls
checkpoint-status | d702d70d-ba3a-46f3-9096-4af7df03bb24 |  | checkpoint | Vent boxes are intalled in correct location as per RCP and SEALED
checkpoint-status | aba5f2e1-bda2-4c93-ae59-db0d29704d20 |  | checkpoint | PVC ducts have been hung and supported indicidually by using hanging straps
checkpoint-no-status | 6c63f57f-c20e-4044-8d0b-8aec7adea843 |  | checkpoint | Access Panel
text | 4aac7158-2099-5d29-8505-ef2d0ed32b55 |  | textbox | Access Panel:
text | 2e12f4c8-54fc-59dc-b8f9-1f3799facf1f |  | textbox | Inspection Date:
checkpoint-status | 40bf3f94-f30e-488b-b63c-e7f6c23749b3 |  | checkpoint | Access Panel location has been marked on floor as per RCP
checkpoint-status | 4bd07130-6082-4740-bf9a-a895ca0c4ad5 |  | checkpoint | Access panel location allows sufficient access equipment
checkpoint-status | a1d98226-d63f-4121-9d8e-02f758ba9ab5 |  | checkpoint | All other other services do not impede access
checklist-flat | 8e639145-c69d-49b9-893f-808f77746c33 |  | checklist | Lobby Area [J] |  |  |  |  | Yes | Lobby Area [J] | bd5a0bea-66d4-4095-80da-d1ef9e908a8a
checkpoint-no-status | 85050dc1-1661-40cb-bc19-a7e1b37c0dab |  | checkpoint | Inspection
text | cd03462c-7051-54c8-af26-0c6eebc386a1 |  | textbox | Inspection Date:
checkpoint-status | 6dba8f4d-8d81-4e66-bd2c-92d46439dd26 |  | checkpoint | Other services installed are not impeding access to fan coil
checkpoint-status | 9133656a-8178-4e1e-ad9a-72d75bfe40a8 |  | checkpoint | All Ductwork passing block walls are flushed and sealed
checkpoint-status | e9fee0a8-cb23-493b-9294-90bc33fc0958 |  | checkpoint | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed
checkpoint-status | 676e8f76-033a-42a0-bd5e-e034642efb1d |  | checkpoint | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed
checkpoint-status | 00682e0c-4193-4d26-9c40-bea376030b33 |  | checkpoint | Refrigerant pipes passing through fire rarted walls are sealed at wall penetratiobn by using approved material
checklist-flat | 56ffc182-d411-4f9b-95de-b36ebf03853c |  | checklist | Sign Off |  |  |  |  | Yes | Sign Off | c7910014-6156-4a19-b4fb-7aecff93d89a
checkpoint-status | 5b5521d8-2d78-4187-ac9d-3a6677d475d1 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | 3e6fe002-dc06-5716-a558-9d1452d9d89b |  | textbox | Inspection Date:
boolean | fe496a2a-628f-5390-8c6e-22cd89b75e72 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 4972974d-d83a-5c78-ba52-f17cfc61def4 |  | tickbox | Builder Representative Sign Off
holdpoint | 44f98ee4-95d8-49ee-9958-10e0a3d72836 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 1cbb82e7-dee5-4460-b7bb-8c19933eb0f3 |  | checklist | Wall Closure Checklist 1 Rough In [A] |  |  |  |  | Yes | Wall Closure Checklist 1 Rough In [A] | c98bf43d-b00b-4782-8387-57e35012c80a
checkpoint-status | c07aacfe-4f12-44c1-8fac-8d7319f1c331 |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint-status | c0f93edd-70f3-4837-97b4-571b599a6474 |  | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule
checkpoint-status | c5955cdf-0aa0-44cc-91b8-e8f64019eb58 |  | checkpoint | FCU installed as hight as possible with 5% slop tward the drain point
checkpoint-status | ac862ebc-200e-41e2-8577-95bca80b4ad6 |  | checkpoint | Thermostat control cabling has been installed
checkpoint-status | e54fdbd5-8a4b-47d1-8616-2b9c241db9e7 |  | checkpoint | Thermostat location is correct as per RCP
checkpoint-status | 8ca4f8c0-1ed9-4860-b6dc-f17c8e99e1db |  | checkpoint | Drains have been run to Tundish
checkpoint-status | 01267ad8-924a-46e6-bd50-92877fffbcac |  | checkpoint | Drains tested and witnessed by Boad Air
checkpoint-status | 38608788-3383-4f1d-a002-bbee737f97d8 |  | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect
checkpoint-status | 84a274cd-9897-4a8e-8191-dd15c06eea30 |  | checkpoint | Refrigeration insulation is not damaged
checkpoint-status | e7584956-754e-4161-b2a3-02fdeb610780 |  | checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation
checkpoint-status | 6b990a2e-8f44-48a4-8333-ea81f80f2f02 |  | checkpoint | Pipe projecting the wall cavities in balconies have been sealed
checkpoint-status | f849e08a-1b8d-489e-9279-931c8d8491e4 |  | checkpoint | Refrigeration pipes are run through cavity without being kinked or damaged
checkpoint-status | a421a2f5-8bc8-47b1-8968-af2d2900434a |  | checkpoint | Refrigeration pipes run is not exceeding the pipe length limits in VRV systems?
checkpoint-status | af45377b-c640-47f9-acf5-05e65f9905df |  | checkpoint | Vent boxes are sealed
checkpoint-status | bc3b97fe-d821-4b11-aef0-d3a88f5aa930 |  | checkpoint | Add divider using brackets inside Exhaust plenum boxes to separate toilet & kitchen exhaust?
checklist-flat | 9d9ac9f8-3360-49a1-a660-823596d59c8f |  | checklist | Prestart OH&S Documents |  |  |  |  | Yes | Prestart OH&S Documents | dd784020-3614-4646-b7eb-4e9b51f8111f
checkpoint-status | 469eca9a-1975-41cc-8760-5aef04b5f210 |  | checkpoint | All Pre-start OH&S Documentation Completed, Reviewed & Attached
label | 6d609ceb-e810-5234-87d0-3b5d9d6fe5f7 |  | note | Public Liability and Work Cover Insurances
label | dd831dd2-a651-5248-9cc7-0e758d606b98 |  | note | Company Safety Plan
label | af4453bf-ca69-50dd-9f50-0f5404de038e |  | note | SWMS & MSDS (Attached below)
label | 10de03cb-54c3-5fa6-8581-87c5dcff3ab2 |  | note | Additional Prestart OH&S Documents
checklist-flat | 945ab14f-7da9-4713-996b-0e96a9bdd15d |  | checklist | Smoke Damper Checklist [I] |  |  |  |  | Yes | Smoke Damper Checklist [I] | e473cd9d-a7f6-40f2-b581-62660d6a55e0
checkpoint-status | a8f2f1b0-82ae-4c33-9a33-de74c82f7092 |  | checkpoint | Smoke damper must be placed in the duct work so the closed blades are with 610 mm of the smoke barrier and before any duct inlets or outlest (See photo attached)
checkpoint-status | d8f25d03-1a84-43eb-8f9f-518b7e45db2f |  | checkpoint | When joining or fastening the damper to duct work, dampers shall be fastened with M6 bolts or M5 screws. Fasteners shall be spaced a maximum of 305 mm center to center with a minimum of two fastners per side.
checkpoint-status | 9aa5c8b6-aef4-4ec9-9df3-5cee15496831 |  | checkpoint | Smoke dampers must be sealed between the damper frames and duct work. The sealant shall be pressed in place to dispel any air and shall be applied to one side of the damper's face. Use the minimum amount of the material to completely seal the joint.
checkpoint-status | c5c6e93e-00e0-4715-9d9c-1c203ce56ff0 |  | checkpoint | Access Panel for Actuator and wiring according code and regulations
checklist-flat | b60d8b6e-b35f-4765-90db-d92820106e57 |  | checklist | Ventilation Checklist Commissioning [G] |  |  |  |  | Yes | Ventilation Checklist Commissioning [G] | e6ad4e04-6605-4f26-97a1-1a28fdc9b60a
checkpoint-status | 6e9e5cf6-e19a-42a1-a824-ace017c02f89 |  | checkpoint | Fan has been tested and is operational?
checkpoint-status | 7f374078-594d-478a-ab1c-e342da0d6187 |  | checkpoint | Adequate flow has been achieved in bathroom 1?
checkpoint-status | 1a815364-10d1-454d-b3f6-4a1d6ad82fc1 |  | checkpoint | Adequate flow has been achieved in ensuite?
checkpoint-status | 7c57d861-f942-4560-8b70-a6ddc1ac7e01 |  | checkpoint | Adequate flow has been achieved in laundry?
checkpoint-status | 3b1ac29d-9951-4bc5-8ded-0845595bab67 |  | checkpoint | Range hood has been tested and is operational?
checklist-flat | 0810237c-a67b-4c7d-9278-da1eda7b4c9e |  | checklist | Ventilation Checklist Commissioning [M] |  |  |  |  | Yes | Ventilation Checklist Commissioning [M] | f2025752-1918-4a34-b91c-e509e879ed0c
checkpoint-status | d7d6e666-cc85-4abc-bf40-b68a9d1b9073 |  | checkpoint | Visual survey of installed area. Are all items secured, compliant and no loose elements?
checkpoint-status | 748a9736-9f06-44e9-a099-41b74af1118b |  | checkpoint | Fan has been tested and is operational?
checkpoint-status | 41d43996-709e-480b-b160-7ab412397b21 |  | checkpoint | Adequate flow has been achieved through the grille / outlet?
checkpoint-status | ea69ba75-bcc5-43b9-bf94-8ec534755672 |  | checkpoint | Does the fan comply to work with control strategy as per the spec?