## ChecklistsITCs
Delete rows that aren't applicable to the project, then create the project breakdown and send to CONQA
type | name | values | prefix | postfix
checklist | Site Establishment and Safety Checklist | Pass, Fail
checkpoint | Delivery and goods lift location
checkpoint | Delivery requirements i.e. booking process
checkpoint | On site storage / office location
checkpoint | Site specific restrictions i.e. noise / starting times
checklist | Ductwork Checklist | Pass, Fail
checkpoint | Rectangular duct installed as per latest drawing | Yes, No
checkpoint | Duct flanges firmly bolted and sealed where required | Yes, No
checkpoint | Cleats installed as required | Yes, No
checkpoint | Correct hanger spacing / supports installed | Yes, No
checkpoint | DW insulated where required and damage free | Yes, No
checkpoint | Ductwork restrained for wind/seismic where required | Yes, No, N/A
checkpoint | Spiral installed as per latest drawing | Yes, No
checkpoint | Spiral joins sealed correctly | Yes, No
checkpoint | Correct hanger spacing / supports installed for spiral | Yes, No
checkpoint | Spiral insulated where required and damage free | Yes, No, N/A
checkpoint | Additional taping/sealing to medium/high pressure spiral | Yes, No, N/A
checkpoint | Pops & flex installed as per latest drawing | Yes, No
checkpoint | Correct hanger spacing / supports installed for flex | Yes, No
checkpoint | Free from support off other services | Yes, No
checkpoint | Flexible duct connections completed correctly | Yes, No
checkpoint | Blade dampers installed as documented and left in the open position | Yes, No
checkpoint | BD pop access panel coordinated and marked | Yes, No, N/A
checkpoint | Cushion boxes installed as per latest drawing | Yes, No
checkpoint | Balancing dampers installed as documented and left in the open position | Yes, No, N/A
checkpoint | Location of register coordinted with other services and marked on plan or floor | Yes, No
checkpoint | Volume Control Dampers installed as per latest drawing | Yes, No
checkpoint | Motorised dampers installed as per latest drawing / actuator fit off | Yes, No, N/A
checkpoint | Smoke dampers installed as per latest drawing / actuator fit off | Yes, No, N/A
checkpoint | Fire dampers installed as per latest drawing / access panel in DW where required | Yes, No, N/A
checkpoint | Damper access panels coordinated and marked | Yes, No
checkpoint | Photos of ductwork correctly sealed through smoke wall & smoke damper | Yes, No, N/A
checkpoint | Photo of each fire damper correctly installed and labelled | Yes, No, N/A
Checklist | Pipework | Pass, Fail
checkpoint | Pipework installed as per latest drawings | Yes, No
checkpoint | Pipework installed level and free of damage | Yes, No
checkpoint | All joins welded / crimped as per manufacturer's instructions | Yes, No
checkpoint | Air bleeds installed in pipework where required | Yes, No
checkpoint | Riser or area branch valve access panel coordinated and marked | Yes, No, N/A
checkpoint | Correct hanger spacing / supports installed for pipe runs | Yes, No
checkpoint | No other services suspended from pipework | Yes, No
checkpoint | Correct coil valves installed as per schedule | Yes, No
checkpoint | Test points, drains and bleeders installed where required | Yes, No
checkpoint | Coil valves accessible and not blocking any service points | Yes, No
checkpoint | Coil valveset access panel coordinated and marked | Yes, No
checkpoint | Pipework lagged where required and correct thickness | Yes, No
checkpoint | Pipework labelled | Yes, No
checkpoint | Pipework secitons though fire walls lagged as per test report | Yes, No, N/A
checkpoint | Photo of each set of pipes correctly fire sealed and labelled | Yes, No, N/A
checkpoint | HHW Pressure Test – ITR attached | Pass, Fail, N/A
checkpoint | HHW Flushed - plan, photos of flow readings and water quality attached | Pass, Fail, N/A
checkpoint | CHW Pressure Test – ITR attached | Pass, Fail, N/A
checkpoint | CHW Flushed - plan, photos of flow readings and water quality attached | Pass, Fail, N/A
checkpoint | Drain trapped where required | Yes, No
checkpoint | Correct hanger spacing / fall | Yes, No
checkpoint | Drain tested | Pass, Fail
checkpoint | Drain pump installed level and tested | Yes, No
checkpoint | Drain terminates at a tundish | Yes, No
checkpoint | Drains, pump and tundish access for maintenance. | Yes, No
checklist | Indoor Equipment | Pass, Fail
checkpoint | Indoor Unit (IDU) correctly supported as per project engineering requirements | Yes, No
checkpoint | Correct IDU installed as per latest drawing | Yes, No
checkpoint | Flexible connections installed and sealed | Yes, No
checkpoint | Access to filter bank / filters installed | Yes, No
checkpoint | Access to all relevant controls and isolators | Yes, No
checkpoint | IDU access panel coordinated and marked | Yes, No
checkpoint | Ventilation fan correctly supported as per project engineering requirements | Yes, No
checkpoint | Correct fan installed as per latest drawing | Yes, No
checkpoint | Fan connections secured and sealed | Yes, No
checkpoint | Access to fan and isolator | Yes, No
checkpoint | Ventilation fan access panel coordinated and marked | Yes, No
checklist | Plantroom / Outdoor Equipment | Pass, Fail
checkpoint | Floor or Platform Mounted Thermal Plant correctly supported as per project engineering requirements | Yes, No, N/A
checkpoint | Maintenance and ventilation clearance maintained as per manufacturer's specs | Yes, No, N/A
checkpoint | All manufacturer specific requirements have been provided in addition to project requirements | Yes, No, N/A
checklist | Grille Fit-Off Checklist | Pass, Fail, N/A
checkpoint | Grilles installed in correct location as per latest duct layout / RCP | Yes, No
checkpoint | Correct grille type installed | Yes, No
checkpoint | Grille installed flush and square | Yes, No
checkpoint | Are all grilles installed correctly? Air leaks, vibration or failure | Yes, No
checkpoint | Grille color as per schedule | Yes, No
checkpoint | Grille left clean of fingerprints and caps installed where required | Yes, No
checkpoint | Grille fit-Off completed to drawings/specification & Area left clean/tidy (Any Issues comment below) | Yes, No
checklist | Refrigeration Pipe Checklist | Pass, Fail, N/A
checkpoint | Correct IDU & ODU installed as per latest drawing & schedule | Yes, No
checkpoint | Installed as per latest drawings | Yes, No
checkpoint | No other services suspended from pipe work (Attach Photos below) | Yes, No
checkpoint | Installation damage free (Any Issues comment/attach Photos below) | Yes, No
checkpoint | Correct supports used and support spacing | Yes, No
checkpoint | Pipe labelled after insulation - provide photo evidence | Yes, No
checkpoint | Pipe mains installation completed to drawings/specification | Yes, No
checkpoint | Pipework system pressure tested | Pass, Fail, N/A
checkpoint | Area left clean and tidy - photos of cleanliness or issues | Yes, No
checkpoint | Photo of each set of pipes correctly fire sealed and labelled | Yes, No, N/A
checklist | All Subbie Rough-in Progression Checklist | Complete, Incomplete
checkpoint | All work in zone completed and appear compliant | Yes, No
label | Pass once all work complete
checklist | All Subbie Fit off & Testing Progression Checklist | Complete, Incomplete
checkpoint | All work in zone completed and appear compliant | Yes, No
label | Pass once all work complete
checklist | As Builts Checklist | Complete, Incomplete
button | Update As-Built's of any known changes | Yes, No

## TO BUILD - Project Breakdown
Project Breakdown |  |  | Checklists
PROJECT NAME: GVH Kitchen & Dining
OHS |  |  | Site Establishment and Safety Checklist
Site QA | Package A | Basement
All Subbie Rough-in Progression Checklist
All Subbie Fit off & Testing Progression Checklist
As Builts Checklist
Ductwork Checklist
Pipework
Indoor Equipment
Ground - Stage 1
All Subbie Rough-in Progression Checklist
All Subbie Fit off & Testing Progression Checklist
As Builts Checklist
Ductwork Checklist
Pipework
Indoor Equipment
Refrigeration Pipe Checklist
Grille Fit-Off Checklist
Ground - Stage 2
All Subbie Rough-in Progression Checklist
All Subbie Fit off & Testing Progression Checklist
As Builts Checklist
Ductwork Checklist
Grille Fit-Off Checklist
|  | Roof | All Subbie Rough-in Progression Checklist
All Subbie Fit off & Testing Progression Checklist
As Builts Checklist
Plantroom / Outdoor Equipment
| Package B | GF & L1 | All Subbie Rough-in Progression Checklist
All Subbie Fit off & Testing Progression Checklist
As Builts Checklist
Ductwork Checklist
Grille Fit-Off Checklist