## ITP Accessways
ACCESSWAYS ITP
Preconstruction
| Design | Issued For Construction Drawings: MSF-EN-CIV-DRG-510 MSF-EN-CIV-DRG-511 MSF-EN-CIV-DRG-512 MSF-EN-CIV-DRG-590 KDC EES2011 | P,F,Attachment
| Survey & Setout | Issued For Construction Drawings KDC EES2011 | P,F,Attachment
Material Procurement
| Granular Fill Material for subgrade improvement (If Required) | Issued For Construction Drawings Delivery Dockets if Imported Granular Fill from Offsite is Used Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite | P,F,Attachment
| Drainage Pipe | IFC Drawings Manufacturers Specifications KDC EES2011 Delivery Dockets Visual Inspections | P,F,Attachment
| Drainage Bedding Material | IFC Drawings KDC EES2011 Delivery Dockets | P,F,Attachment
| Gap 65 Subbase Material | Issued For Construction Drawings MSF-EN-CIV-DRG-020 Delivery Dockets | P,F,Attachment
| Gap40 Basecourse Material | Issued for Construction Drawings | P,F,Attachment
Construction
| Inspect Subgrade layer and Check Subgrade Strength | Issued for Construction Drawings Visual Inspection Scalar Penetrometer with results recorded of No of blows per 100mm on ITC | P,F,Attachment
| Drainage Culvert Installation | IFC Drawings: MSF-EN-CIV-DRG-310 MSF-EN-CIV-DRG-311 MSF-EN-CIV-DRG-312 MSF-EN-CIV-DRG-313 KDC EES2011 S06 Visual Inspection Meets requirements of Issued For Construction Drawings & KDC EES2011 S06 ITC - QF008 Pipelines | P,F,Attachment
| 300mm Granular Material | IFC Drawings KDC EES2011 Check granular layer is minimum of 300 thick. Take photos and measurements | P,F,Attachment
| Gap 40 Basecourse Construction | IFC Drawings KDC EES2011 Visual Inspection Clegg hammer reading of >25 recorded onto QF022 Clegg Hammer Test Report | P,F,Attachment
P,F,Attachment
Close-Out
| Non-Conformance-Reports | Non-Conformances Closed Out | P,F,Attachment
| Handover | At completion of works QA/QC Pack is handed to client Client Verifies Work has been completed correctly and all quality documents are in order | HoldPoint, P,F,Attachment

## ITP Laydowns
LAYDOWNS ITP
Preconstruction
| Design | Issued For Construction Drawings | P,F,Attachment
| Survey & Setout | Issued For Construction Drawings Agree and Confirm Locations and Areas Onsite | P,F,Attachment
Material Procurement
| Granular Fill Material for subgrade improvement (If Required) | Issued For Construction Drawings Delivery Dockets if Imported Granular Fill from Offsite is Used Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite | P,F,Attachment
| Gap 65 | Issued For Construction Drawings MSF-EN-CIV-DRG-020 Delivery Dockets | P,F,Attachment
Construction
| Inspect Subgrade layer and Check Subgrade Strength | Issued for Construction Drawings Visual Inspection Scalar Penetrometer with results recorded of No of blows per 100mm on ITC | P,F,Attachment
| Granular Fill Construction As Required | IFC Drawings Visual Inspection of completed Gap65 after light rolling | P,F,Attachment
| Gap 65 Construction | IFC Drawings Visual Inspection Proof Rolling | HoldPoint, P,F,Attachment
Close-Out
| Non-Conformance-Reports | Non-Conformances Closed Out | P,F,Attachment
| Handover | At completion of works QA/QC Pack is handed to client Client Verifies Work has been completed correctly and all quality documents are in order | HoldPoint, P,F,Attachment

## ITP InverterFDNs
INVERTER FOUNDATIONS ITP
Preconstruction
| Design | Issued For Construction Drawings MSF-EN-CIV-DRG-910 | P,F,Attachment
| Survey & Setout | Issued For Construction Drawings MSF-EN-CIV-DRG-910 | P,F,Attachment
Material Procurement
| Structural Steel | Issued For Construction Drawings Delivery Dockets if Imported Granular Fill from Offsite is Used Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite | P,F,Attachment
| Site Concrete (As Required) | Issued For Construction Drawings Weak mix 10MPa Concrete | P,F,Attachment
| Concrete | Issued For Construction Drawings Manufacturers Documentation Inspection Records All reinforcing bars shall be Grade 300E and 500E to AS/NZS 4671 as shown in IFC Drawings NZS3109/3112 All reinforcing and formwork to comply with IFC drawings | P,F,Attachment
Construction
| Excavation of Foundation | Issued for Construction Drawings Remove topsoil back to subgrade material and place in suitable storage location with silt controls Foundation excavated to line and level shown in IFC Drawings | P,F,Attachment
| Compacted Harfill under Inverter Foundations | Issued for Construction Drawings 200x800 Compacted Hardfill Pad under footings
| Concrete | Lines, levels and dimension as per Issued for Construction Drawings MSF-EN-CIV-DRG-910 Concrete to be min 30MPa at 28 days Test cylinders taken Dimensions to match IFC Drawings with tolerance of +/- 1mm Prepour Inspection Record Completed prior to pouring | P,F,Attachment
| Placement of Footings | Lines and levels as per Issued for Construction Drawings Full contact is required between middle strip footing and inverter. Packing may be required to ensure full contact is achieved Use drypack for installation of inverter if required with min thickness of 20mm | Holdpoint,P,F,Attachment
Backfill
Close-Out
| Asbuilt Recording | Asuilt records supplied of inverter foundations in place | P,F,Attachment
| Non-Conformance-Reports | Non-Conformances Closed Out | P,F,Attachment
| Handover | At completion of works QA/QC Pack is handed to client Client Verifies Work has been completed correctly and all quality documents are in order | HoldPoint, P,F,Attachment