## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
6facfb0c-5759-4ec3-b23c-d8d68dc48160 | checklist | C - 7051 ITC-ITR - Mechanical ITC | itp | Mechanical ITC
8f39aa89-f948-4076-9ba1-ddca8d5476d0 | section | Location Details
1aebb473-fd27-4387-bc62-09681d46aefe | checkpoint | Details
e36ce310-9d7b-5b6c-951f-48fa79e9af20 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
77124a0c-1d70-54ea-ba20-acbcf7960a08 | textbox | Row Number
1ad1c1c0-4bda-5cae-bbdd-e2e68e938950 | textbox | Table Number
9b22b676-50f5-4c89-b9e8-52889d22f11b | section | Construction
71c22888-0d21-40d8-bba3-d16ae90c69a4 | checkpoint | Mounting of Girders
f1586f09-024f-595c-8246-2bbeb5a2ded1 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
800c92c6-bd42-546a-a5ec-89d17ccce8ef | note | ITC Mechanical Installation
94001e3e-ef88-527e-a228-1e1ed27bdeed | note | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
02915e6f-5b1b-5d30-932b-36f277ec8b1e | note | Torqued to value of +/- 5% of 53.2 - 58.8 Nm
3f3228ba-ccd9-560a-ac24-348323cc83bf | note | Each bolted connection shall be marked after torquing
9b8c4c53-26ca-4f54-bc41-dfa40c63f9c5 | checkpoint | Girder to Foundation Post Step Check
690c8009-69a9-5224-b363-b563a5591351 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
09ae7102-fdef-5892-8a7a-2561b534bcf4 | note | ITC Mechanical Installation
76351a79-1260-5ce2-986a-4be4795ac3db | note | Angle of the Girder to the horizontal to be an angle of 23° +/- 1°
4292ae4a-3064-46d1-be9f-f8e2bf523170 | checkpoint | Purlin Connector Installation
12bdf820-8113-5509-8b3c-24b41ada5f72 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
960b36ea-b8fa-57de-96fd-c802dc07a254 | note | ITC Mechanical Installation
fc55cb3e-eae8-59c7-9711-3f9f4bff11f0 | note | Purlin Connector placed under purlin
26bb3e8f-6735-54f2-a245-e7ba28541157 | note | Screwed together with Four x M10x25 bolts for LC/LT Purlins
85e1e245-e983-5605-a05c-e4d4d06f77c0 | note | Tightened to a torqued value of +/- 5% of 32Nm
9652dcff-c18f-586a-9eee-6c630c3aebee | note | Each bolted connection shall be marked after torquing
31c498ab-227f-43f9-b14b-ce5f62163dea | checkpoint | Purlin Mounting Checks
30490f0a-73fc-5cc4-846f-3977d09763ff | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
d169c3a3-a0c5-50a9-a7ef-93793e281bd2 | note | Purlin placed on top of the girder in correct direction
4446e3b4-dce5-52ae-8d11-e8e8fa868026 | note | FS Gen3 Girder Purlin connector bottom part attached
650c67c2-85e0-5c26-9c42-385321a08d0c | note | FS Flex Claw Installed
e6d1d163-ac27-52d9-a773-f1ce4d17f90c | note | Purlin Connector Attached
53bbf837-b92c-5297-8487-0893b38e03f1 | note | 3x Lengths as per IFC Design
94ef7cb8-612b-5dca-adb5-567f05dfc591 | note | East/West 4320mm-5310mm-4320mm
cf4fa027-2e4c-4b61-95c3-2d49993699eb | checkpoint | Connection of Girder and Purlin
d383810c-7ab6-5526-a238-e0046145473e | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
369f821f-69fd-538b-bb4f-3044878d99e2 | note | ITC Mechanical Installation
6cae3466-f3a5-510a-bbb2-906bb91d91bb | note | Girder
8648c22b-9079-558f-b11d-5953797010c7 | note | FS Flex Claw
e6e3017e-7922-51de-b198-89522870c55c | note | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
6fef94e0-bbbc-570c-88b0-1e77fba5f6f8 | note | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
4e8aa4e6-6548-446d-8c44-4046b5a3905f | section | Close-Out
018ab7cd-5595-4eac-be85-521add1dd73d | checkpoint | Non-Conformance-Reports
b775f3bf-6772-58f4-9d02-88951b664dec | note | Each Non-Conformance Reported, Rectified & Closed Out
ce391511-d7b3-47d6-bb30-e8c2c7b5b0ee | checkpoint | Table Mechanical Work Completed
5899f4ac-fc8f-5f40-bc7f-e3eca6318238 | note | Works completed for the table and checked
fd5a576f-473b-4b7b-943e-ff2e0d9cb9a3 | signoff | SIGN HERE
b76b7a9b-318b-437d-bc18-a7ec03f51c99 | checklist | C - 7051 ITC-ITR - Panel Installation ITC | itp | Panel Installation ITC
84b004a2-9be3-449c-84d3-a7f33d0e9858 | section | Location Details
ca5eb87c-25ca-4860-99f0-9ae8037cadc8 | checkpoint | Details
a04f617c-9da7-56bc-bbfe-047c3387deff | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
8ea7f151-935c-5fc4-a5ae-9d73eed7ece8 | textbox | Row Number
a1311ff6-e0d0-5db5-ac45-99d5819d74df | textbox | Table Number
f2437099-edd1-4cf9-a2dc-e7c63076bb7b | section | Construction
8bfcf3c2-6a6c-493d-9ad2-ab9a97a157a5 | checkpoint | Placing Module Clamps on Purlins
48325882-3a42-59f5-ae10-906d1c653181 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
ee113c3c-48a5-50e2-b699-ca93148c228d | note | ITC Panelling
5fac6022-3747-4a71-be7b-a24718b157c3 | checkpoint | Align Module and Tighten Clamps
384f7a8f-11c9-5d83-b6fc-b867efe10f48 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
5930a196-55f5-56b7-a105-99968bdc8ade | note | ITC Panelling
23094c85-32c3-4d73-be19-1f07a67074f4 | checkpoint | Align Module and gap between panels as per IFC Drawings
5c399d65-97cc-58c9-b7ae-46c65ee8f07b | note | Schletter FS DUO - Fixed-tilt Installation Procedure
89965199-47b8-57cf-b127-ffb948a55f49 | note | ITC Panelling
11c9f901-9046-5a3a-80d6-d6079014a285 | note | Top Panel to Bottom Panel: 5-10mm
db11b132-62ac-58e1-9b66-aa53d5b99334 | note | Panel with Module Clamps: 22mm
fc17cff4-59b3-4dc3-ad8c-a1dea40cf119 | checkpoint | Ensure Panels are dry, clean of dust/mud and no visible damage
ff5892ce-07d4-5bd4-8bcb-032cfd6dfe06 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
3838f2e4-8cdf-5302-976c-fbbc28ac9ce7 | note | ITC Panelling
aa149fe5-58c8-4cab-8f43-a4aef239d07e | checkpoint | Ensure Panels Start and Finish at even distances of the Purlin
6960ed9e-33f5-55c2-8fae-bf347f714e6e | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
489c585b-42c5-5805-9e3f-bcda49c6964e | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
7701ec70-6dbe-586a-932f-145ecf772af1 | note | ITC Panelling
9f55b68f-a9fd-5f8a-9587-c6567dcd7bf1 | note | Panels shall be 50mm from the ends of the purlins
0cee966a-21b2-445f-b2e8-3a6ce4ced673 | checkpoint | Ensure correct number of panels are installed for each table
88ed8e54-fc55-5a66-a265-07efff007add | note | Issued For Construction Drawings:
5c1cc5e4-3160-55f1-b91f-aa767f5b5577 | note | 01_Maungaturoto_FS2V-23*-12_DUO_EX
e60d08b7-0697-571e-afbb-8c65ffc9e6e6 | note | 02_Maungaturoto_FS2V-23*-12_DUO_EX
2bab54c3-46c1-5875-8f3a-2ec2bf6bd96f | note | Schletter Electronic Design Data
b4f102ef-a2d2-5e0b-a58e-ea804572c3f0 | note | ITC Panelling
e7f7feb7-db97-4581-ab25-380707bef90e | checkpoint | Ensure Panels are properly secured
1baed857-9c30-5ba5-bae5-6746787c0f57 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
f9046feb-5654-5031-a0eb-f3aac28bb331 | note | ITC Panelling
044b050e-46c4-42fc-97b6-0ac1274e34a8 | section | Close-Out
379095e5-d8e3-4f18-a346-c93e7860af2d | checkpoint | Non-Conformance-Reports
46bc79cc-3690-50f0-904c-566dc82c778a | note | Each Non-Conformance Reported, Rectified & Closed Out
2eaa3569-3fe7-4b3f-981e-3e3cfc0cfa5d | checkpoint | Table Panel Installation Completed
9540b1ae-06aa-5aa8-aebf-392ec4bc838e | note | Works completed for the table and checked
c60af4fb-fb03-4d10-90b3-6192a63fdc7c | signoff | SIGN HERE
9f49e27c-2056-407f-a303-67f99efe0e7f | checklist | C - 7051 ITC-ITR - Pile Predrilling & Filling ITC | itp | Pile Predrilling & Filling ITC
5738c08d-86b4-4b6a-aee8-5fa146c5b879 | section | Location Details
6bda0d81-77cb-4baf-a585-016e28bbad72 | checkpoint | Details
1f596568-9c9d-507f-8dfa-9148345c32e3 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
66ad2c96-597f-5b8b-801e-4a4ad0ddb2be | textbox | Row Number
91a37380-a01f-5a03-b483-721e8c68ab86 | textbox | Table Number
70f7f60f-fc23-5a06-8c42-02366c104d8f | dropdown | Number of Piles | 8 Pile,16 Pile,Other
0360103b-28b5-5317-9919-255653afb097 | textbox | If other, please specify
e3e599ae-f55f-4332-8ef2-4fee6b7066a6 | section | Drilling
508c71b4-a95c-4f7f-85e4-a8ec8c1e6a25 | checkpoint | Drilling
d4c7ded7-3d17-504f-bc36-ddb4cd2b53d9 | date | Date
32a8bf2a-60c0-5fc2-83f8-d7746a1a43ae | dropdown | Drill Depth | 1.8m,Other
9e74df0d-62f5-5017-abf3-3376daa16e42 | textbox | If other, please specify
e7ad25dd-3d6d-5c45-a3cd-4b0337653a13 | dropdown | Drill Width | 300mm,Other
785ca52e-e1c9-5697-a6b7-6ce38cd7cc47 | textbox | If other, please specify
580325e1-ec8e-4ebe-8b42-1ddd964442ca | checkpoint | North/South Verticality +/- 3deg
4f869d6a-9a59-49ae-85fe-129effaa505d | checkpoint | East/West Verticality +/- 3deg
6b0be5bf-672c-427e-8508-ce8b7e30a93d | section | Fill
86af1137-75f5-4602-b8d4-a643a6ccc8d5 | checkpoint | Fill
a319c738-9a0b-5371-94d4-fcd294c63e29 | dropdown | Predrill Fill Mix | 5% Stabilised Sand,Other
ecee9879-2951-57c4-9cec-0a6851849d83 | textbox | If other, please specify
dd6b58a0-8c65-41a2-ab77-af337dd4ff94 | section | Closeout
bbed9555-0561-4c05-b15d-4bb6e7387509 | checkpoint | Non-Conformances Closed Out
60dfc178-4415-52f2-9e08-50d4227ea150 | note | P,F,Attachment
f66a321b-e6e7-4aae-b3b0-8c6903328278 | checkpoint | Works checked & completed
c7e82b73-561e-4f34-8ad1-5c8aae3e0c77 | signoff | SIGN HERE
d4d49fb6-a788-4d67-84f9-aaa64d7adb28 | checklist | C - 7051 ITC-ITR - Piling ITC | itp | Piling ITC
2c59cffa-f77b-4d48-b2d7-2e806a3e03bf | section | Location Details
9c43fd9e-4ab9-4d18-ac64-e1cb29eb2f0b | checkpoint | Details
3b82aae6-5a76-572f-95c6-1cc5e99ffd5d | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
f85f1388-86a3-5eb1-a74a-76626ec0c47f | textbox | Row Number
9369a1e5-1e49-5c9e-802d-6220f2b28de8 | textbox | Table Number
4225b7ab-74b6-53ba-921d-b496e0bb45e8 | note | Number of Piles
ad779398-5f71-5d89-8baa-a2dca8f399c0 | tickbox | 8 Pile
b715c811-2158-5a46-9b66-f3651cf0aa6e | tickbox | 16 Pile
a6bb2bd2-2ac6-5deb-803c-5138e91c4ef5 | tickbox | Other
1c7c3fc3-5164-5713-a8ca-5365030f5d27 | textbox | If other, please specify
244f7754-8063-4499-b3fb-d7609a4b84fd | section | Preconstruction
f921aff3-73fa-4411-9681-aeb8f23c42a3 | checkpoint | Design
a0ea1765-f33c-556c-8db1-2c02a751306c | note | Issued For Construction Drawings:
4ce14052-82ce-503b-b87b-04a347a716b7 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
ae7911c9-e560-52ec-9e53-55e1e43160a9 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
e2cd379e-5ed3-5361-9912-6b12a9e306ce | note | ○ Schletter Electronic Design Data
3a1fb47c-814c-5a95-a3f6-2cfb62fee010 | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
25a4f4df-d6df-4c04-bf5f-17a621e964d2 | section | Construction
8b8bf062-7a28-4692-ba3f-4b4c092bd04b | checkpoint | Pile Distribution to respective blocks
99963f40-6f90-5d52-b019-199abc31f7cd | note | Survey Data
a75bdad7-8e4a-5cc5-9a53-4c9f91cece91 | note | ○ Schletter pile location data
4be5c9e6-a222-525d-abcc-cb7b13150a77 | note | Visual Inspection
79a1c68b-91d3-5d2c-a55f-6fc85947f830 | note | ○ Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
706c3ff7-9c79-41c3-ad35-c70246f52a52 | checkpoint | Pile Refusal
ed7bec2c-cf94-52d5-9c4f-e94704de5660 | note | Drive piles to depth until they reach the point of refusal
42d03e63-fa10-5f0b-b531-44ac68aa0f5d | note | Record Pile location and mark on the drawing
eb386e04-e1ec-5c21-9af0-e5e1b8545979 | note | Record Actual Pile embedment Depth
785d5259-a18f-5421-8df7-56fb9ca58ef2 | note | Pile refusal in accordance with pile refusal procedure
1e2057e4-f9bc-550e-a882-22319dcd9b14 | note | Piles cut and holes drilled as per Schletter documentation
f61bee56-07eb-51c8-99cb-4b5088f2adb3 | note | Survey Record
2aa8946a-5fd5-52be-92cd-7d545f13c7f7 | note | ITC Data Tracker Excel Pile Monitoring Sheet
c8bebe9d-7286-5f44-9d65-69d4e85140e4 | note | – Embedment Depth
a3a44430-0007-51d0-98fc-4bcf23375d54 | note | – Reveal Height
12a3de77-aa35-572b-920c-8a58256807d2 | note | Pile Test Result documentation
c35cc98a-b980-4715-b484-7646e490d23f | checkpoint | Pile Predrill to minimum embedment
aa630883-4e45-5105-b929-ebcda616487c | note | For Each Pile
fab0c7ac-56ec-599b-ad2f-fda482e425e1 | note | Pile Predrill ITC
101bea9a-b9dc-5b72-a672-8583eb411b24 | note | Piles are minimum of 1.8m deep
0d78926f-396b-5c21-865a-292b968ca48c | note | Predrill holes are minimum of 300mm dia
b933a6ba-11b0-5cfe-977b-a2eac0a422bc | note | Backfilled with approved mix as per Schletters Installation Procedure
9141426a-a547-4da5-969c-a4c85c66f271 | checkpoint | Pile Installation
bd89ef17-f188-50d5-a6f8-7ff6c731360e | note | Schletter FS Duo Fixed-tilt Installation Procedure
d6824b71-5bbb-53eb-a05d-8df04b9dfc97 | note | Install Pile on the correct location as per Schletter drawing
d1764b30-9533-5467-88ae-a507148d6e37 | note | Install pile within the design tolerances
21c79310-7a83-573b-b074-5fe76a1ce81a | note | Piles should have no damage or deformation and in correct orientation
4c9d0a4f-3882-5498-a68e-074e5cb7d634 | note | North/South +/- 3°
4370ace4-7833-5bf9-afa6-060ad484673a | note | East/West +/- 3°
ff9adf8c-6d55-5325-9955-703518748c9b | note | Pile Twisting from axis +/- 5°
dbd6eb9d-569e-55ca-b90d-d3312337a4bc | note | Distance E/W +/- 100mm
9296f22c-88b5-5338-9934-e08f5cbc6238 | note | N/S +/- 50mm
19845f46-16ec-5fa4-a8fd-bc5253e4f5a2 | note | Reveal Height +/- 100mm
e1e10c35-b30c-58be-ae80-8957743454fc | note | Height difference foundation posts within one row +/- 50mm
6a234024-ceba-5e06-9188-4e4ca330d310 | note | Piles have no damage deformation and in correct orientation
5f1aa039-e75e-4689-af9e-c8fd46a3505a | checkpoint | Cold Galvanising Repair, if required
4f5df91c-934a-5069-99ac-af64d836d7ba | note | Schletter FS Duo Fixed-tilt Installation Procedure
31998d24-1d0d-538d-82ff-7b27df951c2a | note | Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
8ede4410-24f4-48e9-921c-cff85c54e3b1 | section | Close-Out
afb5eeb7-147e-47f3-8534-0a4a2fa23912 | checkpoint | Non-Conformance-Reports
c125d2fd-915a-5415-8300-09a008f2e125 | note | Non-Conformances Closed Out
c842c45b-15c3-4a61-a52e-ae8a6ffa7425 | checkpoint | Table Piling Completed
fd61497a-e171-51a2-ad5a-0444e1fca77b | note | Table Piling Works checked & completed
aa03b4be-9620-4ec8-99bf-fe15e653eebb | signoff | SIGN HERE
acb67c16-99c7-4b39-91f4-684b49e4ff05 | checklist | C - 7051 MSF Mech Piling ITP - Mechanical ITP | itp | Mechanical ITP
d0241fd8-62d9-4cf3-85f0-438917ddb5f5 | section | Location Details
ee3d459d-edb8-4503-9b06-87e80294a6bd | checkpoint | Details
922d2ef2-0d57-5c07-8696-b276abcdab8b | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
72def926-9ec2-51ab-987d-6d317b4b4938 | textbox | Row Number
18bf7b1c-7c84-51cd-947c-665f9984aa10 | textbox | Table Number
cf6d9be8-8788-41ab-98bf-52a59167adda | section | Preconstruction
9d41c767-4103-4443-ab65-5abd214a379c | checkpoint | Design
17841698-77c6-516b-a2f1-d59b37731676 | note | Issued For Construction Drawings:
fe807eeb-5043-556b-a735-b3afdff43513 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
fcb0d267-8823-5730-8021-b1c984eabef5 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
541e2963-2618-5b8d-b63f-659c6a2f02df | note | ○ Schletter Electronic Design Data
4898b1ad-5888-531a-9a53-9f9d6c109efc | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
2585b6ac-d9e6-4851-b1ab-97dc4fee1846 | checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
27292218-0e51-554e-bdff-a7e12e661586 | note | Supply of all calibration certificates
8cfc7d5e-db35-42c9-87bc-c84204608748 | section | Construction
932e5278-565c-425a-a96b-dc5a99072cdc | checkpoint | Mounting of Girders
6156cba5-1aab-544f-99a7-a38d36ba04cf | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
446609b4-7c70-5c97-9583-4b60aa6a8b39 | note | ITC Mechanical Installation
a08b4369-b812-502f-a9f2-8dc6847231d1 | note | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
68289682-69a7-50f9-ba7b-0553f783b9e7 | note | Torqued to value of +/- 5% of 53.2 - 58.8 Nm
6966ab79-8230-5dc3-bd40-334157713be7 | note | Each bolted connection shall be marked after torquing
3d4ee4d8-5615-4f89-9d57-9b0149769a1a | checkpoint | Girder to Foundation Post Step Check
3de09105-5cba-5021-b0b4-f52f1113120e | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
b4affaea-f403-5e8f-b757-d2941f9aeb6f | note | ITC Mechanical Installation
f64d887e-9d90-5de3-97a3-25c0e4984869 | note | Angle of the Girder to the horizontal to be an angle of 23° +/- 1°
d55413b7-2518-4f40-9821-678b066f3e80 | checkpoint | Purlin Connector Installation
109d315f-fb9f-52eb-a76c-fd1833303c4e | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
45b0ac36-9ff3-5042-bf43-ad01383eb084 | note | ITC Mechanical Installation
83e1dca9-a550-5583-a4d6-809c8d62b727 | note | Purlin Connector placed under purlin
ee0f2625-657b-531e-908d-930ff223939a | note | Screwed together with Four x M10x25 bolts for LC/LT Purlins
b9c7479d-bf68-5c1e-9902-58b7b7e0a04f | note | Tightened to a torqued value of +/- 5% of 32Nm
bb0c3b9d-575c-559c-b178-9ddbdcd7e05f | note | Each bolted connection shall be marked after torquing
cd6aab3a-8459-407a-9a58-862e9dade8ae | checkpoint | Purlin Mounting Checks
d3db74d8-366e-5987-ba3f-013c5b0bb9f1 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
caaad179-b79c-51d6-80bc-bbbfd6b24941 | note | Purlin placed on top of the girder in correct direction
17a48204-df80-5994-adf8-1411082ba2b9 | note | FS Gen3 Girder Purlin connector bottom part attached
8c1137ec-287d-500b-aa00-a972f6404f51 | note | FS Flex Claw Installed
e40ef6e3-d348-511a-9999-d203464ed7f6 | note | Purlin Connector Attached
5ec94299-a1db-5fba-ac1c-a457a5064cff | note | 3x Lengths as per IFC Design
77a325c3-ef4f-58b3-a721-2f2d64b7e99e | note | East/West 4320mm-5310mm-4320mm
6e4ec1a2-2fbc-49d8-95b1-2c5b542a4f1c | checkpoint | Connection of Girder and Purlin
a6bc3bea-d9aa-5db7-9b29-e639bc095785 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
a89f56c0-0479-5687-b90d-66be67451807 | note | ITC Mechanical Installation
9d273922-7b5f-5579-97b4-2a51f4875340 | note | Girder
ab39376f-7d1b-5b71-8633-aed1d82e2b42 | note | FS Flex Claw
6fb9b073-cf63-5c2f-9d03-62295c1d9f17 | note | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
79173cad-f2d3-545e-8e31-a050772d2c69 | note | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
6ef25508-15c5-4843-bd5e-acfb11078718 | section | Close-Out
e29bdd02-49e2-491d-a6cd-ac13ff0144d8 | checkpoint | As Constructed - Redline Markup Drawings
92d9ff4a-7af1-562b-a628-f620833157a9 | note | Red-line As-Built constructed records supplied
899d555c-36fb-428d-99bd-42ee950fb431 | checkpoint | Non-Conformance-Reports
2c1778b0-d8b9-5ee0-950b-03eaafe85cbd | note | Each Non-Conformance Reported, Rectified & Closed Out
f7fffefc-ae3a-43d3-9c84-bcb37ea8c987 | checkpoint | Punch List
995edbf6-d4fe-5892-9f37-14183f7e40fa | note | Development of Punchlist with PM/CM and or Supervisor
a043eb0f-3299-5916-beaa-91501919c569 | note | Punch List closed out in a timely mannor
44d27658-c532-40b3-b3b5-b677daa5021e | checkpoint | Handover
c4a4ffa4-6932-503f-a597-29b64300cfc1 | note | At completion of works QA/QC Pack is handed to client
37ca6f20-87f2-5b8d-8ee3-37da33431c14 | note | Client Verifies Work has been completed correctly and all quality documents are in order
2df054cf-a33f-43b6-810a-4d493b89938d | signoff | SIGN HERE
2e61e5fc-e4e6-4ed0-8468-011274506c06 | checklist | C - 7051 MSF Mech Piling ITP - Panel Installation ITP | itp | Panel Installation ITP
64653546-7bd5-4b05-aac6-0897d446024e | section | Location Details
800ef44a-1514-45bd-9210-2f364eb016e9 | checkpoint | Details
af0fd0a7-6b3a-5795-a064-ac742d545793 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
5d5d6983-8607-5b9d-93fc-67739029ab7e | textbox | Row Number
9b3e1086-e459-5c72-85d6-40ca2dcfe1ff | textbox | Table Number
5beca7c2-c6f6-465c-9fcd-0367e160af72 | section | Preconstruction
805a4cd8-8834-401e-80e4-525b5f728bb5 | checkpoint | Design
08241593-cca5-56b2-b793-da33931f897c | note | Issued For Construction Drawings:
b62c8229-0156-5998-b50f-74b879f39d59 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
f25d5680-08cd-5c2d-9112-03e24b94ee06 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
ffe8a830-7bb4-563b-98d8-d47403d9ed29 | note | ○ Schletter Electronic Design Data
cb259b66-000f-543e-aa12-4541bd88155b | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
ccabc690-4f9b-4d69-9c84-913135ced025 | checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
0771bcc0-9c63-5a8f-aa3a-7042d17bfd9b | note | Supply of all calibration certificates
022ef4c7-64ff-4562-b174-1ad70896e88d | section | Construction
28e8e738-b12a-475c-9ac4-23bd826cebdc | checkpoint | Placing Module Clamps on Purlins
3cfd94cc-15c1-5099-92b1-8c5e5c0c312e | note | Schletter FS DUO - Fixed-tilt Installation Procedure
d4ac6053-a535-5cd5-8186-7d7816856030 | note | ITC Panelling
08f1d335-48e9-4cf7-8a4b-3ac1bb9bc51b | checkpoint | Align Module and Tighten Clamps
2f71ca0c-867e-5a1e-ac3d-852de8ae76d6 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
045f9447-e01b-597c-bcec-55dfb456dc76 | note | ITC Panelling
a64f2239-7a97-4f41-86fd-42998105d4a0 | checkpoint | Align Module and gap between panels as per IFC Drawings
23b66150-bc34-57b5-88f5-3d28d494844b | note | Schletter FS DUO - Fixed-tilt Installation Procedure
0f936382-1671-53e1-8896-0e4205f7f36b | note | ITC Panelling
577d8a36-0a64-538a-b835-81422df68043 | note | Top Panel to Bottom Panel: 5-10mm
ec02fd46-801f-58fd-a6c5-a5d9008a4b52 | note | Panel with Module Clamps: 22mm
02b1c27a-ca9f-4929-be72-25c5c78d796d | checkpoint | Ensure Panels are dry, clean of dust/mud and no visible damage
5a483cab-6e42-55da-8649-94623760b3d2 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
855d083c-7e0b-5b54-b719-7e74d7ec4ab9 | note | ITC Panelling
5fd9a11c-c4f5-4d63-9ade-30c030de1243 | checkpoint | Ensure Panels Start and Finish at even distances of the Purlin
ca6f9f63-0111-55af-b91d-c55c36aae3bd | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
9fe49139-1f1a-5326-8728-913a7dee59c2 | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
5a304470-fdce-5176-b77a-50c0465fa0f4 | note | ITC Panelling
fce15151-1d9d-5328-a2d7-8185508b510e | note | Panels shall be 50mm from the ends of the purlins
5df920a1-f3c3-436b-a9b8-4dd0c9026516 | checkpoint | Ensure correct number of panels are installed for each table
8e6037ef-7043-5980-ab90-687837c8a07a | note | Issued For Construction Drawings:
c7a78ecb-89f2-5289-ad79-6a8497b69a95 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
ce4b2216-5d8e-5441-9ead-642a7fe58dd5 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
d8a98a5b-f438-5212-991e-7ca8db87c7a5 | note | ○ Schletter Electronic Design Data
bae567bd-b7c4-5440-b3d5-963d50d69fbc | note | ○ ITC Panelling
ea53607f-8a17-4bff-949a-9fb99134fcb7 | checkpoint | Ensure Panels are properly secured
105c94bd-2ff1-58b6-9b4c-6183a9a9a323 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
c746d317-69d2-53a1-9671-e8172c316dc8 | note | ITC Panelling
f23e25db-7af9-42a3-b1f7-48755c11e82d | section | Close-Out
eca743ae-f8e6-43c8-bb01-1b2bf89a226e | checkpoint | As Constructed - Redline Markup Drawings
24421239-7dd2-5733-bd41-63023842a09d | note | Red-line As-Built constructed records supplied
c18d0019-4137-42c7-9001-773aa177ec61 | checkpoint | Non-Conformance-Reports
e4674f42-ae29-516f-9acc-8d004d14c3f9 | note | Each Non-Conformance Reported, Rectified & Closed Out
eeffe585-a130-4d6a-ac64-5a5cb74995e6 | checkpoint | Punch List
8bc23ae3-8874-5744-bbea-40e98a9662f8 | note | Development of Punchlist with PM/CM and or Supervisor
94ed1e7c-d66c-5dd8-839a-0e1c73a483b5 | note | Punch List closed out in a timely mannor
c10eedaf-87a4-40fe-84a4-4e8c86f9040d | checkpoint | Handover
aedf6f65-7091-5e22-8ef5-a06f87e4ff82 | note | At completion of works QA/QC Pack is handed to client
25530a46-9e25-5bbf-88c6-b734228e993d | note | Client Verifies Work has been completed correctly and all quality documents are in order
992a7783-7bc6-4203-8680-731f848b375f | signoff | SIGN HERE
3275fde3-0216-49a9-a70e-61726c5a294a | checklist | C - 7051 MSF Mech Piling ITP - Pile Predrilling & Filling ITP | itp | Pile Predrilling & Filling ITP
1c8ee9b8-439e-48b6-8e6f-5d3234eda661 | section | Location Details
0efc51ee-67df-4a28-8b1a-47b8f5626b8d | checkpoint | Details
7ef90fa2-6ab9-531e-91f9-cdfd2ce517ee | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
8a850764-3c26-576a-9ecc-b5ea25823291 | textbox | Row Number
79e1abe6-641b-5e6d-9f16-94a53a4e532d | textbox | Table Number
e925f540-1e39-5cd9-8779-51e1cb5371f1 | dropdown | Number of Piles | 8 Pile,16 Pile,Other
afd666ae-b12a-5043-b5a9-3b0d83104dfb | textbox | If other, please specify
4aff9149-c884-455b-929b-a3672b71708b | section | Drilling
b11938da-bc8c-4848-b88f-fc19657f2069 | checkpoint | Drilling
81ba20e8-09f6-57cd-87c4-78c203bf16e9 | date | Date
bd5716af-cd89-503d-9632-964df44705c2 | dropdown | Drill Depth | 1.8m,Other
59d15605-1db7-5a0a-b86e-b8613adf3dba | textbox | If other, please specify
39ccf2ec-0e5b-5e3c-b529-4267502186b9 | dropdown | Drill Width | 300mm,Other
42f90c0d-4685-5ace-a260-b7cbbbc23b43 | textbox | If other, please specify
6ecc2930-6cad-48ee-bc7c-b5997ff7d737 | checkpoint | North/South Verticality +/- 3deg
ff380154-7a9a-4a5c-b840-47e47b8d2b24 | checkpoint | East/West Verticality +/- 3deg
88c358a2-3473-4335-92a1-7eebbe30072e | section | Fill
0a20bcc0-f2da-4c9d-8bd8-1df70bc6af35 | checkpoint | Fill
8f7ee1f4-080c-5d4d-800e-5f6ba29c4941 | dropdown | Predrill Fill Mix | 5% Stabilised Sand,Other
d01506a3-5970-561f-a2c2-b35224a7c353 | textbox | If other, please specify
5d331144-44cf-4926-8872-2b969cce0e77 | section | Closeout
d097841e-e7ed-42f4-9585-9b4bc5c7a7e5 | checkpoint | Non-Conformance-Reports
11470ce9-d6cb-5bcc-b062-8f4762eddaa1 | note | Non-Conformances Closed Out
60b23068-cdd8-406c-b1b6-dffc5697dc33 | checkpoint | Punch List
246ee27f-66b4-59fa-9c90-0e6197775b91 | note | Development of Punchlist with PM/CM and or Supervisor Punch List closed out in a timely mannor
93c99146-f193-4837-9adc-3afcf64b9da2 | checkpoint | Handover
80f49972-0138-5b14-b6e7-741192f9db2d | note | At completion of works QA/QC Pack is handed to client
3938e0ce-c90f-52f8-b2d1-9ec8059d82ad | note | Client Verifies Work has been completed correctly and all quality documents are in order
315bfa72-0a8e-4f82-90cc-0d7e61c741a1 | signoff | SIGN HERE
4a81aa26-f953-444e-874c-f2eec65d5775 | checklist | C - 7051 MSF Mech Piling ITP - Piling ITP | itp | Piling ITP
83563d74-3222-46bf-b022-befee1e63a3d | section | Location Details
c1093c73-a28a-4f13-8727-fccd164bf707 | checkpoint | Details
0489ea10-5671-5b5c-93e7-ae7c0fb0829e | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
a1f12fbc-214a-5ab2-b813-3b384974b577 | textbox | Row Number
fdf63556-ffb6-5bc5-834a-356cb03c3dcf | textbox | Table Number
05f680cb-b3b3-55cc-8ed2-dd70d89ac55d | note | Number of Piles
6d75e24d-18d5-518a-a388-dcdcfb38a03d | tickbox | 8 Pile
09b0c80e-1dcb-596b-9f8e-c3a3838fe5e4 | tickbox | 16 Pile
360fb29a-88f6-5482-8a6e-0b9fe706afa7 | tickbox | Other
6734c79f-dc9c-57a0-8b0c-487b404e8fc0 | textbox | If other, please specify
66965ec5-4e6b-4fdb-80a3-67698c0e4313 | section | Preconstruction
8b19145c-9a23-438a-ba1f-6121882d492a | checkpoint | Design
891c1d98-d3f7-574d-935a-abf763747e87 | note | Issued For Construction Drawings:
a5bbe4db-776b-53d1-bf40-7c04397bd14c | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
592b9ef4-e082-52ea-a642-847bc9f70c03 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
c0ff6250-31a4-5538-b79b-91eb46158b00 | note | ○ Schletter Electronic Design Data
8754aff4-9b85-551b-afed-84782fcaad01 | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
82f30769-415e-4074-95fb-e0b430adda4a | checkpoint | Survey & Setout
9db06213-f89a-5f3b-b633-0d778cf17b2e | note | Schletter Electronic Design Data
d731d49e-2635-5860-af87-d0dbd26a2f79 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
00419672-e3da-5914-b847-45df658a512d | note | Survey As Constructed Record
fc082ab1-7853-59cd-be7c-b4f9dc5017e9 | note | Pile Location Spreadsheet
cb8badc8-29bb-4daa-8c33-380ed767b059 | checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
80e98806-63c6-515a-977f-fae2324c289f | note | Supply of all calibration certificates
0d92d15f-7bd7-4724-aa74-7ada3ec96205 | section | Construction
12da39be-9320-4831-97e6-d95f8cd930ab | checkpoint | Pile Distribution to respective blocks
f4203caa-e81c-5606-8660-0ac8f99c0296 | note | Survey Data
b4aa54a7-684f-523d-b543-9f5e2cd4093d | note | ○ Schletter pile location data
384e3d30-6ac6-5698-839e-01d46bf6e78a | note | Visual Inspection
5b70bf16-7cf7-53a9-aebc-d23cae3811a7 | note | ○ Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
0229d1f1-b624-4b6b-8bb0-f88ffd75358e | checkpoint | Pile Refusal
4023a66d-5773-53db-9b25-9d8c45845e91 | note | Drive piles to depth until they reach the point of refusal
93a17476-dc33-5cf4-8ee5-cacf91eec59c | note | Record Pile location and mark on the drawing
f41673a5-fb82-516c-8973-4947c6aaf146 | note | Record Actual Pile embedment Depth
9dd89a15-d0e5-58e1-a8b4-7963f15186cc | note | Pile refusal in accordance with pile refusal procedure
3e54b820-9629-59f5-af08-6763a3ced2ac | note | Piles cut and holes drilled as per Schletter documentation
9a82180c-e056-5233-9a89-0521a3fb32a0 | note | Survey Record
0492a1cf-8677-5565-9e6f-7c22fcedac1d | note | ITC Data Tracker Excel Pile Monitoring Sheet
899512a5-ae47-5014-8ef9-ab1527dc0b01 | note | – Embedment Depth
a8ccc813-baa9-5627-9bda-270c5ec89530 | note | – Reveal Height
049efbab-e7fa-5ee8-aa76-62609538e126 | note | Pile Test Result documentation
adfae426-4e3d-4b3f-b497-c89d63fdc739 | checkpoint | Pile Predrill to minimum embedment
93625151-5172-5c4c-b4f0-665885cc5d98 | note | For Each Pile
005ea06b-c66a-5a74-9492-524876d3fbfc | note | Pile Predrill ITC
b514fa02-a888-53b5-a0f8-7f8e7be53245 | note | Piles are minimum of 1.8m deep
6d52910d-ace4-5ff6-8c58-8b8864751cdd | note | Predrill holes are minimum of 300mm dia
c9a3a254-22f3-5327-a419-70da6fe35bb1 | note | Backfilled with approved mix as per Schletters Installation Procedure
f71d80e2-bb5e-4f1f-baf9-3181bee194a2 | checkpoint | Pile Installation
032d0a98-0a4f-5616-ab01-1a921c46c8a7 | note | Schletter FS Duo Fixed-tilt Installation Procedure
b8efa909-00a1-5f20-896a-39209e51cca8 | note | Install Pile on the correct location as per Schletter drawing
ea812ec8-659e-5aee-96ab-581eea1cecbf | note | Install pile within the design tolerances
758db868-dc51-5d54-a226-b3c56dcab2dc | note | Piles should have no damage or deformation and in correct orientation
bbc421dd-108e-5f00-a589-f598e14ed916 | note | North/South +/- 3°
5be5ffd0-6450-595e-9096-8af2e65348a3 | note | East/West +/- 3°
473043eb-90cb-521f-9808-261ddd5fa78f | note | Pile Twisting from axis +/- 5°
6ba5abfe-fec6-5713-82fc-27621c6e52fa | note | Distance E/W +/- 100mm
8783be47-bcc4-56a9-aa82-1b1e9b0f7936 | note | N/S +/- 50mm
38d828db-d017-58e2-a716-0b4ca6c09b4d | note | Reveal Height +/- 100mm
7d555d2c-7e0b-5157-a2c1-c68cbfa26654 | note | Height difference foundation posts within one row +/- 50mm
6766b114-2b4f-5ecc-b642-8f65ecf62e83 | note | Piles have no damage deformation and in correct orientation
8bdf4f30-9803-4290-9337-ef507f080301 | checkpoint | Cold Galvanising Repair, if required
fbf76eb3-d117-5af0-9daa-9c0750ac2f54 | note | Schletter FS Duo Fixed-tilt Installation Procedure
8299145c-52b8-56a7-8322-a0a911f618b0 | note | Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
18a940fb-e2f0-4567-9a97-eed0b1961487 | section | Close-Out
68ea2993-922e-4520-b279-d5d949203676 | checkpoint | As Constructed - Redline Markup Drawings
b435ccb1-cdad-5b25-8fbc-d3f544cfc1a3 | note | At completion of the the piling for each area
b3f36903-03ba-5e8d-b44f-c42d1d2b4fea | note | Markup Redline Asbuilts if different from design and identify changes
2b6a9693-9f9b-4c1d-8c71-2073623b2fd8 | checkpoint | Non-Conformance-Reports
0386f7a6-6b2a-5ea9-98eb-70d488614fa8 | note | Non-Conformances Closed Out
7ec3b818-0887-4db7-8863-958a3ff9f258 | checkpoint | Punch List
5f9a12f6-4e0d-55c8-afa3-0fda8c520eab | note | Development of Punchlist with PM/CM and or Supervisor
27360638-b24d-5fd3-9664-a91eca2e2fb7 | note | Punch List closed out in a timely mannor
745fcd1f-529c-485b-8c27-2ab9c61e6861 | checkpoint | Handover
267a5085-abe9-5af7-8d27-ee6e0a9c5db7 | note | At completion of works QA/QC Pack is handed to client
7e6b79a1-be18-5e78-9049-5ed663169910 | note | Client Verifies Work has been completed correctly and all quality documents are in order
0a1f9f18-2ce8-4565-bc11-bc57b3ca619a | signoff | SIGN HERE
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments