## Table 1
` | [5 empty] | Inspection and Test Plan - Control and Supervision of the Works | [12 empty] | Doc ID: FH-ZU2-QU-ITP050 REV: 0
Client: Melbourne Airport | [7 empty] | Contract No: CP14038-01 | [7 empty] | Prepared By: Ahmad El Wazer
Project: Taxiway Zulu | [12 empty] | Reviewed By: Jamal Khodr | [5 empty] | Date: 04/08/2025
Construction Process: ALER 3 ICT Installation | [12 empty] | Approved By: Marco Poggenberg | [5 empty] | Date: 04/08/2025
Specifications: ZULU-BECA-001-SPC-00005
Structure / Component: ICT Fibre Installation and Migration
Lot No: |  | Lot Details: |  |  |  |  | Lot size/Quantity: | [6 empty] | Date:
Item No. |  | Task/Activity Description |  |  | Inspection/Test | [11 empty] | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
[5 empty] | Frequency |  | Acceptance Criteria |  | Reference Documents |  |  | Inspection/ Test Method |  | Record of conformity |  |  |  | Project Engineer Principal’s Rep. Surveyor Foreman | Principal’s Rep. | FH | Date
1 |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  | Check for correct documentation |  |  | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  | Drawings / Aconex Register |  |  | Verify |  | Drawings and drawing registers |  |  | HP* | Project Engineer / Site Engineer
1.2 |  | Implementation of all measures and controls |  |  | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  | PSP, EMP, TMP, JSEA, SWMS, WP |  |  | Visual inspection |  | This ITP signed |  |  | HP* | Project Engineer / Site Engineer
1.3 |  | Submission & approval of shop drawings |  |  | Prior to commencing activity |  | HOLD POINT Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to: " Netshelter Comms Racks  Power Rails  UPS  Loaded Patch panels  Additional Battery Pack to suit UPS  Hard wired input and output for downstream switchboard" |  | ZULU-BECA-001- SPC-00005 - C3500.2 Drawings |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Site Engineer / Principals Representative
1.4 |  | Material Submissions |  |  | Prior to commencing activity |  | HOLD POINT Provide technical datasheets and compliance certifications for all ICT materials. This includes but not limited to: "• OS2 G.652D fibre optic cable (12-core microblown) • TE Connectivity or equivalent FOBOTS and patch cords • Cat6A UTP/FTP cable and modules • LC duplex connectors (blue or green coded) • Critchley label sleeves or heat-shrink tubing • Fibre warning labels, jumper rings, dust caps, cable markers • Cable trays: pre-galvanised/hot dip (min. 42μm) • UPS APC Smart-UPS 3 kVA" |  | ZULU-BECA-001- SPC-00005- C3500.2 Drawings AS/NZS 1252.2 |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Site Engineer / Principals Representative
2 |  | Construction
2.1 |  | Delivery of Materials to site |  |  | Each item |  | Verify each cable drum label, cable length, and ID matches the approved submission and cable schedule. Inspect condition of fibre drums and verify ends are sealed with heat- shrink and protected from dust or water ingress. All components shall be stored elevated on insulated racking. Equipment that has been damaged or exposed to moisture must be rejected. All fibre drums shall be colour coded yellow (OS2) and visibly tagged at source and destination. |  | ZULU-BECA-001- SPC-00005- C3500.2 Drawings |  |  | Visual Inspection |  | This ITP Signed Materials Inspection Checklist on ConQA |  |  | IP | Project Engineer / Site Engineer
2.2 |  | Inspection of installed Pits, Conduits, Slabs and Structure |  |  | Each Lot |  | Inspect that all underground conduits are clean, dry, and fitted with compliant drawrope. Duct ends must be bell-mouthed and sealed when not in use. Comms pits must include the following: • Approved pit covers • Earthing (if metallic) • Cable support brackets, • Internal spacers (where applicable) Ensure pit depth and position align with survey setouts and installation tolerances. Check slab penetrations are core-drilled or pre-formed as shown in IFC and sealed post-install. |  | Drawings |  |  | Visual Inspection |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.4 |  | Cable Pathway Inspection |  |  | Each Lot |  | Verify cable tray installation matches approved shop drawings. All directional changes must be supported with brackets within 300mm. Maximum tray support spacing is 1.5m. Confirm no tray deformation or sharp edges exist. Earthing continuity must be maintained with bonding links across expansion joints. Segregation dividers must be present where power and ICT cables share a common tray. Firestop penetration seals must be compliant with AS 4072.1 and identifiable by tag number or batch number. |  | ZULU-BECA-001- SPC-00005 Drawings |  |  | Visual Inspection |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.5 |  | Fibre Cable Installation |  |  | Each Lot |  | Fibre shall be pulled using calibrated tension monitoring equipment to ensure no tension exceeds 270N. Minimum bend radius must be ≥10x cable outer diameter or 80mm for microblown 12-core units. Label each cable at both ends using Critchley sleeves or approved printed heat-shrink tubes. Every 4 metres, apply orange warning labels inside shared containment paths. Route must follow a star topology structure unless otherwise specified. Keep micro ducts free of gel, dust, or moisture during installation. |  | ZULU-BECA-001- SPC-00005 Drawings |  |  | Visual Inspection |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.6 |  | Comms Room Fit-Out and Installation |  |  | Each Lot |  | Install racks, patch panels, and FOBOTS as per manufacturer’s instructions. All patch modules to be 19” rack mounted, fixed with screws and dust covers. Incorporate jumper rings, labelling strips, and drawer sliders where required. LC connectors shall be installed clean and dry, colour coded (Blue = PC, Green = APC), and secured to minimise bend strain. Verify the presence of cable strain relief and that unused ports are sealed with caps. |  | ZULU-BECA-001- SPC-00005- C3500.2 Drawings |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.7 |  | Comms Room UPS Installation |  |  | Each Lot |  | Confirm UPS installed are as per approved material submission. Verify battery and/or UPS capacity can operate normally for a duration of Eight (8) hours. |  | ZULU-BECA-001- SPC-00005- C3500.2 Drawings |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.8 |  | Control/Data Cable Installation (AGL & ICT) |  |  | Each Lot |  | Install Cat6A UTP cables in separate containment from power. Maintain ≤90° bend angles and ≤45m run length between active equipment unless boosted. Label within 300mm of each end. Each pair must be colour matched to the patch panel schedule. Testing of all the criteria for compliance with CAT6A, NEXT and ACRF values post-install to validate compliance with ISO/IEC 11801 Category 6A standards. No unapproved joins or patch- throughs allowed inside ceiling space or risers. |  | ZULU-BECA-001- SPC-00005- C3500.2, C3501.4 AS/ACIF 3009:2006 AS/NZS 3080 Drawings |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.9 |  | Cat 6A RJ45 Data outlets Installation (AGL & ICT) |  |  | Each Lot |  | Installation of all Cat 6A RJ45 data outlets are as indicated in drawings. Confirm mounting height of outlets on site with the Superintendent. Generally, and unless otherwise shown on the drawings, outlets shall be mounted at:  300 mm above floor level or 200mm above benches in commercial areas.  1400 mm above floor level in plant and industrial areas |  | ZULU-BECA-001- SPC-00005-C2141 Drawings 030-3100 set AS/NZS 3000 AS/ACIF S009:2006 |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.1 |  | Fibre Testing (OTDR + IL/ORL) |  |  | Each Lot |  | WITNESS POINT Verify fibre cable performance through industry-standard testing methods: • OTDR (Optical Time Domain Reflectometer): used to detect faults, splices, and measure the attenuation along the fibre length. • IL (Insertion Loss): the total loss of signal power resulting from the insertion of a device (connector, splice, or cable) into the optical path. • ORL (Optical Return Loss): the amount of light reflected back toward the source, which must be minimized to avoid interference or data errors. Conduct 100% testing of all fibre cores in accordance with AS/NZS 14763.3: • Use 1-jumper test method to verify Insertion Loss (IL < 0.5 dB per connector) • Conduct OTDR tests bi-directionally (A–B and B–A) for links >150m • Measure Optical Return Loss (ORL > 35 dB per core) • Include test at 1310nm and 1550nm wavelengths Submit OTDR trace files, link loss reports, fibre IDs, test configurations, and calibration certificates of equipment used. All testing must be supervised by the Site QA Representative. |  | ZULU-BECA-001- SPC-00005-C3502.5 Drawings AS/ACIF S009:2006 |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | WP | Project Engineer / Site Engineer
2.11 |  | Tray Earthing Continuity Test |  |  | Each Lot |  | Confirm electrical continuity of all metallic cable trays using a calibrated digital multimeter. Bonding between tray segments shall not exceed 1Ω resistance. Ensure earthing tails are installed and terminated using crimped lugs at each fixed support location. Earth point locations must be clearly marked and photographed as part of the QA record. |  | ZULU-BECA-001- SPC-00005-C1740.6 Drawings |  |  | Visual Inspection |  | This ITP Signed Stowe ITC |  |  | IP | Project Engineer / Site Engineer
2.12 |  | Air Blown Fibre Testing |  |  | Each Lot |  | All Air Blown Fibre (ABF) testing must be conducted using a calibrated tester with a valid calibration certificate not exceeding 12 months from the test date. New test reference leads shall be used. Testing shall include ABF Tube Calibration & Testing for each individual primary tube within the tube bundle in the following sequence: 1. Tube Air Flow Testing – confirm a clear airflow path over the full tube length and correct coupling sequence. 2. Tube Pressure Testing – confirm no leaks in the tube route or connector fittings by applying and monitoring a test pressure. 3. Tube Continuity Testing – verify the bore diameter and concentricity are suitable for blowing the fibre bundle without obstruction. Once tube integrity is confirmed, blown fibre shall be tested in accordance with the fibre optic test regime in C3502.5: • Link Loss Testing (OLTS, 1-jumper method) to confirm Optical Loss Budget compliance. • Insertion Loss (IL) not exceeding 0.5 dB per connector. • Optical Return Loss (ORL) ≥ 35 dB per core. • Bi-Directional testing for each core Results shall be recorded in raw-data and PDF formats, referenced to the tube ID and cable ID, and included in the O&M manual. |  | ZULU-BECA-001- SPC-00005- C3502.5 AS/NZS 14763.3 |  |  | — |  | — |  |  | — | —
2.13 |  | Testing of the Racks Power Distribution Units |  |  | Each Lot |  | Testing shall confirm: • Mechanical & Electrical Installation – PDU securely mounted in rack, aligned with cable management hardware, and labelled in accordance with the rack equipment schedule. • Functional Verification – confirm correct input voltage, output voltage, and phase balance (if applicable). Test each outlet socket for correct operation and power-on indication. • Load Testing – verify the total connected load does not exceed the PDU rated capacity. If PDUs have integrated circuit protection or surge suppression, confirm correct operation. • Earthing & Bonding – confirm PDU body and mounting rails are bonded to the rack earthing system (max resistance ≤ 1 Ω). • Integration with Rack Cabling – ensure PDU installation does not obstruct cable management systems or violate bend radius requirements for adjacent fibre or Cat6A patching. Maintain clearance for fibre patch panels and FOBOTS as per C3502.3(g–j). • Labelling – each outlet and PDU to be labelled in accordance with the approved IFC and as-built drawings, matching the equipment schedule and port mapping. |  | ZULU-BECA-001- SPC-00005- C3502.3 AS/NZS 3000 |  |  | — |  | — |  |  | — | —
2.14 |  | Final Labelling Verification |  |  | Each Lot |  | HOLD POINT Verify that all ICT infrastructure is labelled clearly and permanently in accordance with the approved IFC drawings and the final as- built documentation, Including: • Cable tags at both ends (heat shrink or engraved) • Enclosure and tray ID labels • Rack/patch panel port label • Floor boxes and comms cabinets Labelling must match the naming conventions and ID numbers in the approved schedules. Any mismatch, missing tags, or unclear labels shall trigger non-conformance and require rework prior to Practical Completion. |  | ZULU-BECA-001- SPC-00005-C0171- 7.16 Drawings |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | HP | Project Engineer / Site Engineer / Principals Representative
2.135 |  | Survey As Built |  |  | Prior to Covering Services |  | Survey to pick up services prior to covering |  | FH QMP |  |  | Verify |  | Survey |  |  | HP* | Project Engineer / Site Engineer /Surveyor
3 |  | Communication Service Migration
3.1 |  | Existing Comms Services Migration |  |  | Each Lot |  | The following existing services have been migrated to the new ALER3 Comms Rack: • Building 52 • ALER 2 • Terminal 2 • RVR |  | ZULU-BECA-001- SPC-00005-C2100.2 Drawings 030-3100 set APAM standards AS/NZS 3000 AS/ACIF S009:2006 |  |  | Verify |  | This ITP Signed Stowe ITC |  |  | TP | Project Engineer / Site Engineer
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP |  | Hold Point | Work shall not proceed past the HP until released by the Principal’s Representative | [5 empty] | IP | Inspection point |  |  |  | Formal Inspection to be done and recorded
| HP* |  | Fulton Hogan Hold Point | Work shall not proceed past the HP* until released by Fulton Hogan | [5 empty] | TP | Test Point |  |  |  | Product compliance test to be undertaken and recorded/reported
| WP |  | Witness Point | An inspection which must be witnessed by the Principal’s Representative | [5 empty] | SCP | Survey conformance point |  |  |  | A qualified surveyor to check product/section/structure and report
| AP |  | Approval Point | Written or verbal approval given by the Principal’s Representative
Notes