## Master List Templates
Id | Type | Name | Values | Prompting Name
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
5fa502d6-2de5-4d22-a4a4-f8ff4a60278b | checklist | ITC Concrete Prepour |  | ITC Concrete Prepour
776a58ed-70b6-4be1-bbd4-cbc5f4a3f6dd | section | Preconstruction
40db655b-6c7d-4fe3-b75f-159732bf99d3 | checkpoint | Design Drawings
8d244b29-9f7d-4411-a9de-34187af310d4 | textbox | Contract Name
8ac320a8-c8d6-40c9-acdd-1de1c6f68224 | textbox | Contract Number
2e74b533-d1db-4102-8699-f1f9cc25165d | textbox | Location
97127e2e-1edd-4d13-8fab-12db20f087fd | textbox | Lot Number
7c2c1f0c-a5cb-4abd-878f-ec590b11cb87 | textbox | Description of Pour
09dc4313-c5e3-4597-a2d4-5b5c86cf7f44 | checkpoint | Issued for Construction Drawings available
777b9b74-f06c-401a-b769-6658785e50f6 | section | Formwork
8c3defa3-d9e7-4fc2-b0be-024df6a7f825 | checkpoint | Formwork/ Moulds Braced and Secure
75006d7a-84a3-44a1-8108-68770d306c53 | checkpoint | Dimensional Check Completed
0b825dd2-c062-47b0-8cd8-e599c9eb6931 | checkpoint | Formwork/ Moulds Within Tolerances
d976042c-2322-435d-a111-5fed2d719214 | checkpoint | Formwork/ Mould Surfaces in Good Condition
4c4a97f4-f23d-4af7-8860-c0a81f1c847a | checkpoint | Chamfers in Place as Per IFC/ Shop Drawings
4f2e05dd-e745-467f-ab86-3b4eb8ec7b1c | checkpoint | Formwork/ Mould Release agent Used
55b4321e-f5c6-4292-ba8e-4e5def27fd49 | checkpoint | Construction Joints Allowed For
335f5839-5f16-4065-bf70-20cc8388fdf2 | checkpoint | Penetrations Set Out as Per IFC/ Shop Drawings
cea4ae05-5f90-4734-8129-08a012fe9fd5 | checkpoint | Cast In Hardware as Per IFC/ Shop Drawings
1357bcb5-8197-4e9b-b554-c213f661f93c | checkpoint | Surface Finish Meets Specification
e4dd1ddd-ac67-44d1-aa9f-d0077450a8c5 | section | Steel Reinforcing
0e7d42e0-53c5-4282-81d9-8dcd4f5d4dae | checkpoint | Reinforcing Braced and Secure
34357b61-0e89-4289-ade0-9cb96273efcd | checkpoint | Dimensional Checks Completed
4b0bf00e-245b-4e8b-984d-24f319af195c | checkpoint | Bar Diameters as Per IFC/ Shop Darwings
6851a67d-9248-4e96-ab3c-4415ece7d0e9 | checkpoint | No. of Bars as Per IFC/ Shop Drawings
2126edd1-61e0-47df-bb8b-570a075ecf44 | checkpoint | Bar Spacings as Per IFC/ SHop Drawings
19bf12db-3827-4b42-8570-d6822f36cd96 | checkpoint | Cover as Per IFC/ Shop Drawings
25436ef0-0ae6-40a6-a827-83446a7d5923 | checkpoint | Lap Lengths as Per Specifications
ecb81068-9da5-4b64-b2ca-a8f2b5761aa0 | checkpoint | Lifting Hardware as Per IFC/ Shop Drawings
09ab0e70-10d6-450a-86a2-df99b9f95004 | section | Concrete
021628f9-19c1-4609-a5f8-439a4db2be27 | checkpoint | Concrete as Per Approved Mix Design
1830ec36-2fe4-4715-bce6-4e045bc93196 | checkpoint | Strength Required
ebe669d8-37ae-46c0-b215-81c0c9dd3073 | checkpoint | Slump Tests Undertaken onsite
1a18503e-942e-4c12-83cd-628b32cb311e | checkpoint | Test Cylinders Taken
379aeef6-c698-47dc-ac72-ccc369862d90 | checkpoint | Surface Finish as Per Specifications
955e2a6a-06cc-423a-88bc-18f347617102 | checkpoint | Construction Joints - Surface Preparation Completes
bf410485-a4b6-4b16-be65-83cdbb07d95a | checkpoint | Additional Curing Measures Required
debd48af-83d1-4c81-bba9-bcf23ce1be56 | checkpoint | Client / Engineer Inspection Required
03083730-f70e-4397-88c9-7c133bac31e6 | section | Pre-Pour Checked and Accepted
34063abb-5bb8-4bfc-99a4-2e3cf4cad1e4 | checkpoint-no-value | Holdpoint
35a7e9ef-4956-5414-b556-625e365884f6 | date | Date of Inspection
0eb9fbfe-765c-4204-a7ec-eb86f747e517 | signoff | Sign off
b73f5f19-ff05-48fc-bbf6-f086e19524e1 | checklist | ITP - Concrete Foundations | itp | ITP - Concrete Foundations
e25eae3f-64a5-481d-857d-7ac6178c5ca3 | section | Preconstruction
c2e5a43e-0a8d-4596-86f9-ae9d38b312e7 | checkpoint-no-value | Design Drawings
f06419e7-7470-59fa-ad50-abc719b09f10 | textbox | Contract Name
c3b453e3-1736-5543-a7d5-f31039891df8 | textbox | Contract Number
6f13d90b-4745-5188-b821-04a3562ed932 | textbox | Location
210f2720-a6b4-59fb-a725-aec23205abc0 | textbox | Lot Number
c669074d-e5c6-5ce5-b100-fbb5c3a123cf | textbox | Description of Pour
6bb7256a-9198-4f81-865c-07ead461cbce | checkpoint | Issued for Construction Drawings available
aedb9e03-076d-40a9-898d-cde697f61709 | section | Construction - Formwork
a5201bcf-40cb-4ff2-8003-c85d2bcb99ba | checkpoint | Formwork/ Moulds Braced and Secure
1d472fe3-e333-4c17-a945-be675661717d | checkpoint | Dimensional Check Completed
f5d3f214-8161-4cf5-9d9a-a3cf0a48289d | checkpoint | Formwork/ Moulds Within Tolerances
ceb5f838-f92f-4653-a0c3-a3cd00f342cf | checkpoint | Formwork/ Mould Surfaces in Good Condition
6b67d2cd-42fd-4b04-89da-501205882c1e | checkpoint | Chamfers in Place as Per IFC/ Shop Drawings
57eac1e3-d210-4691-b9fe-ce12f6e6c8de | checkpoint | Formwork/ Mould Release agent Used
a7127d0e-aabc-42fe-a9c1-711f6124a853 | checkpoint | Construction Joints Allowed For
377d2d90-1039-42c1-9cb1-2f9b787e1c71 | checkpoint | Penetrations Set Out as Per IFC/ Shop Drawings
1cb19f9e-a7d6-4c78-9eaf-b25ecdbe59fd | checkpoint | Cast In Hardware as Per IFC/ Shop Drawings
e9a6e56a-8671-4bb6-91fa-dd876e03dc0e | checkpoint | Surface Finish Meets Specification
f1b29556-745b-462b-b201-7006bf0b2a86 | section | Construction - Steel Reinforcing
3bd30614-ed94-4f09-9ead-f78bd8e96def | checkpoint | Reinforcing Braced and Secure
cdc863d1-f6f6-468a-b104-b2f18e379b92 | checkpoint | Dimensional Checks Completed
9cc87a4b-7ade-4a62-babf-757b618a2c3c | checkpoint | Bar Diameters as Per IFC/ Shop Darwings
9e5e6383-52ba-47f7-b254-6e52ec44377a | checkpoint | No. of Bars as Per IFC/ Shop Drawings
c8c68d62-ac51-4ed0-aa56-256edcb522bf | checkpoint | Bar Spacings as Per IFC/ SHop Drawings
16c6a15a-7ab9-40f4-a792-64a882f32f8f | checkpoint | Cover as Per IFC/ Shop Drawings
e3bfd2d2-d0bb-4aef-aad1-5d926f27f447 | checkpoint | Lap Lengths as Per Specifications
54c40871-e592-40bb-9a8d-82e5d8f051a1 | checkpoint | Lifting Hardware as Per IFC/ Shop Drawings
479870f5-8a72-4271-9ad7-096770da9394 | section | Construction - Concrete
6062f58d-e938-48cd-a553-fa853702c61b | checkpoint | Concrete as Per Approved Mix Design
0f7b7e01-db03-42b7-98f5-5b8dbe26869b | checkpoint | Strength Required
168c2967-4bdf-5ffd-95f8-104c68f7d31a | textbox | Strength:
300acdc4-530a-4d07-a456-aa4f65e2d47c | checkpoint | Slump Tests Undertaken onsite
85cd9480-55a6-42c0-ac1c-a921d9e1f9e1 | checkpoint | Test Cylinders Taken
724812ab-ae91-4740-a149-e3cfbaa18c69 | checkpoint | Surface Finish as Per Specifications
c18d7e3c-39fa-408d-9097-be38c824f092 | checkpoint | Construction Joints - Surface Preparation Completes
51e62a8a-b0b7-4ae5-a916-7eadaac15b77 | checkpoint | Additional Curing Measures Required
9b5f8cfc-c126-438c-a4d7-b946b1eac60f | checkpoint | Client / Engineer Inspection Required
5fd5d36a-aae8-40ba-8118-8d53e5857c0a | section | Construction - Pre-Pour Checked and Accepted
f88428c1-bf2f-462b-8574-fac77ec3f0a6 | checkpoint | Pre-Pour Checked and Accepted
19b46217-ee54-5977-8723-a72c43f36e84 | date | Date of Inspection
dc1481b0-2b75-4f84-9b3e-8306af22516d | signoff | HOLD POINT
fe1bd0d3-9527-4a5d-903e-c0b192398112 | checklist | ITP - Drainage | itp | ITP - Drainage
c26f1bd0-1930-4796-84bf-1e5b80063381 | section | Location
c82a7f58-4b81-4455-bfe2-d73266a2bf67 | checkpoint-no-value | Drainage Location
fea24dea-1f52-51c6-b7ec-c42a6302b2d7 | textbox | Location of Installed drainage line
e0d1f0bc-5944-5d71-af4e-ca62fa030591 | textbox | Project drainage line reference (if applicable)
300f4514-48ec-4f56-8aa8-ca5a9638616a | section | Preconstruction
8409e24a-8897-4e4c-aa23-5d9fee7357c4 | checkpoint | Design Drawings
02dcefa5-5ce8-59c9-9bcc-92d5b476a2e7 | note | Issued for Construction Drawings available
11f9f648-c18a-4b7a-bbc8-04666e575329 | signoff | United Civil Hold Point
cc299b21-a832-4ca8-81a9-533785981f31 | checkpoint | Site Preparation
4a09b00f-3974-5740-9868-799c03ce7ba4 | note | Visual inspection of cleared and levelled area
bbb985f2-a089-5731-8dd8-76a07c5869e9 | note | Site free from debris, vegetation, and unevenness
1e081ace-a08f-4510-878a-98f7b95f4087 | checkpoint | Survey and Marking
87eccc8d-1ee4-5fc4-8f3d-f0803116521c | note | Verification of layout and drain alignment & grades
75f44d1e-8235-52f1-8d1a-a6481e7720d9 | note | Alignment with approved IFC drawings
9fb60223-f9e8-45e2-8434-e898d42a50dc | checkpoint | Material Approval
bb6ea80c-6f46-543a-8cb2-b114aed74139 | note | Review and approval of pipes, culverts, and other materials
10d975f8-03a5-586c-bd0f-065da03077d9 | note | Compliance with IFC drawings, specifications, KDC EES - S06 for accessways, and standards
66b310d0-d4e5-5632-a455-aba610ae7e66 | note | Material Test Certificates / Delivery Dockets attached
0329a0c5-e51e-4272-8d16-980e7e1d7b6a | signoff | United Civil Hold Point
0cf24214-8126-4e31-bb6c-1625d561fee8 | section | Construction - Excavation
011178e6-14bd-459e-ac8a-c13d6a61f614 | checkpoint | Excavation
e8e5837e-1dcc-5783-98f3-0bb95be2f4da | note | Visual inspection and measurement
cab8a44e-73da-54b6-b719-6c6d236aa5a2 | note | Depth, dimensions, and cleanliness
47ac976f-43a5-5a31-bc69-a0b6aaac5a6a | note | Compliance with design drawings
06ce6ecb-4394-4cf7-8237-f6aa97de3ddc | checkpoint | Soil Stability
23d24620-9022-52f9-b963-23eeba51577a | note | Inspection of trench stability and shoring where necessary
a2f11b00-f1e3-51dc-815f-97f66dc37a97 | note | Stable and safe for pipe laying
2745c1dc-453e-405f-bdf4-feebee584f94 | section | Construction - Installation
c74fff2e-c134-4395-a9a3-37bd53d298c2 | checkpoint | Pipe Placement
433d4825-90dc-50b0-b4b7-fb0383962858 | note | Visual Inspection of pipe placement, alignment, and bedding
b315b5eb-2fdd-54ee-8db9-a99e13c2c297 | note | Compliance with approved IFC Drawings
ed25c9a1-2d62-4138-a50a-69c86da02522 | checkpoint | Joint Sealing
5c13a856-599d-5798-be1e-87fb2d0af99d | note | Inspection of joint sealing materials and application
e49f1c3f-dd95-5241-ae99-1a78d5a98eae | note | No leakage; proper sealing per specifications
be00973d-b7f1-46ed-933b-4d12e0b9f835 | checkpoint | Backfilling
82b95dd9-2b37-51bb-9d5e-1d5700d7a526 | note | Inspection of backfill material and compaction
589aea76-2d64-54aa-b2bf-cfa53fdbdbb9 | note | Proper compaction as per specification
301a1a98-2a3f-5d71-8e94-7a7acf6d0e10 | note | ITC for compaction
749f476e-b31a-4f3d-9394-6cd230c6a199 | signoff | United Civil Hold Point
a8c9bd8d-517c-4403-b682-9333cdfc110c | section | Construction - Testing
c9c69a5c-311f-4981-ab92-6a412772d647 | checkpoint | Hydrostatic Test
b06f66d4-c14a-5d31-bc1c-5c530dc761fc | note | Pressure testing of pipes for leakage
1d5dd7dd-089f-58b5-aa1c-f3f498dc1f94 | note | Meets pressure standards for type of line being tested
ab7a5ae2-a11a-58f8-8554-bc96792696db | note | Test Report Completed
09f77e55-c152-4460-aeae-73579dedf99a | signoff | CHINT / United Civil Hold Point
87252f93-946d-42ad-b803-e167aeb988cc | checkpoint | Flow Test
374fc425-31e2-56d7-9ee4-8d2172182eca | note | Visual Inspection to verify water flow through drains
bc7953f1-a6a3-506f-aa32-e790ac9a7e28 | note | Smooth flow; no blockages
764f79cd-0f50-42b2-8d5b-e9622bbb713f | section | Post Construction and Handover
fdbeda9b-2428-4a57-9876-f59ed126781d | checkpoint | Final Walkthrough & Inspection
e62b0d29-3126-5256-b44e-c63efeb67fb3 | note | Comprehensive Visual Inspection of Stormwater and that it is ready for use
6e982035-3e05-50ea-9d30-f258afb646b3 | note | Comply with IFC Drawings / Specifications / KDC EES
bf157520-4f75-5dca-9ff0-32d517d98d10 | note | No misalignment, defects, or debris
0141d802-0986-4be2-8a53-90c1341733b0 | signoff | CHINT / United Civil Hold Point
a42f8a2d-7862-4ee4-84c4-a768e23b4492 | checkpoint | Non-Conformance-Reports
669bdfeb-11e0-5cb7-96ab-87a4aeaa90b4 | note | Each Non-Conformance Reported, Rectified & Closed Out
59242f9b-14f4-45e4-aa7b-eb970429b410 | checkpoint | Punch List
75c8c67b-2148-55ff-a823-77a3a691fbe0 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
7070abe9-5ad5-4b29-87f9-cc8a7a58a1df | checkpoint | Documentation
4e597be3-a8b7-5e30-8f97-afaa43d7f0da | note | On completion of the Mechanical works for this Block
e5419cd3-3e95-544d-af73-0b2339d110e4 | note | Submission of all test results, ITC's and any as-built drawings
5c481f09-c457-5a33-8103-1e625e474e0e | note | Complete and approved by client
9f70a944-0cd1-44cf-a3e4-20e189c758cc | signoff | CHINT / United Civil Hold Point
fe0d2eaa-c289-4e50-81d5-b33ba171e031 | checklist | ITP - Electrical Cable Trenching & Installation | itp | ITP - Electrical Cable Trenching & Installation
f916d41e-935b-436d-8f2c-7e64ee653636 | section | Preconstruction
f8242ff6-87a3-4144-81bf-beb9ea77859d | checkpoint | Design Drawings
a72086ad-2182-5e0f-959d-b022148cf1d9 | note | Issued for Construction Drawings available
18314cb6-ff5f-4a42-b435-eec26d29db6b | checkpoint | Site Preparation
605d34f6-40ed-54fe-ae26-0999895d6070 | note | Visual inspection of cleared and levelled area
bb5b6de4-fb06-5c5c-a422-b9bb53f73e7e | note | Site free from debris, vegetation, and unevenness
8fe70f6c-0626-4f8b-b30a-643b45039cf6 | checkpoint | Survey and Marking
bcc2ede4-a229-5511-b545-db453b018282 | note | Alignment with approved IFC drawings & Digital Designs
55e91040-cdea-4f3f-b052-15e7889bc970 | checkpoint | Material Approval
6c407164-eb24-5b4c-83d3-ff559269ab4c | note | Bedding and backfill sand complies with the specification notes for thermal resistivity
1e6b4431-7488-448f-891d-9aeb4c7f524d | section | Finger Trenching - Trench Excavation
4c440875-26cc-4f2f-8419-3aa2cf632c60 | checkpoint | Trench Excavation
679363d8-5a4f-5c08-8a29-d4b9cf3ab05d | note | Finger trenches excavated to a minimum of 900 deep x 250mm wide
fe96aeea-30f6-570e-a556-a7be210b1633 | note | Finger trench invert is smooth without stones or rocks protruding
0db45145-2deb-47e6-bc46-d67eea15a31a | section | Finger Trenching - Trench Bedding
53d51188-125d-4f52-a6ff-e1d7e2ed3b9a | checkpoint | Finger trench bedding consists of a minimum of 100mm of sand
0ec6fc78-fa3c-4bdd-bec0-9e486cbef4f3 | section | Finger Trenching - Cable Installation
fc521dff-d97c-45ec-8149-7592773330a3 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
321ac694-1512-4546-837f-1080def44c63 | section | Finger Trenching - Trench Backfill
53b66f48-c97d-45ee-b094-49a53d1facde | checkpoint | Finger trenches shall include 75mm of sand over the cables
ddf813bd-fed9-45a9-9458-c276219af3f9 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
74e7838a-74f9-480c-9070-5494227e842a | checkpoint | 75mm of sand has been placed over the hard protective cover
207a1567-e053-4479-b6b0-d5c0e1bf8d69 | checkpoint | Earth cables have been installed on the final layer of sand
ee279c8e-f3b7-4b2c-9731-8141f77ae7bc | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
33b0cf62-597b-40f7-ad07-b62823c9fea1 | checkpoint | Existing excavated material is replaced and lightly compacted
cb50af2f-beac-416d-b01a-e49263751f66 | section | Finger Trenching - Reinstatement
ba1219aa-46fa-4e7b-94d8-6f79c32001a5 | checkpoint | Finger trenches are reinstated back to tie into existing ground levels and contours
fb3f40ec-fda8-4151-a8f8-ae10c5b2bc52 | section | Combined Services/DC Trenches - Trench Excavation
0fdc9fa6-9680-4f7c-b390-eb8b756f26dc | checkpoint | Combined Services trenches are excavated to a minimum of 900 deep and wide enough to accommodate all of the cables required including minimum separation distances
096eb1a4-0401-4fd3-8e21-501128334fe6 | checkpoint | Trench inverts are smooth without stones or rocks protruding
78803658-2920-4797-9ada-d5c352c97086 | section | Combined Services/DC Trenches - Trench Bedding
d94f93df-327d-4ab3-a949-60e0a95870f8 | checkpoint | Combined Services trenches bedding consists of a minimum of 100mm of sand
04a2b694-7465-4325-bd85-536f28e6d1fe | section | Combined Services/DC Trenches - Cable Installation
0bfeb3a6-196b-4dd4-b251-f95f50a2ad39 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
8c3cc5d6-a65e-4208-8584-13f16f9fb337 | checkpoint | Minimum separation distances are observed
1439c217-a033-4163-b1db-5019c1d28cfd | section | Combined Services/DC Trenches - Trench Backfill
f63cff05-0e73-4a37-836b-e0b89c4e390b | checkpoint | Combined Services trenches shall include 75mm of sand over the cables
da4c43ab-4a99-4bb0-8362-aee68977ca63 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
0bc1cead-6f4f-5033-aa79-5de95f2e1732 | note | 75mm of sand has been placed over the hard protective cover
3fae18d0-2989-5424-a44e-250643ef00fa | note | Earth cables and comms ducts have been installed on the final layer of sand
be4294af-16bc-5a46-8b61-e52d1b0e283e | note | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
c944b01a-6c23-5cbe-a024-e9ba481114b2 | note | Existing excavated material is replaced and lightly compacted
4a16169f-01e9-4eca-8fdb-5e201cb89a02 | section | Combined Services/DC Trenches - Reinstatement
2cb773af-1efc-401f-b7ef-0b68fb2cefa1 | checkpoint | Combined Services trenches are reinstated back to tie into existing ground levels and contours
234bfa1d-2314-49ce-9b05-cd29b13c6936 | section | Comms & LV Trenches - Trench Excavation
51edcf40-f521-49d6-a022-abf702d097f2 | checkpoint | Comms/LV trenches are excavated to a minimum of 800 deep and 250mm wide
13af962c-672a-48e9-90a4-00fb7375f365 | checkpoint | Trench inverts are smooth without stones or rocks protruding
b3da0b78-8f27-454f-9670-20f7f74af30a | section | Comms & LV Trenches - Trench Bedding
22cef000-4647-4ef7-8dce-dee64332b80e | checkpoint | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed
c22ee600-855c-4713-8eba-5e16a1461cef | section | Comms & LV Trenches - Cable Installation
632a1b2d-27f7-45a4-bce2-e2a7e6569d86 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
e497b53c-5575-4f24-89f6-19719bc4ec95 | checkpoint | Minimum separation distances are observed
13375d84-bd55-55c2-87e7-19d0edc546a5 | note | Cables have been installed in conduit
92ca59d2-c40e-4462-9b21-e163a32a930f | section | Comms & LV Trenches - Pull Pit Installation
1792fb15-fc90-4aa8-a4fa-d86b201df75e | checkpoint | Pulling Pits are installed on a 100mm of Gap20 bedding
5c5e60c6-29de-47f6-8c6c-2494e90d468b | checkpoint | Pulling pits are installed on the line of the conduits
51d703b3-27c5-4e01-a54d-bdfc9a17d822 | checkpoint | The tops of the pulling pits and level and clear of the road lane
690385f2-3bb6-4050-b0f3-1c4523526177 | section | Comms & LV Trenches - Trench Backfill
52079e5b-7f01-4065-b323-b0c91ef719a8 | checkpoint | Comms/LV trenches shall be completely backfilled with excavated trench material
f3b4ff6d-6b41-4822-a2c1-b4d517e3ff90 | checkpoint | Hard protection shall be installed over 75mm of backfill above the conduits
ec219b66-a8ff-4a13-a3a4-0400a8662b0c | checkpoint | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface
73220fd3-35c8-4d6b-b369-f7b72ced93a3 | section | Comms & LV Trenches - Reinstatement
8e83f3b0-6b71-4874-93a6-3d1a0d01d55b | checkpoint | Comms/LV trenches are reinstated back to tie into existing ground levels and contours
d865720c-bd47-42be-8fcc-96a05d6721a2 | section | 33kV AC Trenches - Trench Excavation
9f7ad33c-6039-49b4-b48a-f4a977677b61 | checkpoint | AC trenches are excavated to a minimum of 1200 deep and wide enough to accommodate the three cables laid in a trefoil arrangement
b74fe42c-b536-4fa4-8505-61f9f2c575af | checkpoint | Trench inverts are smooth without stones or rocks protruding
fd0e2850-9442-41a5-a009-cf0328eb5599 | section | 33kV AC Trenches - Trench Bedding
bb1e6682-6cc9-4cb1-ae1d-53f671a2a62d | checkpoint | AC trenches bedding consists of a minimum of 100mm of sand
bd326020-2350-4261-94d7-575ec94bb964 | section | 33kV AC Trenches - Cable Installation
acc8459a-c598-444e-bbda-894883092a9b | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
45a0368c-c655-4b20-93ed-4dff726b8c86 | checkpoint | Minimum separation distances are observed of 1200mm to any other cable
1b4550a8-92b9-44e3-a7a0-e7c0a6be7825 | checkpoint | Cables to be installed with minimum of 1200mm cover
111ac375-4c17-4be6-ae8c-8e35dfb45a87 | section | 33kV AC Trenches - Trench Backfill
db5572c9-9b47-4230-9488-6b05d008b7e3 | checkpoint | AC trenches shall include 75mm of sand over the cables
2040fc37-1d8c-437d-8a61-15cb42e151c7 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
f0ad483c-7c55-40e2-bd8d-6c8d104f58b7 | checkpoint | 75mm of sand has been placed over the hard protective cover
f4afef49-1797-4ca0-b819-bab46c52ed91 | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
54ed10c1-47e0-4dde-9ce2-be3e5f231b0b | checkpoint | Existing excavated material is replaced and lightly compacted
03aa8aab-46ae-414d-978e-7d04e82c82de | section | 33kV AC Trenches - Reinstatement
cbe9b74b-34be-43e7-8e97-0aa136e44514 | checkpoint | AC trenches are reinstated back to tie into existing ground levels and contours
b06132aa-1bfb-48ba-bda2-95c580726294 | section | Road Crossings - Trench Excavation
c07d8057-cf30-40f1-90d1-704473ba765d | checkpoint | Road crossing trenches are excavated to minimum widths and depths as described in the cross sections of the Electrical Drawings
5a08d1f7-3978-5d37-9502-53a4a71c2f5b | note | Minimum cover shall be:
07ebdd21-a626-5a70-9048-5de6087c91f3 | note | AC Cables - 1200mm
a782c5e8-ff8e-53af-8f12-9490ccb119d6 | note | DC Cables - 800mm
74678479-2c76-5e43-b98e-9ce95ec40366 | note | Auxiliary/comms/lighting - 600mm
cec7ee00-6f71-4d46-aa75-bb95db944651 | checkpoint | Trench inverts are smooth without stones or rocks protruding
577e782c-116d-43c8-8593-418ce416d34c | section | Road Crossings - Trench Bedding
49be1cb6-0832-4ec7-a3d1-5abe4beafb60 | checkpoint | Trench bedding consists of a minimum of 100mm of sand
e0359bab-fa7e-474f-88b1-0660d6d6461d | section | Road Crossings - Cable Installation
c29388bc-b01c-45d3-9874-f1ebe80bdb0f | checkpoint | Cables installed in accordance with the IFC Drawings and specifications in 100mm HD Conduits - AC cables to be in 150mm conduits
b9ae2163-a838-42f7-90c7-3cec98ff0172 | checkpoint | Minimum separation distances are observed:
b086d1fd-d02d-5158-9da9-5c1774908132 | note | 33kV - 1200mm
0c1cd4d9-e194-5209-9c84-56c5bdd9d57e | note | DC Cables - 300mm
18f15eb1-fd80-59e8-84f7-5e1664f7bb5b | note | more than 24 DC Cables a gap of 150mm in the middle
aa70f7bf-a7ac-54fc-8b36-1c05b0aa49d2 | note | Earth cables - 150mm
23170a8c-fa85-4ab8-a728-80a0c471faf1 | section | Road Crossings - Trench Backfill
1091e89f-6c06-4688-beb3-55dd45729d29 | checkpoint | Road Crossings trenches shall include 150mm of sand over the conduit
fd1ca2a3-0000-4d4a-9f82-28dad9e7601a | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
1fbcdcdb-6323-4098-adb4-c1dc19f7d61a | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
5664e8a8-0999-4b95-abe3-fb1d53039273 | checkpoint | Backfilled material shall excavated trench material backfilled and compacted to 95% native soil density
64e9289f-eb23-47e0-9374-19c63b802c99 | checkpoint | Existing excavated material is replaced and lightly compacted
076dc458-2126-470e-8515-f67dfb809254 | section | Road Crossings - Reinstatement
224cfd76-b775-4c40-8508-b2dbd0c8f5ac | checkpoint | AC trenches are reinstated back to tie into existing ground levels and contours
116a6bc3-958d-4e6a-ab50-997dd14d3e02 | section | Incoming LV Trench - Trench Excavation
6bef3b69-4ac0-4a74-8ce6-0d03e3844055 | checkpoint | Incomming LV trenches are a minimum of 800 deep cover if Direction Drilled
39bf0718-ec43-4628-89f6-676a87fd8607 | section | Incoming LV Trench - Trench Bedding
b9e9d86a-b468-43bd-bd9d-18867698bed9 | checkpoint | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed
e87e9479-a5c0-43f9-a1a6-791b478dcdec | section | Incoming LV Trench - Pull Pit Installation
f0f93b8d-eaf7-4fa5-a173-4f84b6bd110c | checkpoint | Pulling Pits are installed on Gap20 and Bidim
4b5061d2-0d57-43e7-9061-385a15b24d7b | checkpoint | Pulling pits are installed using 1050x900 Concrete Manhole Risers with Concrete and CI Lids
006ce0bb-b88a-4c9b-ba3e-cde47a565e3f | checkpoint | The tops of the pulling pits and level and Protrude a minimum of 300mm above the surrounding ground
fdf80a42-2fed-457f-9121-be0a0f6a2a00 | section | Incoming LV Trench - Trench Backfill
2e4142df-e3ca-4619-aa59-068c58e10278 | checkpoint | Comms/LV trenches shall be completely backfilled with excavated trench material
2b42f2d5-2334-4fff-80e1-1f29d3bd9333 | checkpoint | Hard protection shall be installed over 75mm of backfill above the conduits
3f871fbf-9eed-462f-a4d6-6598e01b15bf | checkpoint | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface
62a20fae-9d90-4d22-86b6-74649dc4fda7 | section | Incoming LV Trench - Reinstatement
dd2497f5-647f-4c4b-90a4-4a9676287eb0 | checkpoint | Comms/LV trenches are reinstated back to tie into existing ground levels and contours
8170426c-8430-47c5-82f2-deadeb05810e | section | Post Construction and Handover - Asbuilt Information
81fd7a9e-7868-4fbd-a460-59791e590f28 | checkpoint | Asbuilt information of trench layouts and locations are supplied
3897a9a6-a063-4ddc-a2b2-aab050a6cb9f | section | Post Construction and Handover - Final Walkthrough & Inspection
72761f1c-b6ac-4065-975b-d66d5ac38b66 | checkpoint | Final Walkthrough & Inspection
5bbe1f3b-3421-5cf1-971d-e82784b5370d | note | Comprehensive inspection of all elements relating to the Electrical Trenches
28afd4b1-d283-5940-9192-19da7a9c229e | note | Compliance with IFC drawings and specifications
fdb71828-fc43-5bf6-8aa3-ba10557ce9cb | note | Verify all Drainage meets design and functional requirements
6e9fa474-68e7-4ff1-8c06-cd343398e3c2 | signoff | United Civil & CHINT Hold Point
d0a35101-1a75-495d-990f-c8aed4abea90 | section | Post Construction and Handover - Non-Conformance-Reports
d809cd6b-1aa2-4308-8bcb-21dac26226ae | checkpoint | Each Non-Conformance Reported, Rectified & Closed Out
f90e2ca3-a10b-4fd9-902e-5297b67ec1da | section | Post Construction and Handover - Punch List
c9f2813c-b739-4f39-bf7d-c492f31d9432 | checkpoint | Development of Punchlist with Client and Contractor Representative
0de1d6c9-d086-5e13-acdc-17eaf781d619 | note | Punch List closed out in a timely mannor
11a63b49-57be-4463-9d2a-f8d37c52515c | section | Post Construction and Handover - Documentation
96c51761-fdbe-417f-aec7-0fbf96e74a7e | checkpoint | Documentation
55967e0b-a625-5db1-90d8-fd975f8f77ec | note | On completion of the RMU Drainage
d2958864-784d-553d-aceb-042e0af2730f | note | Submission of all test results, ITC's and any as-built drawings
0ce25684-2956-569c-b7cf-9f948ae4133e | note | Complete and approved by client
2ab9614e-e4f5-4c7f-8e7c-3c1de7244518 | signoff | United Civil & CHINT
a1ffbecd-5483-4987-99f0-6db17b15bad9 | checklist | ITP - Internal Roads | itp | ITP - Internal Roads
abfc9555-4821-46f3-ac16-fb4d67f207db | section | Preconstruction
0776b846-c07f-4692-8b70-f16cd3d05627 | checkpoint | Design Drawings
2238628c-8cf2-553b-8f45-6e39f3de361b | note | Issued for Construction Drawings available
024abe8f-8342-4b72-8e84-430043e54510 | signoff | United Civil Hold Point
b6f13de5-cc0d-41d3-aa72-db20489a34f3 | checkpoint | Survey & Setout
0abc92ba-0810-5b3c-bd79-b1af67e034be | note | Verification of road alignment and layout
0fc00044-d1e4-52db-9586-91002bbf7b40 | note | Alignment with approved IFC Drawings
3912272a-594e-42e2-a15d-472e475aef35 | signoff | United Civil Hold Point
d2a617b8-c410-496a-b3f5-5a123b8ee170 | checkpoint | Site Clearing
2120c002-71b1-5a2e-b5c8-bf1d0669b819 | note | Visual inspection of cleared area
4a4b9df3-632c-5459-8f50-d92e79245ca0 | note | Free from vegetation, debris, and obstructions
b540acb9-1e62-47b8-beb7-b9934a8a7c87 | signoff | United Civil Hold Point
93276520-d40f-4b5e-900b-047ed05bd7d5 | section | Material Procurement
148d3182-847c-49c9-af39-5b54c73f578a | checkpoint | Material Approval
174e789f-e894-50f9-b290-fa881ae31d89 | note | Approval of road materials (e.g., aggregates, subbase, basecourses
754edef6-3360-518e-a601-829daff5ab40 | note | Compliance with KDC EES2011 specifications and standards and IFC Drawings
dcc2d280-7437-5097-85d5-43de06aad03f | note | Material Test Certificates - Gradings, CBR, Crushing Resistance
1dd95988-b5e0-4856-9ee8-f0abec7e4981 | signoff | CHINT / United Civil Hold Point
d1b99d41-c515-4673-8fd3-d7da726eb858 | section | Construction - Subgrade
93da8519-de31-477f-818c-907e840b6283 | checkpoint | Excavation/Grading
2f3c9e05-13cb-56ba-a524-999fdbc5cdbe | note | Inspect grading and levelling of subgrade
8cab52cd-6fde-5c1f-8784-88c7edddd5bc | note | Uniform surface with proper slope and drainage
5fcd1af1-9655-5871-b1df-d2332df22a8a | note | Visual Inspection and Measurements
b1e1f99a-073b-5eec-bdcd-f4af0d9363d2 | note | Every Internal Road
d5d9d7fe-78a1-4b0d-95ae-02dc593220f6 | signoff | United Civil Hold Point
e1341a0f-b5da-443f-9f16-debff9d10358 | checkpoint | Compaction
2c2f04cf-a4e3-5fa5-9e29-9af067e33e6c | note | Field density test
89e9803b-fd74-5e9c-b119-29ecc9f382c5 | note | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m
2c91c0d5-234c-5e0b-a6df-b83d96632778 | note | Scalar Penetrometer test check sheet
e1fec911-3f38-5bff-aec3-04160b8cf706 | note | For each section
d9afe38a-faa1-522f-aebd-a09367f6da71 | note | Hold Point for United Civil
c480b89c-e1d4-4b79-b339-77488bda7137 | signoff | United Civil Hold Point
7022365b-5974-4e77-88c5-3c1d400dc41f | section | Subgrade Improvements (Where Required)
58a0000b-dade-4f74-833f-e0c5ec1924f4 | checkpoint | Identify areas of Undercut
7593c718-dd98-5a1a-a276-a3146917fa88 | note | Identify areas of undercut and liaise with Client
17e8d11a-32e8-432b-b7c7-8bc6a6393ab9 | checkpoint | Excavate Undercut
5da30a04-3c77-5c98-ad2f-850fbf889e9b | note | Excavate a minimum of 200mm in depth full width of the road
a29cac63-962d-54cc-80f9-7bf930e9e6b5 | note | Any free water has a path off the road in a controlled manor
ceff2c65-988b-5770-b00c-72fbc463e9fe | note | Visual inspection of subgrade with Client
30fa97c4-319b-5862-b19a-7d48a499ffc4 | note | Undercut ITC completed
d3fd2b39-37c7-415c-85ef-2455f0e37a43 | checkpoint | Geotextile & Geogrid Installation
fc1e9c11-bf82-58a7-bf6c-b491d97be119 | note | Visual inspection of geotextile & Geogrids placement for each section
461ff8e7-c8f4-5412-a3cc-23d1b9b2341c | note | Correctly installed with proper overlap and anchorage
504d9c88-0c24-5919-9021-15890f3c9ccd | note | Product Data Sheets
ed8a9e06-170c-44ce-b71e-127831c545ad | checkpoint | Backfill Undercut
99ffefd8-bad9-558e-98c6-aad3062fbb63 | note | Visual inspection of backfilled material
f8620507-29bb-5ff3-b153-1363d322d11c | note | Compaction to be static compaction only
105f7cab-d663-53ff-b1d5-e5b14bd05c93 | note | Proof rolled with no obvious weaving or areas of instability
143968f7-775b-4f67-81dc-faba663e2893 | section | Construction - Base and Subbase
dd216a86-f22b-4873-91e8-0007d8676041 | checkpoint | Material Placement
defef8f3-d1cd-5959-9d49-4cb4f805a40c | note | Inspection of base and subbase layers
ae9c0bb9-9b60-5f6d-a0d2-1851520452f4 | note | Compliance with IFC Drawings and Product Data Sheets with Material Specifications
12468dcb-6ccb-5dad-8650-949821e220b2 | note | 100mm thickness of Gap40 and 50mm of Gap20
27e0e1f1-14ba-5389-8729-a28c2499d8b0 | note | ITC Completed for Internal Roads
9c5e0da1-1e55-47f8-bcab-ad7b4673c31b | checkpoint | Compaction
e9b41fe9-d11f-5de7-ad9a-228784fdea1b | note | Proof Roll
4aa5701e-2ef5-538f-bf83-00a9982ba838 | note | Visual Inspection of Compacted Base and Basecourse
89e5753b-e427-5fe5-b297-eb39f2fc3c5a | note | Each Road
4c4053ba-88b6-40c7-ab7e-961284b4a235 | signoff | United Civil Hold Point
b4e6ae2b-0065-4bd3-acf5-eb276050e093 | checkpoint | Level and Alignment
bde5091f-fcfc-5f23-b916-fdcd976764d6 | note | Visual Inspection of Alignment
3f0b7cb7-15e3-5795-8473-aed4d11c9aa6 | note | Compliance with design tolerances
2175eb03-8a36-51d9-bf42-4c0d301694c3 | note | Each Road
aeea9e42-b247-42d7-baa9-c3e3475f6bb2 | signoff | United Civil Hold Point
58fccf82-627c-45b0-aa15-c2690c41ed47 | section | Construction - Surface Layer
25c6ddd6-5172-431c-b00d-ca9015e06a70 | checkpoint | Aggregate Placement
6aec105c-9013-586a-ae86-53028e2ac8e6 | note | Inspect placement of aggregate layer
9e1d4dc4-3dec-50f2-b43f-b8eb7118b65a | note | Even distribution; meets design thickness of 50mm
2ee4b183-43cc-5975-bce3-2cb17514c7b2 | note | Every section
453c6bfa-3d4a-49e1-ad76-4b7ebef1e357 | checkpoint | Surface Compaction
aabb312f-dd1c-591e-a2df-f748d65e6316 | note | Proof Roll
fa242066-de5d-56ba-abbc-7aa606054710 | note | Visual Inspection of compacted surface layer
8ef3ac72-a5df-546f-8df0-e718366c816d | note | Each Road
6c13be30-0508-4e03-b92a-aedcbc49a11f | signoff | United Civil Hold Point
55071e8d-3eb9-4f5c-85fe-3ea0545b91b1 | checkpoint | Final Grading
d2248020-475b-5aff-b0d9-b1af034f62e3 | note | Visual Inspection of final grading and surface finish
c19a0554-41ab-547c-ad33-5f12a8adf3d2 | note | Smooth surface with proper slope for drainage
40f6ca79-b919-5ab8-ba77-e827c188c201 | note | Each Road
544f8d91-4a45-40a3-83f7-30fbdbc573a4 | signoff | United Civil Hold Point
fb4f2991-ead6-40d5-a4cf-6a62a0347e55 | section | Drainage
2b48e84d-2509-47ce-a6eb-8d4a4c0d0019 | checkpoint | Culverts and Drains
13c200ef-d50e-5d23-b7f2-5b74d0f90ae0 | note | Visual Inspection of installation of culverts and drainage channels
8a3cdedb-d4e9-505d-b989-81fea6cbe335 | note | Installed as per design; no blockages
9e6bad61-e694-5515-a19b-b90c1880900d | note | Water will flow without deviation
39003a07-0f48-59cf-b798-69d19b2fc210 | note | Reference Drainage ITP for Culverts
515aef71-d44d-4dc3-a3a3-e8ed81446ede | section | Post Construction and Handover
6368d12d-fff5-4de2-94f1-ebd0ee0e961d | checkpoint | Final Walkthrough & Inspection
1eac03a4-2c45-58b8-bebf-b8f8771718f4 | note | Comprehensive Visual Inspection of road construction & ensure roads are ready for use
a46d8159-1f74-58ec-8d2c-b4239fa4daba | note | Compliance with IFC drawings and specifications
e30b8f41-0fa2-58f9-a208-18c45d7c2926 | note | No defects
158441f5-cd44-43c2-b568-59ecb9eb47fc | signoff | CHINT / United Civil Hold Point
1023f131-e9f2-4af8-abe6-f66cdb935a47 | checkpoint | Non-Conformance-Reports
80496d78-6851-5494-a291-9914e58b22e0 | note | Each Non-Conformance Reported, Rectified & Closed Out
ba9533d3-86c7-449b-bb47-7f2b0b8fbcb2 | checkpoint | Punch List
7a342d89-983b-5472-9864-b00b2eda6010 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
fbff592b-230b-4e3c-be0b-c63cf7c252f9 | checkpoint | Documentation
7814b046-9a6a-522a-b694-5d8cda674e12 | note | On completion of the Internal Roads
c4b2fca8-684a-56be-bd39-c8b32170045f | note | Submission of all test results, ITC's and any as-built drawings
be5347e4-6e83-55db-8284-2567c995f49d | note | Drone Survey as-built for alignment and levels
3ce083c9-b2b9-483c-8c99-e8bf7b2617b4 | signoff | CHINT / United Civil Hold Point
d84173c5-21b0-4319-850a-3de723280854 | checklist | ITP - Inverter Foundations | itp | ITP - Inverter Foundations
cd3f2687-c440-402d-be29-9cb94f7ea436 | section | Preconstruction
d0e35911-877c-4c23-bc81-e4ab0c116a73 | checkpoint | Design Drawings
752fe0ba-6758-5ad7-879c-f090b86a0cfc | note | Issued for Construction Drawings available
26fe4fb9-3493-4b8e-8321-7a031dc55586 | signoff | United Civil Hold Point
134881fe-2994-40ff-9b44-70ae5f7c1ff1 | checkpoint | Survey & Setout
48934026-fd6e-5d93-9b4f-1fb54cb50923 | note | Visual Inspection of Inverter Foundation layout
58919954-6dcd-5c72-82f8-3b69b8745b10 | note | Alignment with approved drawings and site plan
eef92179-269a-42b6-b6e2-c7883bb9fc88 | signoff | United Civil Hold Point
e94e29ce-db08-4d9d-9d7d-d3249e76f17e | checkpoint | Site Clearing
89b21391-9ab5-57c7-9d70-6f6ed7462346 | note | Visual inspection of cleared area
99bad2ea-93c6-503a-ad31-c3bed656ee6a | note | Free from vegetation, debris, and obstructions
2b398180-937a-4cd0-9466-13dffc0777f7 | signoff | CHINT / United Civil Hold Point
cb98e4ed-fbf3-484b-9f71-11cb6d1f466b | section | Material Procurement
ac627828-823a-4e48-b9fc-03ee2a6d1540 | checkpoint | Review of Concrete, and Reinforcement steel
7be5fb85-e7ea-5d8f-a331-93766c6a279d | note | Compliance with IFC Drawings, Specifications and Standards
7fe1abae-c63b-5f74-89cb-95dcebca2b0f | note | All reinforcing bars shall be Grade 300E or 500E to AS/NZS 4671
34308fcc-5c28-593d-a0cf-0725be1b1ff7 | note | All concrete construction shall be in accordance with NZS3109 and IFC Drawings
cebc259c-71db-5a9f-914c-9f97417ef779 | note | Concrete shall be 40MPa Minimum Strength for precast elements or 30MPa for concrete poured insitu
5cb7c252-138b-5aa3-b126-1317931d4e0d | note | Material Test Certificates / Dockets supplied for each delivery/Pour
a791eb8e-6026-43b3-8290-7f41ce74bade | signoff | CHINT / United Civil Hold Point
d3aa878e-3d56-4910-bb35-727385d270f9 | section | Construction - Excavation
ea1a3a50-e6f0-4173-9422-da581ab169af | checkpoint | Excavation & Footing Construction
7602fcee-e56c-5fbc-9697-6d064190b6a0 | note | Visual Inspection of each footing location
d4a16d6b-209b-5535-ab5b-fd7935f0b71f | note | Check that depth & dimensions comply with IFC Drawings
0b9ae81a-4cd1-59d2-bac4-de51edca302b | note | Compacted hardfill pad under footing locations
fcb5a40c-8b8f-5ee1-87a9-717b216ee6bb | note | Results Recorded on Clegg Hammer Checksheet for compaction of each footing
11e95a57-9016-4174-8bcc-80aadc76dd5b | signoff | United Civil Hold Point
4a44a0a6-e99b-4174-9f08-23ed8c3aa6d3 | section | Construction - Concrete
4660680a-43ff-4856-86ba-b8bd56a509fb | checkpoint | Formwork Installation
5d461957-ccbc-5c17-baee-1d6d9a7559c1 | note | Visual inspection of formwork alignment and cleanliness
d5583a83-eaca-5c09-9c15-ae561d586923 | note | Compliance with IFC drawings; no gaps or damage
3c64d48a-bcea-5452-805a-6159fb2bab1f | note | Prepour Inspection completed for each pour
b980daa9-ee59-4eb4-9d9a-725decc80ffa | checkpoint | Reinforcement Installation
bff7b163-6acf-59ed-bce5-146bc5195139 | note | Visual Inspection of steel bar placement, cover, and tying
7db7c8d9-615f-504b-943f-5cdabb9ed3f4 | note | Compliance with bar bending schedule and specifications
525154c4-f998-524b-93be-72b40e4bb2a5 | note | Prepour Inspection / Inspection Report for each Pour
5cdef193-1bc2-4f07-90fe-b7cf69b6e00b | checkpoint | Embedments
dd591385-07c0-57ba-b54e-600fdfdea6c7 | note | Positioning of anchor bolts or inserts
16a7fb7a-aa13-5455-8095-e21710bf4d93 | note | As per approved IFC drawings
407064ad-5a3c-547e-b2b3-f8eebd611004 | note | Dimensional check
22cb0ec2-cb22-526e-975b-ffc4daf11bc9 | note | Prepour Inspection / Inspection Report
b0e8091c-bdb1-4010-9ee6-5f245063461d | checkpoint | Concrete Mixing
82177146-006d-5df4-a91f-8cc3025e501c | note | Verify Certified Batching Plant is used
d9f48488-8220-59c2-82a0-23109661363a | note | Concrete Mix Delivery Records
90f5027a-6ea8-5da0-acd4-0da25119576d | note | Prepour Inspection / Inspection Report for each Pour
2a94e774-eddf-4f37-83ab-d99916fd838f | checkpoint | Concrete Placement
15790235-56c2-5501-b83a-60de9c8af924 | note | Visual Inspection during pouring
a3f3fa93-f52e-5792-b5f5-e32315c321cb | note | Proper compaction of poured concrete, no segregation
844ec4c0-eec0-5619-b3de-4177110e5b0a | note | Each Pour
27e2532d-5643-4866-84e8-07dd87b2427b | checkpoint | Slump Test
7b036388-786b-5d5a-a91a-6d853e4a3be7 | note | Tests Taken in accordance with NZS3112.2
8093842c-991e-50bb-ba34-605e21aad6a8 | note | Slump Test Report
f6cc91e7-cd01-57ea-b54f-9cd805e8094c | note | Per Pour
2f280c82-78f9-4b17-8305-b7e8c2769396 | signoff | United Civil Hold Point
574ca381-0a84-4be0-9a6b-b8a71643204e | checkpoint | Concrete Strength
aa588c8e-ce2a-5a11-bcf9-679d59cf375e | note | Compression test on cylinders taken in accordance with NZS3112.2
17f887bc-3e1c-5e98-8996-130b17cbf062 | note | Meets required strength of 40MPa for precast element or 30MPa for concrete poured insitu
5a12dca7-fe69-5b47-b582-2b2563b07cd6 | note | Test Report
d0a25b7c-de58-4ae3-a600-f711937e89a9 | signoff | United Civil Hold Point
565142c5-cc5c-473b-8555-bdfe11d2b5fb | section | Post Construction
9b8f54af-6abb-4c1f-aa37-e04d9181a816 | checkpoint | Curing
7132febf-4e5a-55a4-b0ea-b8158562792d | note | Visual Inspection of curing of concrete
08fed105-2018-4304-805b-d2efbc4872df | checkpoint | Foundation Alignment
32095aee-468e-5b70-9184-17b52f9c76c8 | note | Check position and alignment of foundation
f2bedc2f-f5e1-5a50-a534-82d8de75aa50 | note | Dimensional checks & compliance with tolerance in drawings
21c2601d-3d4e-576c-9c00-383505c8ec0c | note | Larger Block dimensions should be 3338mm x 600mm x 770mm
e2f0ce4e-2634-5ba7-acdf-c0b2c4c49f25 | note | Small block dimensions should be 3338mm x 500mm x 725mm
175e39a4-d59a-4fa8-8626-4c96885ba60a | checkpoint | Surface Finish
6f7550b9-e1ff-53b7-9d46-cb9309c30e79 | note | Visual Inspection of surface for cracks, voids, and finish quality
0e79732d-697a-56f9-964d-f776c0530b75 | note | No visible defects or honeycombing
32f0db4c-221a-5bd1-baaf-0000bdc62831 | note | Every foundation
14728c59-0247-4c49-9d8b-4bf6d0815ed4 | section | Inverter Container Installation
ecb27e44-36bf-4186-ad98-8d389c35c95c | checkpoint | Anchor Bracket Installation
d7e454f7-60d6-506a-b89a-4dad787d2ee4 | note | Compliance with IFC Drawings, Specifications and Standards
1c65f327-6e1d-5a7a-8d78-248954adf6c2 | note | Material Test Certificates / Dockets supplied for steel and galvanising
dee699c4-fb20-5464-83fc-ed3abd9ec3b0 | note | Hold down bolts as per IFC Drawings and specifications
4ffed571-688b-5c3d-a356-622727685a28 | note | Epoxy to be as per IFC Drawings and specifications
1db7adfe-e027-52cb-9651-1e2febdff8b5 | note | Grout to be a minimum of 20mm thick under Anchor bracket plate
a84dd9dc-3cf5-4960-bcbe-bb65823a9962 | signoff | CHINT / United Civil Hold Point
f7557f18-62cd-4d2d-96d5-73969ca4ea0e | section | Post Construction and Handover
fe7034c8-ec42-43eb-a048-4d2bd9e18cd1 | checkpoint | Final Walkthrough & Inspection
2b922f96-2fd5-5b63-97d2-f02a8a862701 | note | Comprehensive inspection of all elements relating to the Inverter Foundations
7526a8bd-384e-5a73-8659-3cea3c40afd4 | note | Compliance with IFC drawings and specifications
74034241-f72d-569b-9efe-2708b468dc0e | note | Verify all Inverter Foundations meet design and functional requirements
df82b430-6537-53e0-9c98-1b60f28c6484 | note | Inverter Foundations ready for subsequent construction activities
3fa83fa4-7062-4eae-af00-f517cefebc4c | signoff | CHINT / United Civil Hold Point
476e73d6-a552-43cb-9b13-8ac37bad88da | checkpoint | Non-Conformance-Reports
58391f23-4839-51ef-a108-b9c12861bbe7 | note | Each Non-Conformance Reported, Rectified & Closed Out
bda39839-e5b2-42f8-8282-0b4d3632b451 | checkpoint | Punch List
74d5a0ed-2ab2-5638-b275-a90fa168bf2d | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor
5380513b-1284-402e-a654-3b6aaf93aa40 | checkpoint | Documentation
d7daa829-a1a5-56d5-9877-adc2c7f12721 | note | On completion of the Inverter Foundations
0f6ba1ea-312a-5cf6-b917-c08a47a80d52 | note | Submission of all test results, ITC's and any as-built drawings
6543104d-127e-5445-8422-83a5354c19f3 | note | Complete and approved by client
01941b37-1bde-4938-b1fe-c3bf21a6bc19 | signoff | CHINT / United Civil Hold Point
681eac53-c863-4037-b100-cc05a8b51ba5 | checklist | ITP - Laydowns | itp | ITP - Laydowns
ba5cf97b-09db-46c9-a908-940b44ba2f11 | section | Preconstruction
a940e2f6-7a75-460e-8ed5-fc8604befee2 | checkpoint | Design Drawings
9bfbd26a-d788-5e80-aea6-008b3266f68e | note | Issued for Construction Drawings available
e0df34b2-cbea-4b83-836d-18458998052c | signoff | United Civil Hold Point
2832fc8d-ec1f-4b6b-ba49-63a740a5c68a | checkpoint | Survey & Setout
4a4251b5-6e05-54f5-82c2-58a1135362c7 | note | Verification of road alignment and layout
caf462fd-d9a2-5201-a127-af27024487e5 | note | Alignment with approved IFC Drawings
5d53cac9-6879-4944-a666-67aa34c29fe7 | signoff | United Civil Hold Point
54ec5e4a-2cd9-43f0-92c7-38144d582785 | checkpoint | Site Clearing
079395b3-ee20-5fbb-8bf8-a890c58dc723 | note | Visual inspection of cleared area
acbf29b2-1547-52a3-8c0c-c09a52daa933 | note | Free from vegetation, debris, and obstructions
cce89b13-2477-4a9c-84da-07948115f86f | signoff | United Civil Hold Point
22c4f7c0-ecf8-4a61-a5e4-adbd3681530b | section | Material Procurement
8a8b9fb3-cf85-4d75-94d3-417e9d369d30 | checkpoint | Material Approval
f826cc1f-4e46-5ab8-8a09-0ee21aa1ca66 | note | Approval of road materials (e.g., aggregates, subbase, basecourses
79b96f08-3167-5dc7-894f-cfe21f874537 | note | Compliance with KDC EES2011 specifications and standards and IFC Drawings
8f01c985-450e-520c-8b3a-53bdfb562301 | note | Material Test Certificates - Gradings, CBR, Crushing Resistance
0b978d38-d8bd-490f-9706-fd2cb3cbe365 | signoff | CHINT / United Civil Hold Point
a8fb1cb4-bbc6-48e4-90c1-d034eef6f070 | section | Construction - Subgrade
57bc44a1-eaf3-40ba-ace7-e6c7f7bdd530 | checkpoint | Excavation/Grading
be68cb35-f164-5f39-8c69-087dce1674e1 | note | Inspect grading and levelling of subgrade
1cd9ccc3-4412-5f32-bfbb-84f70bd03a8b | note | Uniform surface with proper slope and drainage
e8d96996-69d6-5e54-854f-bf244b53bb48 | note | Visual Inspection and Measurements
3ad8dc38-ab5c-59f4-b84b-8e5bf89535ba | note | Every Internal Road
3ad1a8ad-77a9-4303-b829-f0e80b78541e | signoff | United Civil Hold Point
16eaa2d6-469b-4421-9cc6-bf0b5d0a9c34 | checkpoint | Compaction
e2682894-b734-54f8-bb62-250838caccd9 | note | Field density test
5ab292c0-438c-58d7-8f95-da91d86f62ca | note | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m
ed5c81f2-c794-569c-8a13-49ecc9d38ea7 | note | Scalar Penetrometer test check sheet
2c7411ae-f78c-57f7-92d2-26f28da300e0 | note | For each section
7aed4907-979e-49e6-9d57-d0aecf4b39ea | signoff | United Civil Hold Point
aeca93b5-5c58-4a64-99ea-62cdf1efc8a2 | section | Subgrade Improvements (Where Required)
c3fd6497-ca12-4f6e-b467-5ca4622f05e6 | checkpoint | Identify areas of Undercut
8e5a224b-953e-5557-bed7-da324aa78494 | note | Identify areas of undercut and liaise with Client
32407700-5097-435d-89ff-4e1389986bad | checkpoint | Excavate Undercut
a1994f7c-ecb3-5c07-866d-74a95d80ba45 | note | Excavate a minimum of 200mm in depth full width of the road
b019de98-0455-5dc1-bbb5-4f4b012bd381 | note | Any free water has a path off the road in a controlled manor
c0091483-b0a3-50b8-97cc-d540022d0fd1 | note | Visual inspection of subgrade with Client
b7804623-1b1f-5790-a945-5377019fe9b6 | note | Undercut ITC completed
7f10ae93-8bd2-402f-9482-cd635a4b6042 | checkpoint | Geotextile Installation
15a71406-33a1-5c22-acfa-c5a208784f3a | note | Visual inspection of geotextile placement for each section
1b09907f-375e-5755-94ad-39d85b53cbeb | note | Correctly installed with proper overlap and anchorage
b22a95a7-3b80-5be0-972c-01ec09445984 | note | Delivery Dockets
4cfdc63e-6313-470e-9607-8a622cef0870 | checkpoint | Backfill Undercut
3e78876a-520b-520d-a0c3-5a468dc357bf | note | Visual inspection of backfilled material
b2bfd069-0ef1-5ba1-b6b0-71af9e059a8b | note | Compaction to be static compaction only
97384a70-1952-54fb-8829-689ff8086459 | note | Proof rolled with no obvious weaving or areas of instability
25a48c49-65d6-4539-9274-45a30f1e2f27 | section | Construction - Base and Subbase
c69293d5-16b5-483e-8537-9ecc591d2258 | checkpoint | Material Placement
87993e91-54bb-58e3-a38d-e1b17384695e | note | Inspection of base and subbase layers
04e73905-2c27-504a-b4ec-c50367338fb3 | note | Compliance with IFC Drawings and Material Specifications
b4953d51-1ba3-5220-867a-021a5d337e65 | note | 100mm thickness of Gap40 and 50mm of Gap20
74b70a3c-4a36-4c8a-8bdd-5f74915a2d0d | checkpoint | Compaction
982fcaf4-ec99-5dc3-8716-f0d232d96e54 | note | Proof Roll
d1ec8c7b-e571-533a-9a4a-2a0e8fefa23a | note | Visual Inspection of Compacted Base and Basecourse
2c614dc7-0272-5d8e-9d10-9919c237d594 | note | Each Laydown
e1bfe800-0792-4e9e-b13b-c7845269e820 | signoff | United Civil Hold Point
2df93a48-58d0-487a-a496-1f563135399c | checkpoint | Level and Alignment
0fd7c24d-6f4f-5631-9041-463a8b2d3789 | note | Visual Inspection of Alignment
ca794cb3-58a5-52c7-9b75-b202d36d9dd5 | note | Compliance with design tolerances
db74f754-a884-57f2-81e7-158a89dbc28c | note | Each Laydown
2100772b-fb20-4399-ad0b-3ccea36b49a2 | signoff | United Civil Hold Point
ea31d84d-5417-41bc-9c3c-398ee56863ae | section | Construction - Surface Layer As Required
a144a0be-cf6a-4d5e-96ff-f41127e8e956 | checkpoint | Aggregate Placement
091b5675-b146-5bb3-a92c-572db289636d | note | Inspect placement of aggregate layer
25cd98f9-0b2e-5482-a709-288cebf70c90 | note | Even distribution; meets design thickness of 50mm
11006f77-82ca-51be-bab8-8f198bfd573e | note | Each Laydown
7076234e-a2c4-4c9c-8eac-8d9df0cf86c9 | checkpoint | Surface Compaction
07845a50-b67d-5435-9dcb-dc56a1155a41 | note | Proof Roll
77bf7cda-c137-557a-8037-ce585232b84b | note | Visual Inspection of compacted surface layer
36103f0a-5824-5a6d-910d-d0aea6f5af8e | note | Each Laydown
0b894adc-10f0-466a-8843-68bf3038ea0f | signoff | United Civil Hold Point
03da886e-d1ec-469d-84f8-0ed8c1268e2c | checkpoint | Final Grading
27b1f1ab-624e-576d-b4df-cffa2c625b8d | note | Visual Inspection of final grading and surface finish
5f990bd4-ccf5-5db9-990c-8e5ae27fde5b | note | Smooth surface with proper slope for drainage
8d60a8a0-a573-5d19-b1f0-008e5df926db | note | Each Laydown
4b32bf93-4fbf-453f-87a3-80f50c97a26a | signoff | United Civil Hold Point
80eb25a2-2f96-47f8-91ea-c6f939804f41 | section | Drainage - If Applicable
41fe9584-5cb7-4b79-9309-16f57427eb43 | checkpoint | Culverts and Drains
d13da9fc-bd63-5c1a-bd70-d93d5bd2b933 | note | Visual Inspection of installation of culverts and drainage channels
204707cf-36f0-5c68-b0c7-7a18c16c2412 | note | Installed as per design; no blockages
ff2b66c6-10e0-587c-91fe-6bab26a7bcab | note | Water will flow without deviation
1dc4ab8a-ad93-48ae-ab44-0b884b888bb7 | section | Post Construction and Handover
16217ce7-3c62-4dd1-b9a2-0424a91ff8e2 | checkpoint | Final Walkthrough & Inspection
352d3fd4-0318-5cb9-b013-502c65ade5bf | note | Comprehensive Visual Inspection of laydownsn & ensure laydowns are ready for use
176647ed-45c2-5f4b-a0cc-492df4fb88d0 | note | Compliance with IFC drawings and specifications
79b86a1b-96e6-5983-aac5-ea53a3aab398 | note | No defects
d304e028-0e03-4aaf-8e09-d4123682402f | signoff | CHINT / United Civil Hold Point
1fc48483-e371-4ec0-90ed-d80223510008 | checkpoint | Non-Conformance-Reports
98989017-ce48-5830-949e-d87ec00a19a6 | note | Each Non-Conformance Reported, Rectified & Closed Out
9705bcd5-6f69-466f-8776-e381197afd3c | checkpoint | Punch List
4d9aa531-384f-56ae-904f-0da745c719a5 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
5691c122-46f4-48df-85d0-2a826ade9f85 | checkpoint | Documentation
d91346bf-aad7-516a-804a-70d9437bd25d | note | On completion of the laydowns
786492a2-8704-597d-966f-68c3df604396 | note | Submission of all test results, ITC's and any as-built drawings
c21c3a04-826c-5094-95b3-ab9da2b8a605 | note | Drone Survey as-built for alignment and levels
a9454d01-5d84-4588-9980-8c723085d649 | signoff | CHINT / United Civil Hold Point
90cbf5b7-d277-4f4b-9faa-45df984e4a77 | checklist | ITP - Light Pole Foundations | itp | ITP - Light Pole Foundations
806018a6-f2cd-4f20-b9e3-02d77ff83c45 | section | Preconstruction
0ee23d5f-1444-46d4-8c06-4a814a3b3443 | checkpoint | Design Drawings
66db5928-911c-5c8e-aba1-631f0e7f502b | note | Issued for Construction Drawings available
d083f88c-5629-5d09-92f6-617b4865d49b | note | Drawing MSF-EN-ELE-DRG-070
7efc776c-a6b2-4720-a181-35dc74927a27 | signoff | United Civil Hold Point
8bc01336-a9af-474c-b949-b0dcf73ac162 | checkpoint | Survey & Setout
6766e542-2a5a-5e99-8162-c37815927ea8 | note | Visual Inspection of Light Pole Location setout
a6d64fcf-b37d-5c5e-868d-2c4dfaf43444 | note | Alignment with approved drawings and site plan
9025d4b3-a0d0-469f-be49-b04583e08404 | signoff | United Civil/CHINT Hold Point
e97fd8b1-dde0-4733-8501-928ad7d09420 | checkpoint | Calibration of Plant
0da20da5-b030-565f-9588-2dd123328c55 | note | All testing and measuring equipment calibration certificates valid
825066e9-cf8b-470b-bbbe-066ce24a11d6 | checkpoint | Site Clearing
c7d6b7f3-b752-5280-a02b-54a680d0abd2 | note | Visual inspection of cleared area
86a8c6d2-d1cf-5143-aa5d-92e61dbcf5a9 | note | Free from vegetation, debris, and obstructions
540fbb08-4de6-4d92-a68b-059cbd1c5a9b | section | Material Procurement
315b913c-61fd-4bbf-9577-28e968b9b22a | checkpoint | Review of Concrete, and Reinforcement steel
176e31fb-105c-5e8f-b437-8c4cde91177f | note | Compliance with IFC Drawings, Specifications and Standards
a264f3a7-2232-5b03-8cea-7404f159e981 | note | All reinforcing bars shall be Grade 500MPa to AS/NZS 4671
230edadf-e7ad-5c58-9b6a-f730a626dc1b | note | All concrete construction shall be in accordance with NZS3109 and IFC Drawings
c4cbaf59-f808-5ea9-8d19-8261e4829636 | note | Concrete strength shall be 25MPa
48b61cef-f99b-5f2b-891d-a9ca5646d16a | note | Embeded threaded rods, nuts and washers shall all be M16, grade 8.8
d7cd0ab2-1be6-5604-88bd-c77a175f258f | note | Delivery Dockets supplied for each delivery/Pour
d54a2b2f-96ef-403b-90a0-e6d7bec3eb3e | signoff | United Civil/CHINT Hold Point
6c9fb1f6-374d-410c-9f62-e1c6a797db59 | section | Construction - Excavation
9824b7f3-0582-49e4-bc67-ce491a78dc0d | checkpoint | Excavation & Footing Construction
538c4da4-9d75-5e98-8b08-1c63dbff4bab | note | Visual Inspection of each footing location
057b156d-f1ab-5ba7-b44f-ac935113513f | note | Check that depth & dimensions comply with IFC Drawings
f6cd1063-2ccb-5f92-9996-a5910616c0e8 | note | Bottom of foundation pad must be at least 350mm below ground level
90964c9e-00f5-5432-a781-57ceacb52601 | note | Compacted hardfill pad 200mm thick of Gap40 under footing locations
fb2fd412-debb-57ad-9b2f-910cb9d975e8 | note | Test acceptance to be a clegg test recorded to min of 24.
efb5cf26-d116-4488-b9cd-a826ad641cda | signoff | United Civil Hold Point
03a533af-94cb-4257-99a4-7465d39ec550 | section | Construction - Concrete
7156fec8-cfd9-4973-8590-48334e50b4d2 | checkpoint | Formwork & Reinforcing Installation
7628125e-d178-5c26-907a-1f8d13ee01cf | note | Visual inspection of formwork and steel bar placement, cover and tying, alignment and cleanliness
69d15d14-07cd-5acf-8349-5b15dc8a9be2 | note | 75mm Cover is maintained to ground and all formwork
d3900731-0c08-5818-b845-de37e93401c7 | note | Compliance with IFC drawings; no gaps or damage and formwork set for finished level to be minimum of 20mm above finished ground level
794ca97b-58c7-5250-a118-78fe736f40f5 | note | Prepour Inspection completed for each pour
d955e090-6610-491f-8311-ea8ff8fca94f | signoff | United Civil/CHINT Hold Point
303ab262-fea1-4f76-ab14-fb24238891fa | checkpoint | Embedments
693f5e37-00cf-5209-8f37-d3a93fb453e8 | note | Visual inspection of all embedded items before and following pouring
27b422c7-186f-520f-b106-894b74207963 | note | Positioning of anchor bolts or inserts is as per approved IFC Drawings
c48660fb-f18d-5650-8f20-e0fba57c8267 | note | Hold Down Bolts dimensional check - min. 30mm from underside of plate to top of foundation & 220mm from embeded plate to top of threaded rod
3114a1a0-1a83-5fb3-b5ad-5d3e6757b0e3 | note | Installed electrical ducting to have a 32mm duct for earthing & 2x 50mm ducts with 400mm radius extending 800mm below the finished foundation and 200mm above the foundation
00a34af2-6e08-5d41-9b0d-508bb539b544 | note | Prepour Inspection
dd5320e1-00a4-4496-a49d-3afe8c6c74ba | checkpoint | Concrete Mixing
4fb66e45-e579-5d9a-a3d3-4b8b8376b2ff | note | Verify Certified Batching Plant is used
c31cf2d1-5f6b-5a4b-a3a0-42ed2334af91 | note | Concrete strength to be min of 25MPa
fca0acf6-2f67-5c47-94f4-ce0a9980149f | note | Concrete Mix Delivery Records
93f7fac8-8e15-4dac-95d0-f1df51270386 | checkpoint | Concrete Placement
844d2477-62bf-5b5a-9e44-c4052c0fac1a | note | Visual Inspection during pouring
84d44ab7-63f8-5427-921c-186dcf5995b3 | note | Proper compaction of poured concrete, no segregation or honeycombing
052e7820-0670-5a0f-86c3-a277af7579d4 | note | Each Pour
f1cc32a7-237c-47e5-9fe6-b24886c0ead5 | checkpoint | Slump Test
57d3f5d4-520e-5fcd-ae94-7ebd59a1bd17 | note | Tests Taken in accordance with NZS3112.2
c7c4a652-05e3-5f54-bba1-a0d57277f8fa | note | Slump Test Report
96d124e7-f418-5537-bf15-7a1444142796 | note | Delivery Dockets indicating slump
09168e06-9b6e-4e2e-9d1d-9e65352e4839 | checkpoint | Concrete Strength
a8030ce8-abfa-541f-85c2-b4faca2e8aa6 | note | Compression test on cylinders taken in accordance with NZS3112.2
c888e8c2-ca40-59dc-918a-72ebbb15a01c | note | Meets and exceeds 25MPa at 28 day test
be1dc705-805e-54af-90de-4a5a915ec1b7 | note | Test Report
6ec66220-8f7b-4bd6-8882-cd91d0d93257 | signoff | United Civil Hold Point
03c5b3c2-d80b-4d54-b4b5-5dd195147552 | section | Post Construction
f90403d7-76af-461d-bfc1-cb9e7195b22d | checkpoint | Curing
aaf4c5e8-6926-54ab-8e38-dd872834e177 | note | Visual Inspection of curing of concrete
48d5e346-4076-465e-93e8-862264b4be23 | checkpoint | Foundation Alignment
d181a816-e9f5-5e84-b187-dd11358c71a9 | note | Check position and alignment of foundation
7f619241-8263-5390-9537-35e9b6481ea4 | note | Dimensional checks & compliance with tolerance in drawings
42a99296-76e2-4179-9c20-d44fcb797560 | checkpoint | Surface Finish
67fc3750-b462-515c-b988-4701ed0c0822 | note | Visual Inspection of surface for cracks, voids, and finish quality
e0a40f2c-755d-517d-abac-abacf49e23fa | note | No visible defects or honeycombing for each foundation
244b7d5c-d42a-4ea3-87f9-87027d2152c4 | section | Post Construction and Handover
97ab37c4-4e67-44c1-b3f3-ab773c031e37 | checkpoint | Final Walkthrough & Inspection
34eb5770-2338-581a-b440-d16330b5c4c0 | note | Comprehensive inspection of all elements relating to the Light Pole Foundations
79328e9f-2895-5ff0-a1aa-a2d0ea76b11d | note | Compliance with IFC drawings and specifications
0a5ac852-d740-5793-b94c-60ae571deac9 | note | Verify all Light Pole Foundations meet design and functional requirements
c52d19e8-ab1e-544c-a1f7-cb7df96827bb | note | Light Pole Foundations ready for subsequent construction activities
1ef57d62-63e0-4166-93f6-47a061568486 | signoff | United Civil/CHINT Hold Point
0ffc9612-a928-4cf3-95dd-03b16644c6d1 | checkpoint | Non-Conformance-Reports
f2e1d1df-d7a6-5cae-be96-0cd092f7c3c9 | note | Each Non-Conformance Reported, Rectified & Closed Out
c96b058d-4903-407a-9270-34b8bd1a44ed | checkpoint | Punch List
4a9f15ac-a761-589f-88eb-cefc432218ca | note | Development of Punchlist with Client and Contractor Representative
725b527e-3dcc-5ef6-80f5-1c90d76fc2c3 | note | Punch List closed out in a timely mannor
c028214a-51a4-4d71-b465-3605b94a88ea | checkpoint | Documentation
03dc73d1-9cd8-5774-a21d-c47851112407 | note | On completion of the Light Pole foundations:
6e344650-9945-57c1-a615-b823f43c0ff7 | note | Submission of all test results, ITC's and any as-built drawings
b11063b3-b7b1-591c-8ffb-87d93d63d6b1 | note | Complete and approved by client
15f9688a-1e21-4961-8f99-b7cb420fa77a | signoff | United Civil Hold Point
8f7e776c-f69d-4f09-8042-f77bcd5d50fb | checklist | ITP - RMU BUILDING SLAB | itp | ITP - RMU BUILDING SLAB
931809e6-4bc3-4939-a3f7-cfc36c770c97 | section | Preconstruction
baf5c203-e68f-4acc-86a5-d1cb52b9173a | checkpoint-no-value | Location
13430bc0-8844-5f89-9b15-b30f87fdb68f | textbox | Location of Foundation Construction
eeaa1b35-b32e-4f4b-8725-ae8fb3d96092 | checkpoint | Design Drawings
60cccacd-1c07-5872-a63a-1117bea07593 | note | Issued for Construction Drawings available
3275b5c8-fa9e-44f8-851c-0a1b00ad5851 | signoff | United Civil Hold Point
31744272-f799-40f0-a2db-4b50595b5122 | checkpoint | Survey & Setout
7ee075a0-60be-53db-9a47-27839266e275 | note | Visual Inspection of RMU Location setout
3b2538d2-a6f1-5c91-9d21-408d68e3bf49 | note | Benchmark established as a dataum for levels
8f591962-bbc9-58eb-a2a9-58e9cd1e68dc | note | Alignment with approved drawings and site plan
3745c3ea-c1a8-4c3a-8658-92511b521371 | signoff | United Civil Hold Point
1c66b7ca-4f8e-47fb-a01d-f7a7ded6eeaa | checkpoint | Calibration of Plant
f2959b21-9369-572b-baf1-1ed42cd6c4d7 | note | All testing and measuring equipment calibration certificates valid
9e083e31-2af7-4790-8095-6852d6aa0cd5 | checkpoint | Site Clearing
2e079dd8-6cc9-513e-9b37-cfa2902b747d | note | Visual inspection of cleared area
aab65677-57da-5427-979e-2944c6f339a6 | note | Free from vegetation, debris, and obstructions
a47a2f11-7e7d-43b1-894e-fc7b2da1a340 | section | Material Procurement
d5d4be4b-14af-4dbe-b604-4ab6344d1afb | checkpoint | Review of Concrete, and Reinforcement steel
d0deea6b-eb57-5f92-8ea3-4a181bc42cb2 | note | Compliance with IFC Drawings, Specifications and Standards
71b36c45-1b3a-5bab-a221-0b6525a23f0a | note | All reinforcing bars shall be deformed grade 300 to AS/NZS 4671
8217fe7c-707f-50a9-be78-02d0b40dd48f | note | All concrete construction shall be in accordance with NZS3109
c948bb2a-bb88-5a69-8091-f72b0d2e437f | note | Geogrid and Bidim to minimum Class B
352543f3-efde-5381-850b-a45ca6152de8 | note | Concrete strength shall be a minimum of 25MPa
8fe3e502-4e37-5f1b-9890-f2a50a255d7a | note | Delivery Dockets supplied for each delivery/Pour
b2813b41-5963-5ebc-8ab9-06b349daf967 | note | Material test certificates supplied for reinforcing steel
9a4f0633-132b-42b3-980d-9ae873243a76 | signoff | United Civil & CHINT Hold Point
792e3b47-f52c-46c9-a4fc-dc1c6b5426cd | section | Construction - Slab Foundation
d488a055-ddfe-40fb-8049-b8f76cabab1c | checkpoint | Excavation to Subgrade
74bfcccb-b8f8-508f-b94f-a28be33e33db | note | Relevant Specification: IFC Drawings
e4df372f-4369-5e43-8c76-4b92ff2c39ce | note | Test Method: Visual inspection and photos
44fd142b-9394-55b0-9f8f-fc74216fb53c | note | Timing/Frequency: Visual Inspection of the foundation
3e93d2c6-3794-5d4d-a2b2-68b301b7e5f5 | note | Acceptance Criteria:
27cabe23-c994-5fe6-8d7f-42770fdecc29 | note | ○ No organic or unsuitable material is present
5796005e-017e-59d2-bfa9-9056996516a2 | note | ○ Foundation is at the correct level
6dfd1137-dc37-42c0-8c7b-a54831860c1e | checkpoint | Foundation Subbase Construction
8f36f7e9-f4d2-58fd-bb03-04f201553cd8 | note | Relevant Specification: IFC Drawings
ef513674-8607-5091-aeb5-dbbdb829fe73 | note | Test Method:
bb0f7a2f-fd61-5651-bfdf-3492a28ad4d9 | note | ○ Photos and dimensional check that the construction and RL's comply with the IFC Drawings
b4bf4f11-fc24-5064-b446-434efd96864f | note | ○ Minimum of 200mm of compacted Gap40 over Geogrid and Bidim
b73a377c-d8c1-5859-9c4f-34d390fc2b51 | note | ○ Test the foundation layers strength with a Clegg Hammer
9b1d8951-e076-5761-8fa5-d6f4b1ab209d | note | Timing/Frequency: 4x sets of Clegg Hammer tests and measurements to determine the compaction of foundation layers
84fcb2f7-4354-5de0-be6c-b2d84e6cdcc9 | note | Acceptance Criteria:
d5a866b4-eec7-5dec-9b22-87ca40969bc2 | note | ○ Visual Inspection and photos of compacted aggregate and tests
6f9b8faf-53a8-5a1c-b346-fe106d243e9c | note | ○ Thickness of Gap40 shall be 200mm over bidim and geogrid as directed
0e694561-7cc1-5ea3-8f75-bc2acc6a42e5 | note | ○ Clegg hammer tests shall meet a minimum CIV of 24 on the 4th blow for each test
171f3db9-5ba1-427e-9b26-7dffede3eef4 | signoff | United Civil & CHINT Hold Point
6b398b62-20fc-4773-9085-b221d1fe86f9 | section | Construction - Concrete
b6860046-e54a-4568-8afc-2d0c41056d02 | checkpoint | Prepour Inspection - FORMWORK & REINFORCING INSTALLATION
b61853ee-f352-561e-a2b9-b1c96459e9ee | note | Relevant Specification: IFC Drawings
c55618dc-bd06-5e7a-ba77-a918b9776a8c | note | ○ Steel Reinforcing shall comply with NZS3109
a6038130-a7c8-5e6e-b832-b21faff8b52b | note | ○ Concrete formwork construction shall comply with NZS3104 & 3109
eca23f3e-2f2e-5d73-a494-c04f700e4713 | note | Test Method: Visual and dimensional check that the construction and minimum cover required complies with the IFC Drawings & Specifications and Standards
886435c0-c7cb-5733-8bab-be50fbf6aa16 | note | Timing/Frequency: Prior to pouring
1b7622bd-9e97-5088-afc0-d9848ae6db84 | note | Acceptance Criteria:
effc8c24-3c86-55bd-8472-eae00597238c | note | ○ Formwork shall be free of warps, bends or kinks, and the tolerances of the top surface of the form shall ensure compliance with the finished floor tolerances of +/- 10mm
3913fb58-3689-5a83-8815-80291e073426 | note | ○ Reinforcing materials - hooks, bends, bars and surface condition of reinforcement, spacing and fixing, splices, cover and placing tolerances shall comply with NZS3109 unless modified in the IFC drawings
2cb20f7a-6b9c-55c7-84bb-d1dc5e668ae8 | note | ○ Prepour Inspection completed and filled in
f052497b-1a9b-4b8f-9c0b-7fc990197ca1 | signoff | United Civil & CHINT Hold Point
619e09eb-567c-4214-9963-628523a09a39 | checkpoint | Prepour Inspection - EMBEDMENTS
6ed146c1-a8e7-517b-b08e-892bfa71a9d9 | note | Relevant Specification: IFC Drawings
b883ab69-2cbf-57e0-9bb3-3e5f1559e8d8 | note | Test Method: Visual inspection, photos and dimensional check that any embedments comply with the IFC Drawings
236168d3-7974-5c67-9f25-904bc0d13c55 | note | Timing/Frequency: When installed and prior to pouring
d880e265-5249-564a-aa7f-6bfb1f68bc0a | note | Acceptance Criteria:
5cce287d-6ddd-59df-9e46-9b5992c5e09a | note | ○ Embeded items are installed to meet expected outcomes against the IFC drawings
25b0df10-2efd-55c7-b9ab-f246d4a478c2 | note | ○ Noted in the Prepour Inspection ITC
039cfd69-ad06-4620-b2d9-d743eeae3748 | signoff | United Civil Hold Point
2a2340f6-d5af-4d73-8e77-449c602cb16c | checkpoint | Concrete Mixing
589d5715-c28e-5db8-86d8-b0bb44577eb9 | note | Relevant Specification: IFC Drawings NZS3104
c73028a0-1e29-5df0-a1e2-802508d663cc | note | Timing/Frequency: Prior to and for each pour
a0a7d3a5-80ca-5981-8db5-d04763c71605 | note | Acceptance Criteria:
b44ccea3-91f1-53cf-98f6-ad66cde0e668 | note | ○ Concrete baching plant is certified to batch concrete under NZS3104
8fc51bab-63ab-51b7-83aa-799cef7c79ee | note | ○ Concrete strength to be 25MPa
ac6c0fad-4451-50be-b47e-d9c61d016a55 | note | ○ Concrete mix delivery dockets
129d237d-eb93-4352-94aa-a17297e22457 | checkpoint | Concrete Placement
bd946835-7b0c-5278-944c-96800e15ffcf | note | Test Method: Visual Inspection during pouring
8b94073c-721e-56e8-abe2-a9867fc13b7e | note | Timing/Frequency: During each pour
cc1d99f2-051d-5870-8ba6-b115ebdf31b2 | note | Acceptance Criteria: Proper compaction of poured concrete, no segregatation or honey combing
ad813f37-e9fe-485e-b461-d3fc707df9c8 | checkpoint | Slump & Strength Testing
2742a782-6ae8-555e-8802-f0d31dd9e966 | note | Relevant Specification: Tests taken in accordance with NZS3112.2
0fbacdf2-ce24-5a72-8b4e-e4438c0a2404 | note | Test Method:
31d482d6-7288-54e8-a597-0accab2fbd59 | note | ○ Slump Testing
7d63a85e-746d-5636-b544-a2e7cfbcd83d | note | ○ Cylinder compression testing
104d6cc2-852e-575e-9b9e-d0f2851bbd03 | note | Timing/Frequency:
fedb1e9b-45a7-57c7-9dd0-1ba7d4218d83 | note | ○ Slump Tests are prior to pouring
2275da4f-5dcf-5983-b8fd-d5c56a3144ab | note | ○ Compression testing shall be at 7, 14 & 28 days post pouring
9a608d16-14a9-5a1b-9c87-1a160025fa6f | note | Acceptance Criteria:
85c82639-df49-5506-8eab-f6a3531da2b4 | note | ○ Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring
3bdddae8-337d-51e0-9f4a-db90a3f64ecb | note | ○ Test report/dockets shall be supplied
ff30539f-3347-4eeb-aad7-016d67035ee6 | section | Post Construction
2724dae6-7a75-408b-9175-a3fee6d90156 | checkpoint | Curing & Surface Finish
94fb6aa3-a418-5e0b-bbbb-771cdbcf0c0c | note | Relevant Specification: IFC Drawings NZS3104 & NZS3109
4927d11f-6913-50a6-a412-1e0986fd174a | note | Test Method:
36afddd5-97dd-5505-a20e-7d1af043eae6 | note | ○ Visual Inspection of curing concrete
bf6de765-51ef-59f5-a1e2-e0f4b1a74ef0 | note | ○ Curing concrete shall remain damp during the curing period
43bb1a69-0962-5499-a3fb-5f37429ad978 | note | Timing/Frequency:
44ae3500-9e74-5fcf-a916-4c52a625c804 | note | ○ Slump Tests are prior to pouring
92b7d0d9-82a8-5d6b-8a9d-f6c52adaa399 | note | ○ Compression testing shall be a set of 3 cylinders taken from freshly batched concrete and tested in accordance with NZS3112
74b0b0ec-006a-5988-8dda-ceffc6d67a38 | note | Acceptance Criteria:
751e8b43-b067-5509-80a6-8f53f4ce2ce3 | note | ○ Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring
5497b0b2-7076-5b25-82fc-7711f0f5d4df | note | ○ Test report/dockets shall be supplied
e77eb762-17cd-42a2-87d7-a68f527868a6 | checkpoint | Surface Finish
7bc74f9c-3dab-5c98-816e-ab38abf50f40 | note | Test Method: Visual Inspection of surface for cracks, voids, and finish quality
18b0a367-d6ae-509f-b9cf-120452ec7b4b | note | Acceptance Criteria: No visible defects or honeycombing for each foundation post striking of formwork
97ce8a07-9b02-427a-a2ee-70be08a48a99 | section | Post Construction and Handover
7f217a06-75f0-455c-b4b9-4a891d873f1c | checkpoint | Final Walkthrough & Inspection
d22f86ec-6b16-550a-aa75-3c20256b3823 | note | Comprehensive inspection of all elements relating to the concrete foundations
3870ab30-f7d6-5254-9708-e6f1f497bc70 | note | Compliance with IFC drawings and specifications
4aa9da67-59ac-50d1-86b2-3c642a8b7e62 | note | Verify concrete foundations meet design and functional requirements from the IFC drawings to what was constructed
be9cda16-fab3-5f01-a50e-966666a0ac32 | note | Concrete Foundations ready for subsequent construction activities
519ee541-fad1-4f22-8b22-53b0a455e27e | signoff | United Civil & CHINT Hold Point
f27ae57b-2bd3-40c5-844c-6317433cc433 | checkpoint | Non-Conformance-Reports
cd23f437-e488-5e92-8572-cf2b8fd59b03 | note | Each Non-Conformance Reported, Rectified & Closed Out
9690b95f-db18-4976-850c-6b4e1acdb8f2 | checkpoint | Punch List
08736f9e-9e4b-5eec-9312-7266e27820fb | note | Development of Punchlist with Client and Contractor Representative
b4e5a8c7-39bb-5b26-aab3-0e7734bdbac9 | note | Punch List closed out in a timely mannor
a1adffb6-85fc-4845-a6bb-9c79aa4902df | checkpoint | Documentation
ca4781fb-e28e-5c0b-979d-c7b397b7a187 | note | On completion of the concrete foundations:
75ffdb9e-480a-5230-a3cd-cbacd36edbdd | note | ○ Submission of all test results, ITC's and any as-built drawings
f80c3247-3fc7-5713-8465-55c16c03694a | note | ○ Complete and approved by client
c666f2c5-26f9-40f2-98e0-b1d415446761 | signoff | United Civil Hold Point
60bb6767-b7ba-4e23-9352-580637944e33 | checklist | RMU2 Building Drainage ITP | itp | RMU2 Building Drainage ITP
f29b63f1-ea16-4bf1-8d8a-c1c4710939dc | section | Location
58378c64-5265-447f-979b-15f5514ccf01 | checkpoint-no-value | Drainage Location
612fdf5c-8958-53a9-a7fb-68552372b96d | textbox | Location of Installed drainage
b5780f09-38ba-4b65-892a-7ae2652c0e02 | section | Preconstruction
e5ecf769-8d7f-472e-bf6c-9736bce6ff29 | checkpoint | Design Drawings
a2cd9c3a-056b-54be-a239-d11ddd47377e | note | Issued for Construction Drawings available
62b81d1f-bbd3-43e2-bf6a-93e43c9cbeba | signoff | United Civil Hold Point
820bdc55-fcdd-42e7-896f-74a8ad3a60d4 | checkpoint | Site Preparation
74a8c3d0-14df-5ebe-8900-99334a56e448 | note | Visual inspection of cleared and levelled area
85af35c9-44e9-589e-9eda-2e3ed0349018 | note | Site free from debris, vegetation, and unevenness
948847d0-e2dd-437e-af46-78424adb0d06 | checkpoint | Survey and Marking
48ec0c4e-9a6c-5dbc-bf04-2cdc1f0cbff9 | note | Verification of layout and drain alignment & grades
76882df8-2966-53f1-a871-67676af1a780 | note | Alignment with approved IFC drawings
57743ef9-c6ac-50f7-ad5c-3d696fbe86d2 | note | Local site datum found, marked & protected
8c2a5003-c8dd-41c0-baa7-3918fb8f5509 | section | Wastewater Construction & Installation
c5ccb4f9-1ce3-41f0-942f-7ea4563fa6a5 | checkpoint | Material Approval
a890d70d-61e4-5430-956f-e36ff24657da | note | Review and approval of pipes, culverts, and other materials to comply with IFC drawings and specifications
18f62a62-e9bf-525c-b333-0aaa30183e7f | note | Wastewater pipework shall be DN100 PN12 PVC-U, all fittings shall be rated & compatible with the pipe
b66431cf-adee-5167-a7de-2e72cdb020d5 | note | Wastewater tank shall be a Promax Enduro 5000L Septic Tank
602ae1e6-6a21-5dfc-afb2-9267287b76c6 | note | Material test certificates and or delivery dockets attached
368f1596-5278-48a9-9c2f-13d652045a77 | signoff | CHINT / United Civil Hold Point
8518ea4e-f0ca-4554-a4cf-518f48263744 | checkpoint | Excavation
d81a80a7-b4e0-51f3-88de-3810db5379a9 | note | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework to comply with IFC Drawings
21206bbe-75ac-54c2-b2cb-02f18aae27de | note | Depth, dimensions, and cleanliness checked and maintained
ad774618-7a25-41b2-9451-1ee52d0c27c2 | checkpoint | Soil Stability
126fb4c0-d012-54dd-a823-944d9d37bf25 | note | Inspection of trench stability and shoring/battering/benching is installed where necessary
30b2e48f-1f3d-5c04-94d0-f46205a7fea2 | note | Stable and safe for pipe and tank laying
2c965a05-e704-4236-94ad-68183519ddbd | checkpoint | Pipe Installation
9e0b3140-f5f6-5d47-a6bd-b8546c79d30a | note | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
fb6515e3-63fc-5e63-b1a4-742b230b3038 | note | Pipes to have 75mm of Gap7 bedding and top cover
4e802db9-6cc5-5814-a8df-afae089c0033 | textbox | Wastewater pipe grade installed to
d89df939-44a4-5c13-acaa-5d7d3808241b | note | ITC Completed for pipe installation
7fcd3b16-79c1-4f2c-a32b-1a38b348e21f | signoff | United Civil Hold Point
90f1f6ee-b122-4c78-95ae-9c2bc2d5c8a3 | checkpoint | Tank Installation
bd8bbccf-585e-5574-b9d2-d51041cffc4c | note | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
757be7c7-5693-55a5-8b73-4ff09a31fabc | note | Tank to sit on 100mm of compacted gap20 then be backfilled with Pap7 to the pavement layers
60a153b8-b213-5a54-a141-3649073c3d2d | note | Tank half filled with water before backfilling
fc1f34c7-3815-4c3b-ab4e-938a23d9d6b2 | signoff | United Civil Hold Point
43307eb3-d7b4-4d4c-820b-93aa2ef26dd1 | checkpoint | Backfilling
c42c5aa2-6d44-55af-9d21-cf7f7ec867ea | note | Visual inspection of backfill material and compaction
11e5fdb2-22b5-5c6c-956d-7974f061e66e | note | Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
f9439541-6fd0-57f4-890d-bad5075f9932 | note | Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
cc034f02-68b7-5efe-a1cf-6d1b0d3d35a6 | note | ITC Completed for Compaction Testing
5746b55f-d98c-449e-ab72-03bedb8ead75 | signoff | United Civil Hold Point
dfb52a01-736c-421e-b851-1e16f4a35641 | checkpoint | Hydrostatic Test
4cca0b21-31d8-5a30-87d5-9905e54e62e5 | note | Visual Inspection of hydrostatic leak test being performed
427fe18c-5ade-52df-95a4-d53cc2ee032a | note | Hydrostatic pressure testing of pipes for leakage As per NZS4404 Appendix C
61144f43-14f4-5e7c-b2a8-e86662eb9302 | note | Leakage/make up water does not exceed 0.5L / Hr per metre length per metre diameter (0.5 * 5.5 * 0.1 = 0.275 L / Hr)
6ecb4a71-9a2c-58ed-9785-e147db6ca914 | note | Hydrostatic test holds and passes
b51630ab-9345-4294-9015-e312289f9f9c | signoff | CHINT / United Civil Hold Point
ca0f7a86-1514-44c9-9984-bf1426775e76 | section | Subsoil Pipe Construction & Installation
a153ca46-103c-4b55-9889-12c3377abce3 | checkpoint | Material Approval
7930c267-21df-53e0-999b-9c384a3f9ce6 | note | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings
2927c3ac-ec28-5966-a05e-31a0b282e6f0 | note | Subsoil pipe shall be 110mm dia Novaflo subsoil drainage pipe with geotextile sock surrounding
953e16fe-83b8-5612-98ff-3635f4363739 | note | Material Test Certificates / Delivery Dockets attached
fefebf48-a911-4140-9eab-c19e74d4ce01 | signoff | CHINT / United Civil Hold Point
ee2a9231-fd85-4b56-b4f7-af22c26414cc | checkpoint | Excavation
8e87e2c2-28be-5dcb-8bd0-cee6f6fbd2ca | note | Visual inspection and measurement of trench to comply with IFC Drawings
51fb7678-a127-54b2-8190-2d55ac4b260b | note | Depth, dimensions, and cleanliness checked and maintained
c219dde0-bf2e-48ae-b108-579971a20632 | checkpoint | Soil Stability
3ec60ee2-c092-549d-90e4-4c77ea4f65e5 | note | Inspection of trench stability and shoring/battering/benching is installed where necessary
c5c61739-9839-5426-81d1-8b65dbd5ad3c | note | Stable and safe for pipe and tank laying
63d9eadc-c941-4375-8541-5070af80e34f | checkpoint | Pipe Placement
b4ca311b-d1b8-544f-8cb7-e7ac8730ff5a | note | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
17375416-b66d-5776-bbc9-0eba9bb97be9 | note | Subsoil pipe to have a 1% grade to outlet
affcc8fd-0418-4fd1-be33-f6ae675a0058 | signoff | United Civil Hold Point
44c0f696-ebc8-4415-8cb2-c677c4884223 | section | Stormwater Construction & Installation
15101936-47ca-43eb-9e48-ce4522b7570f | checkpoint | Material Approval
d8c15633-4169-5295-946c-19d5d28ce492 | note | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings and Specifications
c355d4ea-d842-52f7-8f3f-203827e8b2d1 | note | Pipework shall be DN90 SN4 PVC-U, all fittings shall be rated & compatible with the pipe
fde16a61-ba51-59a0-91e7-26bcc109c369 | note | Stormwater Channel to be lined with Bidim A19 Filter Cloth
541474f8-bf4d-5224-9704-b3f09c657a8c | note | 150x50 H4 Radiata Timber edging for the water tank surround
b6151099-bc5d-5890-a7a1-8dbb6b5aa88d | note | Material test certificates and or delivery dockets attached
bd0d82bd-dfdb-44d7-859e-10815d3d9b3b | signoff | CHINT / United Civil Hold Point
75a18d38-1aef-4929-a0c5-1d21fe133efd | checkpoint | Excavation
a129e3e6-8bf1-547c-91e2-0cb44bf87e46 | note | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework
11c10e1b-ca68-56b7-b7a2-4b97d1eb839a | note | Depth, dimensions, and cleanliness checked and maintained to comply with IFC Drawings
f2b17227-d0c1-4675-bba1-3ebb7b036800 | checkpoint | Soil Stability
69cf1f8a-8a6d-540b-80b2-1aef46600c2e | note | Inspection of trench stability and shoring/battering/benching is installed where necessary
cda42e2f-8d5f-59b4-b119-e036d0b91e51 | note | Stable and safe for pipe and tank laying
210a4a6b-37b7-4427-a3fb-5f266725af9a | checkpoint | Pipe Installation
aa844b31-5ece-538d-b54e-fd35fde07e0a | note | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
2b88dda9-bffe-580d-b397-5bb16685876c | note | Pipes to have 75mm of Gap7 bedding and top cover
b8db178b-e454-5811-a0c6-c423520a5db5 | note | ITC Completed for Pipe Installation
445b521e-ce6f-42cb-b696-3b8f363c791b | signoff | United Civil Hold Point
b627d264-d528-4755-a9f6-9b2ffe0bdc99 | checkpoint | Tank Installation
d2328b93-0da7-5da8-8e62-510516f4c67e | note | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
2c8498f3-29ea-5b33-a3e5-1b2da903adb2 | note | Tank to sit on 150mm of compacted Gap40 and 100mm of compacted sand
04de7dab-7aaa-51c8-ab8e-b7ce94789804 | note | Compliance with approved IFC Drawings
0fb4ab3e-dd47-4e0c-a5fd-a958ec2c0cbc | signoff | United Civil Hold Point
512b833b-6b86-4a3f-bfc8-52d59437d24d | checkpoint | Backfilling
72918d12-f319-56e3-ac61-85fbd67a533f | note | Visual inspection of backfill material and compaction
d57637c9-9a45-551b-a5b4-c720c3d77590 | note | Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
cc638918-fa3d-501e-bd18-c17a33867a6c | note | Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
6c44c46c-edc9-536c-a1d5-4e957ec4c539 | note | ITC Completed for Compaction Testing
8d9661d1-262e-4265-949d-b3047d7048e9 | signoff | United Civil Hold Point
f676f856-60e0-44fe-bee9-201765e39fc7 | section | Post Construction and Handover
d3234399-680d-495f-9cf8-60711c8eee13 | checkpoint | Material Approval
d3d3ff99-2477-57dd-a5d9-3ee011e4c316 | note | Final Walkthrough & Inspection
3e25baf4-4189-58a6-b240-ebd6fe005bb5 | note | Comprehensive inspection of all elements relating to the RMU Drainage
1bf9e0e5-e75e-5d1c-a435-ce812e236480 | note | Compliance with IFC drawings and specifications
c55bc136-149a-52e8-a096-23d47afb627a | note | Verify all Drainage meets design and functional requirements
895d6fa1-f6bd-4fe1-b2f8-707f8a6dc0a0 | signoff | CHINT / United Civil Hold Point
5a20980f-c8b3-4076-bc60-1e2902934b10 | checkpoint | Non-Conformance-Reports
4a94fd4b-c9ae-51fc-bdf3-f4359c8a1c40 | note | Each Non-Conformance Reported, Rectified & Closed Out
05f3162d-82da-4ee3-82bf-e6385f036a7f | checkpoint | Punch List
835b2a48-8360-5614-9e53-7b137a817032 | note | Development of Punchlist with Client and Contractor Representative
77688090-dc9f-556d-9614-8765f8276194 | note | Punch List closed out in a timely mannor
caf50dfb-9be1-45f0-ae7a-d432fde351db | checkpoint | Documentation
82920611-04f8-55e2-9971-8248e19db9b7 | note | On completion of the RMU Drainage
a74d5de9-ff35-5489-a367-b8c1ac973ace | note | Submission of all test results, ITC's and any as-built drawings
28366fe9-c399-5e0c-8b7a-b1d55f0c7811 | note | Complete and approved by client
8a3fea00-5d26-4fe0-aa0f-6a34df70400f | signoff | CHINT / United Civil Hold Point
7764bff6-43ab-4953-be92-49cc8d2044e7 | checklist | Ω (DEPRECATED) ITP - Accessways (v0) | itp | Accessways
eb44411e-7358-4f2c-a007-7b9ede5805e6 | section | Preconstruction
f0b19fe1-3d53-4b4a-b100-c8b48f75002c | checkpoint | Design
6b98d0ad-8ae1-5108-9935-cb9a89121bc6 | note | Issued For Construction Drawings:
91f65b03-5f68-5032-b750-db71d7a41a6e | note | MSF-EN-CIV-DRG-510
9df10d6d-b9f8-5651-9016-fa4888f52a93 | note | MSF-EN-CIV-DRG-511
24c3d089-3bd2-55f0-8a9a-a6847102203e | note | MSF-EN-CIV-DRG-512
e3ec4cdd-21c6-5698-b342-b66f0097d92b | note | MSF-EN-CIV-DRG-590
acc871ab-4f6e-5110-8a46-ed2ea77fb990 | note | KDC EES2011
789b6101-2934-4995-915b-d84e6fbacbae | checkpoint | Survey & Setout
94103601-f42f-5db8-9d52-dd2f121979f8 | note | Issued For Construction Drawings
79123cde-23d9-5856-af07-cc5663029d53 | note | KDC EES2011
34b14c6c-1a18-40e2-8490-cd85a6cb9fb4 | section | Material Procurement
b51652d0-f9f9-4285-aaa3-53f617f7ae95 | checkpoint | Granular Fill Material for subgrade improvement (If Required)
26a91109-7d97-5eff-9b59-32afdd8915cf | note | Issued For Construction Drawings
a43eb1b5-f5a7-5d71-a45a-f368a329a8d2 | note | Delivery Dockets if Imported Granular Fill from Offsite is Used
1875ad4b-b9f3-547a-b3d4-9868f38e8672 | note | Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite
f5eb650b-7d7a-4fd5-bcfe-c02f1a8d65df | checkpoint | Drainage Pipe
33a1658f-feb2-5ac9-8e78-46fbf5c179e1 | note | IFC Drawings
cc1f2aff-4625-5a9a-ab32-630c68ef7a9d | note | Manufacturers Specifications
e1bf37cc-3dc8-5c4c-ad43-6b9ec96f4c9b | note | KDC EES2011
c47e58c3-9271-5ecb-803d-5111f0838a13 | note | Delivery Dockets
3a30820f-c2cf-589e-b8c8-2691db06e2b9 | note | Visual Inspections
1683c8f3-93e8-4f82-aa11-03e826e78d45 | checkpoint | Drainage Bedding Material
fc1c298b-c2fb-5dd4-b292-77e02a5e6cca | note | IFC Drawings
c1f66b3b-952c-5e13-9358-a02a11251b9e | note | KDC EES2011
83c44c81-8d67-5bd7-9988-b15b04b5c28d | note | Delivery Dockets
25c90b0f-b24e-41f8-9984-581b7f18aee1 | checkpoint | Gap 65 Subbase Material
f1aed3b5-e8e9-593f-81b6-8ce2ed5e48b3 | note | Issued For Construction Drawings
5e90003e-769a-5c09-bda9-2063d1243487 | note | MSF-EN-CIV-DRG-020
fbb929b0-e819-555c-ae23-ec0bdc7e3e1c | note | Delivery Dockets
84143a42-41fe-41b1-8d2d-a115af5eec4d | checkpoint | Gap40 Basecourse Material
646cd695-8c89-5334-a876-2328fa54eda1 | note | Issued for Construction Drawings
5595ae99-7a76-4399-9876-733188a71f6a | section | Construction
c9fca17f-af4e-4b46-b54c-b7db6aed9db3 | checkpoint | Inspect Subgrade layer and Check Subgrade Strength
d7a656ba-8d74-52b7-ace0-14c6e034aba8 | note | Issued for Construction Drawings
4890f3c5-ef28-59d1-b2a8-18855d7e163a | note | Visual Inspection
2d630f4a-4551-5353-ae4a-01ca87c0c315 | note | Scalar Penetrometer with results recorded of No of blows per 100mm on ITC
31c29654-5b2d-4272-8b69-ab512d85be08 | checkpoint | Drainage Culvert Installation
72033076-ab35-50de-98c7-f96962d44074 | note | IFC Drawings:
3a42cb8a-8b5c-5a46-93d3-e566348d69b3 | note | MSF-EN-CIV-DRG-310
8a7498c3-36e1-5e1a-b81c-498fdcbb2c99 | note | MSF-EN-CIV-DRG-311
f8391e5b-6905-5f1c-926f-50cd423a6344 | note | MSF-EN-CIV-DRG-312
075f95d4-8c07-5d33-8a8c-9723c196f899 | note | MSF-EN-CIV-DRG-313
4af014fb-eca5-5333-b87f-319e40e1b1d5 | note | KDC EES2011 S06
b3f7a670-47f3-5a90-9e69-2932f800bb6e | note | Visual Inspection
ff7e6c06-aea3-5393-b4c2-d326e1aac559 | note | Meets requirements of Issued For Construction Drawings & KDC EES2011 S06
c6fec8aa-2f99-5cdc-adb4-f382bfc69948 | note | ITC - QF008 Pipelines
77840656-7cd5-4495-97cf-dfbe4866881b | checkpoint | 300mm Granular Material
62fe8a47-3387-564c-92c3-659a574a2dac | note | IFC Drawings
ced8b997-2eff-5ccc-bce0-8e2b5dd46985 | note | KDC EES2011
00825d5b-0279-5363-9254-be3ee07e27c2 | note | Check granular layer is minimum of 300 thick. Take photos and measurements
923a7538-16e8-4b46-982f-c12cbc6c38c7 | checkpoint | Gap 40 Basecourse Construction
274fb8e6-0447-5888-8768-f39445922bab | note | IFC Drawings
c789ec65-0c02-5083-a389-4a814e6a24ac | note | KDC EES2011
ff769968-93b8-5f94-b646-5d6b3594a8f3 | note | Visual Inspection
9904891e-6094-5613-bae6-02d32156d581 | note | Clegg hammer reading of >25 recorded onto QF022 Clegg Hammer Test Report
60558203-6883-48f3-b1d2-0dc94f796c3a | section | Close-Out
b8e2bf98-e339-4e4d-9861-9cf797cee585 | checkpoint | Non-Conformance-Reports
d8678374-ca06-5b0e-87b3-e87e30b0637f | note | Non-Conformances Closed Out
4dbf2774-f95c-445e-9911-2773d7d7f8f7 | checkpoint | Handover
de7b20e0-27b0-5779-a9bc-12cf6cfa5df8 | note | At completion of works QA/QC Pack is handed to client
9e9faa7a-803d-5007-9d52-99b6c71222bb | note | Client Verifies Work has been completed correctly and all quality documents are in order
9b42f0b3-df03-4035-ae5b-572231961d30 | signoff | HOLD POINT
de3c1bbb-f660-42cc-9b37-55c300b0e3f3 | checklist | Ω (DEPRECATED) ITP - Inverter Foundations (v0) | itp | Inverter Foundations
59a0ec18-7bed-434b-ac60-312a9296b0b8 | section | Preconstruction
eb2dd0be-505d-4ab5-bd90-96c3113ec6e6 | checkpoint | Design
b56a07fd-73c8-5512-ae0e-8c9dac5ca9bb | note | Issued For Construction Drawings MSF-EN-CIV-DRG-910
00924679-d926-4775-9355-f35bf416ab48 | checkpoint | Survey & Setout
6c2b39c6-98b6-5fcf-9673-cabb6133048d | note | Issued For Construction Drawings MSF-EN-CIV-DRG-910
bc233d78-f462-4e11-9209-e6b744faf3d1 | section | Material Procurement
e05fc5f8-be18-4fe3-8a14-a8a2378c9520 | checkpoint | Structural Steel
74f9c0da-d98e-5aeb-b0e8-d470d62fa7e2 | note | Issued For Construction Drawings
a99459bb-db23-5497-b498-c541fc840107 | note | Manufacturers Documentation
d612e0d8-a21a-5906-88b8-6fc5bc7e9605 | note | Inspection Records
31f6712a-096c-5d2e-9645-aaf1d12e7ac4 | note | All reinforcing bars shall be Grade 300E to AS/NZS 4671 as shown in IFC Drawings NZS3109/3112
987f8e1a-755b-53b7-9cea-ef900e20213b | note | All reinforcing and formwork to comply with IFC drawings
f59d4451-aca6-4d6e-adee-11288440cd46 | checkpoint | Concrete
eaf7c8e9-ac7d-59cd-beb8-63a8e1bd175a | note | Concrete shall be 30MPa Minimum Strength for precast elements
15d1d4b5-d153-4fbb-a6f0-de62af57e92b | section | Construction
bb3f0ea7-3b51-4840-bde2-3afcf9fd6814 | checkpoint | Excavation of Foundation
1a5da599-70e6-56fa-aaf2-b751bfdcb073 | note | Issued for Construction Drawings
5ed13c5d-795f-5d31-8dd3-76a82d0bab11 | note | Remove topsoil back to subgrade material and place in suitable storage location with silt controls
bd95f6a1-d875-565b-92f9-57f297119dbe | note | Foundation excavated to line and level shown in IFC Drawings
4db4c888-08af-5d3d-abc9-09f45ebb345c | note | Scalar Penetrometer test results recorded on Checksheet
e6987a3d-f17a-4f96-aaec-937c56895840 | checkpoint | Compacted Harfill under Inverter Foundations
25bcec1e-dcf3-566c-95ca-1539c52c2e07 | note | Issued for Construction Drawings
e9b8aed0-b631-51e1-9d5f-71bd9b204446 | note | 200x800 Compacted Hardfill Pad under footings
a505b5c4-c886-587d-b2b2-c2477c6cfff2 | note | Results Recorded on Clegg Hammer Checksheet
17794923-7566-4060-ae74-d10c0d99878e | checkpoint | Concrete
37908c62-1c0b-5b94-a290-3e7f71a2de31 | note | Lines, levels and dimension as per Issued for Construction Drawings MSF-EN-CIV-DRG-910
fa3e9e98-aa58-5224-9357-6692c70bde46 | note | Concrete to be min 30MPa at 28 days
921278a0-e6e7-5019-9ffe-592f6d46bb35 | note | Test cylinders taken
9ba80f64-fbd7-590d-b055-10efb88a50cb | note | Dimensions to match IFC Drawings with tolerance of +/- 1mm
c9090453-e3a5-5d85-8f00-69f9783809b6 | note | 50mm minimum cover to steel
a420436d-0276-5475-803a-fde1674bd17c | note | Prepour Inspection Record completed prior to pouring
01c9fc68-9a61-4f34-8739-aefbe53b320f | checkpoint | Placement of Concrete Elements
64749212-9f2e-52c9-bb18-f4e520ce19b9 | note | Lines and levels as per Issued for Construction Drawings
507834a2-6053-51f2-ab4e-82d09c47c000 | note | Use drypack for installation of inverter if required with min thickness of 20mm
4ea374b0-96d4-5dca-8614-eea13a470555 | note | Middle block must be setup for container to sit fully on level and true
3db2480f-eeba-55d6-ba28-8f1655f7f8d7 | note | The outside blocks shall be set lower than the centre block
8ab61453-d374-4b35-a3b3-3f098aeea3e4 | checkpoint | Backfill
a539dd9a-03fe-54c5-96fa-7d3eaf3fc273 | note | Issued for Construction Drawings
aed4fbf8-bbdf-5229-be8b-edaa747d8681 | note | Sand Backfill to be watered and compacted in by mechanical means to provide backfill and support around the foundations without voids or areas of non-compaction
c4099739-fe37-4d18-8b8e-c1086c3591bf | section | Close-Out
f4d99418-1283-4aa3-824d-4f08dd620254 | checkpoint | Asbuilt Recording
b54dfc68-2789-5c6a-a4c8-332b5222cb31 | note | Asuilt records supplied of inverter foundations in place
d3d95e49-335d-4fc9-9e6e-7f6615782a7d | checkpoint | Non-Conformance-Reports
3df03fa2-d666-5eb6-a8f9-27e0ef42f3dd | note | Non-Conformances Closed Out
74b7aa2b-6c09-4428-af8d-938e940f06a7 | checkpoint | Handover
6431aa81-5311-54cd-b718-cdc51e6a5ba9 | note | At completion of works QA/QC Pack is handed to client
c86bdd48-dcc2-530c-95e9-496ba70b9da3 | note | Client Verifies Work has been completed correctly and all quality documents are in order
0167b8f0-2878-41bd-ad24-9def06d3f6c5 | signoff | HOLD POINT
4553f8ca-75ef-457a-b3e7-dca763385291 | checklist | Ω (DEPRECATED) ITP - Laydowns (v0) | itp | Laydowns
be5ca94f-622c-4646-b293-242c1b81e7bf | section | Preconstruction
9d8b0d70-4dfc-481a-9c10-2ce88aabe462 | checkpoint | Design
c628de2f-de23-5213-a5dc-7d90ed6a618b | note | Issued For Construction Drawings
11285c88-5e2c-42ed-87f5-081405efa843 | checkpoint | Survey & Setout
2dc701fc-0576-518e-b33a-c7dd60f9de04 | note | Issued For Construction Drawings
f1fbb0e5-0369-54f1-a9bc-0f1884c738df | note | Agree and Confirm Locations and Areas Onsite
0d9c17d5-da0c-4679-abcd-5490a7773a0e | section | Material Procurement
d05d1f64-48f7-422e-9bfe-c85da59d7fe9 | checkpoint | Granular Fill Material for subgrade improvement (If Required)
f86b0c34-d475-5ebd-8337-a49996dc4e9b | note | Issued For Construction Drawings
20224b78-a6a9-5994-9ff1-c8950e8d2909 | note | Delivery Dockets if Imported Granular Fill from Offsite is Used
3c505003-042e-5453-9d86-67e5dbeffbf5 | note | Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite
660aaeb6-bba2-4b24-8a3a-8ff6b6186fab | checkpoint | Gap 65
7c012d0f-600d-55dd-9e2c-dad2fdd19028 | note | Issued For Construction Drawings
244de326-152d-5ef1-bbe5-99d133aca03f | note | MSF-EN-CIV-DRG-020
89611d25-8b76-50f5-924d-252cf61b8e7a | note | Delivery Dockets
0bc62211-51e3-4df3-9132-ec41c6220232 | section | Construction
928f2289-e3d2-4f6f-ad13-4ea5b8055516 | checkpoint | Inspect Subgrade layer and Check Subgrade Strength
7cdac74e-84c1-5dc4-bd2d-11495d689dde | note | Issued for Construction Drawings
cb9b35fc-e053-538e-b616-bf47fa83ae90 | note | Visual Inspection
c1bbad87-deee-5ca8-8e85-7ac754cb9a80 | note | Scalar Penetrometer with results recorded of No of blows per 100mm on ITC
961df082-a9b5-4d52-8c17-b781abf48ead | checkpoint | Granular Fill Construction As Required
eb0af80b-bf17-5e3e-89ea-393e8fe601ef | note | IFC Drawings
33db383b-1c05-50fa-ae62-f6c36e2df4af | note | Visual Inspection of completed Gap65 after light rolling
6c03afef-6373-4710-b43c-c7b188c8bcea | checkpoint | Gap 65 Construction
8a34dab8-03c3-583d-9399-19327a52ebe0 | note | IFC Drawings
371e5d43-f947-5277-a4e4-529e8d67942d | note | Visual Inspection
378e0697-60d8-5074-b03e-a232020efde8 | note | Proof Rolling
29662279-38cb-4e68-86f1-e4c6ee11a9f8 | signoff | HOLD POINT
ff74ccdd-b836-46af-8b00-f120f5673eae | section | Close-Out
df20b992-26b4-47ea-b87e-d352794f3444 | checkpoint | Non-Conformance-Reports
fa384922-93a6-5ff5-abf8-c8864da4413e | note | Non-Conformances Closed Out
ba7b12c1-c615-40a1-bdfb-aa6be7f39ebb | checkpoint | Handover
b71c06d6-55bc-5800-9e1f-51a20bc9e7e5 | note | At completion of works QA/QC Pack is handed to client
260a3ad6-a6ac-5478-81c4-3a3b9543cfdd | note | Client Verifies Work has been completed correctly and all quality documents are in order
968fda64-b812-4de1-832a-2aac68fa0305 | signoff | HOLD POINT