## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP Masonry - ST-00019 | itp |  |  |  |  | ITP Masonry - ST-00019 Rev1
section | Pre
checkpoint | 1 - Prerequisite quality check
label | Frequency - Prior to commencing each work face
label | Spec/standard - All notes
label | Acceptance Criteria - Check: Starter bar location Grid set out Scabbling surface Reinforcement detailed and supplied to site
label | Measuring Devices - NA
label | Reporting Format - N/A
label | Inspected by: HCL - I
label | Inspected by: SC - W
checkpoint | 2 - Setout hand over
label | Frequency - Prior to commencing each work face
label | Spec/standard - As per set out drwgs
label | Acceptance Criteria - HL to confirm datums and setout marks for each work face
label | Measuring Devices - Physical marks provided onsite
label | Reporting Format - N/A
label | Inspected by: HCL - I
label | Inspected by: SC - W
checkpoint | 3 - LBP details
label | Frequency - Prior to starting
label | Spec/standard - 8.3.1
label | Acceptance Criteria - Accept/ reject
label | Measuring Devices - N/A
label | Reporting Format - Certificate
label | Inspected by: HCL - R
label | Inspected by: SC - SUB
label | Inspected by: Consult - R
checkpoint | 4 - Material certs for masonry units
label | Frequency - Prior to starting
label | Spec/standard - 8.3.3; 8.6.1
label | Acceptance Criteria - 12.5MPa
label | Measuring Devices - N/A
label | Reporting Format - Certificate
label | Inspected by: HCL - R
label | Inspected by: SC - SUB
label | Inspected by: Consult - R
label | Remarks - Hawkins-TSUB- 000164
checkpoint | 5 - Design Mix
label | Frequency - Prior to starting
label | Spec/standard - NZS3404 8.3.4., 8.6.6
label | Acceptance Criteria - 25MPA
label | Measuring Devices - Off site
label | Reporting Format - Design Mix
label | Inspected by: HCL - R
label | Inspected by: SC - SUB
label | Inspected by: Consult - R
checkpoint | 6 - Propsed method of grouting
label | Frequency - Prior to starting
label | Spec/standard - 8.3.1
label | Acceptance Criteria - Accept/ reject
label | Measuring Devices - N/A
label | Reporting Format - Methodology
label | Inspected by: HCL - R
label | Inspected by: SC - SUB
label | Inspected by: Consult - R
section | Onsite
checkpoint | 7 - Reinforcement steel placements
label | Frequency - Daily, Continually throughout laying process
label | Spec/standard - 8.6.7, 8.8.1 table 8.1 NZ4210 As per drwg DP001- MMD-DRW-ST-Z-5050/51 & relevant details
label | Acceptance Criteria - +/-6mm and =/50 / ¼ grouted wall, centred in cell
label | Measuring Devices - Measuring tape/ level
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
label | Remarks - Starter bars, tied reinforcement, ref to engineer if remedial works required
checkpoint | 8 - Laps
label | Frequency - Daily, Continually throughout reinforcement process
label | Spec/standard - As per drwg DP001- MMD-DRW-ST-Z-5050/51 & relevant details NZ3109
label | Acceptance Criteria - 400mm – 1400m depending in the bar
label | Measuring Devices - Measuring tape
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
checkpoint | 9 - Cast in items
label | Frequency - Each elevation prior to pouring
label | Spec/standard - section 6 8.6.6 MMD-DRW-ST-Z-5050/51 & relevant details
label | Measuring Devices - Visual inspection
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
checkpoint | 10 - Blockwork
label | Frequency - Continually throughout laying process
label | Spec/standard - Table 8.2 , 8.8,8.8.2 NZS4210 cl 2.6 MMD-DRW-ST-Z-5050/51 & relevant details
label | Acceptance Criteria - As per table bottom course20mm ma and typical course 10 +/3mm
label | Measuring Devices - Measuring tape/ level
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
checkpoint | 11 - Block clearances
label | Frequency - Non strucuturual blocks and structural elements
label | Spec/standard - MMD-DRW-ST-Z-5050/51 & relevant details section 5
label | Acceptance Criteria - 25 -200mm
label | Measuring Devices - Measuring tape/ rotating level
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
checkpoint | 12 - Joints
label | Frequency - Continually throughout laying process
label | Spec/standard - MMD-DRW-ST-Z-5050/51 & relevant details section 1 or as specifies
label | Acceptance Criteria - Every 6m or as per drwg or change in wall height, thickness or amove/below movement joints
label | Measuring Devices - Measuring tape/ level
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - S
label | Remarks - 4 hour fire walls to have intumescent jointing sealent
checkpoint | 13 - Cleaning Out
label | Frequency - Each vertical bar
label | Spec/standard - 8.8.3 NZS4210 sec 2.8
label | Acceptance Criteria - 100 x 75 mm opening
label | Reporting Format - QC checklist
label | Inspected by: HCL - R
label | Inspected by: SC - Sub
label | Inspected by: Consult - R
checkpoint | 14 - Grout testing
label | Frequency - Each pour
label | Spec/standard - NZS 4210 App 2A, NZS3112,2 8.3.4
label | Acceptance Criteria - 25MPA at 28 days
label | Measuring Devices - Off site
label | Reporting Format - Report & Drwg
label | Inspected by: HCL - R
label | Inspected by: SC - Sub
label | Inspected by: Consult - R
checkpoint | 15 - Protection of blocks
label | Frequency - If temperature is extreme
label | Spec/standard - 8.8.2 NZS 4210 2.18/19
label | Acceptance Criteria - Less than 5 more than 25
label | Reporting Format - QC checklist
label | Inspected by: HCL - M
label | Inspected by: Consult - R