## Table 1
Ill' Item I | ConnructJon Actllllty or Material Element | Standard, Drawln& or Speclncation Reference | Con,tructJon Activity Dcwlptlon,TertType and Acceptance Criteria |  |  |  | QA Record
1 1.1 | PRELIMINARY & GENERAL
Method Statement & JSEA Completed & signed b relevant authority
| Method Statl!ment Oe11elopment & Safety Analy•I• | The Downer Standards [TDS) | Prior to con1tructlon: document re11lew. • |  | Once
| Confirmation of superstructure position. | Signed ITP | Signed ITP required for the position of the supe tructure before grouting. |  | Once |  | Signed ITP
1.2
2 | MATERIAL APPROVALS
2.1 | Non Shrink Grout Approval | 323SS99-SP03·ST·3200• PROPOSED ACCESS RAMP· EXISTING PIER 1 DETAILS , 323S599-SP03·ST·3201• PROPOSED ACCESS RAMP· EXISTING PIER 2 DETAILS 3235599·SP03·ST·3202• PROPOSED ACCESS RAMP· EXISTING PIER 2 DETAILS 3235599·SP03-ST·3250• PROPOSED ACCESS RAMP­ ABUTMENT DETAILS- SHEETl 3235599·SP03·ST·32S2· PROPOSED ACCESS RAMP· ABUTMENT BEARING App 1C. 746-24-847-AC - Tc,ch Spec·Geo&Strut Spc<: • C0602.10.04 | Non shrink crout - slka 212 HP to be submitted to defolcner for ravlc,w :ind approval as It obtain,85 Mpaafter 28 Days> 50 Mpa as per 32S2• Note 1,4 |  | Onco, |  | MOS, In Eight Ref
2.2 | Glass Plate Trial |  | As per 3235599-SPOJ-ST-3252 - PROPOSED ACCESS RAMP-ABUTMENT BEARING· Note 1.4. Glass Plate trial to be undert.iken to rc,pllcatc bearing pad footprint of 230mm x |  | Once |  | Site Observation Report Wrlttl!n acceptance of material followlng trlal.
3235599·SP03·ST·32S2 • PROPOSED ACCESS RAMP· 230mm x 20mm. Area ls to be poured prior to lnst.1llatlon of bearing grout to confirm ABUTMENT BEARlf'jG · Note, voiding ts lefos than 10%of area. Undc,rtaken with MSQA observations Methodology to beiubmltted prior to commencement.
2.3 | Curing Method | According to MOS shc,o,t lor Slka 212 HP, See bdow, grout to be seal«!d with timber shutter, left to cure within small shutter and them tro,ated with Slka Anti Sol as per data I sheet attached.. CURING TREATMENT Formwork should be left In place for at least S days if App lC • 746·24·847-AC • Tech Spec·Geo&Struc possible, to prevent moisture evaporation and provide Once restraint to early :igc h.irdcncd cxp:lnston. Once fom,­ work Is removed a suitable curing membrane such a Sika Antisor• should be applied to any exposed faces. Refer to scp:irate data sheet for further lnform:itlon r |  |  |  |  | MDI Phot\
3 | CONSTRUCTION ACTIVITIES
3.1 | Con,truct/on Joint • | 323SS99-SP03-ST-3252 • PROPOSED ACCESS RAMP­ ABUTMENT BEARING | Formation of con•tructJon Joint required on top of pier/ abutment lo !he construction Joint mu,t bevisible. | Once |  | Photo, ,
3.2 | Groutlnc Pro-Pour ln,pectlon | 323S599-SP03-ST-3202 • PROPOSED ACCESS RAMP- EXISTING PIER 2 DITAILS App lC • 746-24-847-AC· Tech Spec·Geo& Struc | No relnforclnn requirements. Chock to onsure that!he ,urface Isprepped, under.Ide of bearlnc pod I•In correct location prior to pourlnn. Nominal 20mm willbe poured. •' | • Each Structura |  | MSClASVR Pre-Pour Chockiln Photos
3.3 | Groutlns Pour | 3235599-SPOJ-ST-3252• PROPOSED ACCESS RAMP­ ABUTMENT BEARING NS3109 ASlOU Spec- C0602.10.04 | Concrete to be poured•• permanufacturer. recommendations whore 3.7 lltre• per bog. S..mple• to be taken from each batch uslnc steel mould• whore l, 2, 3, S. 14 and 28doy te,ts•re to be taken to en•uro that wout has reached nece•""rvstrength MlXING Place about 70-80 %of the premeasured clean water (depending on consistency required- refer toMix Ratio") into a clean container and gradually add the whole bag of SlkaGrou -212 HP Into It while continu­ ously mixing. Add the remaining water until the de• sired consistency Isobtained. M1x for 3-5 minutes witha low speed drill (500 rpm max.). Allow to stand so.iny entrapped .ilr can escape. Donot add more wa• ter to Increase flow of the grout If amixhas stiffened due to time delays, If the grout isunworkable discard. | Once |  | Photos Test Report for Compreulvo Strength
3.4 | Po,t Pour lnopectfon | App lC • 746-24-847-AC-Tech pee•Geo&Struc 32JSS99-SP03-ST-3003 NZS3114 | Joint lnopectlon bo undertaken with deslcnor to ln,poct ,huttors of •tructure followInc removal of ,hutten.and ,urvey/ chock dimension of structure hove achieved stlpulated tolerance, stated In drawlnll suite and NZS3109 | Once |  | Vlsuol ln,pectlon Photo,
4 | FINAL RECORDS
4.1 | AJ•Bulit | N/A | ln,talled •• per d••lnndrowfn . Allcompllanco recorded CAO file• | Once |  | As•Bullt
4.2 | Non·-conrormance.s | ON1212·00W-PLA-PM-OOOS QMP | Non-conformance, reports to be raised when speclflc.itlon not met.All non-conformances within !he area under review need to be listed on the NCR report. NCR Reference | Each NCR |  | NCR forms on ln£1ght