## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP047 - ALER 3 HV Installation | itp |  |  |  |  | FH-ZU2-QU-ITP047 - ALER 3 HV Installation - Rev 0
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | — using the correct and complete set of drawings.
label | — all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.3 - Survey Checks
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the panels.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed Survey Report
label | HP*
label | Responsibility - Project Engineer / Site Engineer / Surveyor
date | Date Completed:
checkpoint | 1.4 - Submission & approval of shop drawings
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - HOLD POINT
label | ○ Submit shop drawings to the principal’s representative for approval prior to fabrication commencement.
label | ○ Items to include but not limited to:
label | — HV Kiosk
label | — ATS
label | — DB-GEN
label | — 400 KW Load Bank
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Material Submissions
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - HOLD POINT
label | ○ Items to include but not limited to:
label | — Bonding Conductors
label | — Copper Conductor Connections
label | — Earth Backfill Slurry Mixture
label | — Earth Rod Inspection Box
label | — Grid Conductor
label | — Permanent Earth Cable Elbow Connection
label | — Sub 164 Retention Barrier
label | — V90 PVC Insulated Un-stranded Class 2 Copper Conductor
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS/NZS 1252.2
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Temporary Works
label | Frequency - Prior to commencin g activity
label | Acceptance Criteria - Submission and approval of the following documentation based on the Temporary Works Design Process Matrix.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
label | HP*
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 1.7 - Off-site Inspections
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Inspection and attendance on site for Factory Acceptance Testing for:
label | — HV Kiosk
label | — ATS
label | — DB-GEN
label | ○ Following these inspections FAT testing shall be submitted and associated certificates.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Factory Acceptance Tests
label | WP TP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
section | 2.0 - Construction
checkpoint | 2.1 - Delivery of Materials to site
label | Frequency - Each item
label | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
label | ○ Identify any damage/defects prior to unloading of the material.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Materials Inspection Checklist on ConQA
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.2 - Inspection of installed Pits, Conduits, Slabs and Structure
label | Frequency - Each Lot
label | Acceptance Criteria - HV contractor to inspect the builder’s installation to confirm suitability and as per design
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.3 - Isolation of existing cables
label | Frequency - Each Lot
label | Acceptance Criteria - Cable to be isolated and earthed at both ends. Ensure correct cable is being isolated as per information on hand. Check Isolation by testing at a suitable point.
label | ○ HV cable to be disconnected and taken out of cable compartment.
label | ○ Existing HV Cables shall have Seath IR testing completed prior to modification to the cable to provide a baseline final testing as per MAS- ELC-002
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Test results. Nilsen ITC
label | IP / TP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.4 - Cabling – Mains, Submains & Earthing
label | Frequency - Each Lot
label | Acceptance Criteria - New cables to be pulled through pre-laid conduits using the provided pull strings.
label | ○ Cables to be sufficiently secured out of the way prior to component installation.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Nilsen ITC
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.5 - Lifting Preparation (Kiosk)
label | Frequency - Each Lot
label | Acceptance Criteria - Lift Study available and approved.
label | ○ Temporary Works for Crane Pad approved and constructed.
label | ○ Complete Pre-Lift/s Commencement Checklist prior to each component being lifted.
label | ○ Ensure relevant drawings, lifting & fixing plans available to the crew.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings Lifting Plan
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - Pre-Lift/s Commencement Checklist, This ITP Signed
label | IP, SCP
label | Responsibility - Site Engineer / Foreman / Surveyor
date | Date Completed:
checkpoint | 2.6 - Component Placement (Kiosk)
label | Frequency - Each Lot
label | Acceptance Criteria - Survey to confirm component placement as per the design.
label | ○ Install all fixings as per the drawings & engineers plan and suppliers’ specification.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings Lifting Plan
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP / SCP
label | Responsibility - Project Engineer / Site Engineer / Surveyor
date | Date Completed:
checkpoint | 2.7 - Installation of Earthing Grid
label | Frequency - Each Lot
label | Acceptance Criteria - Installation of Earth Grid as defined by IFC Drawings and MAS-ELC- 002 (Section 5.7.3).
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS/NZS 3000
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Nilsen ITC
label | WP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.8 - Earthing Grid Testing
label | Frequency - Each Lot
label | Acceptance Criteria - Earthing system to be tested as per MAS-ELC-002 HV Standard – Appendix B, including:
label | — Continuity testing (earthing and bonding conductors)
label | — Earth resistivity testing
label | — Earth potential rise measurement
label | — Current distribution measurement
label | — Transfer voltage testing
label | — Touch voltage testing
label | — Step voltage testing
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings AS 2067, MAS-ELEC-002
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP is signed Test results
label | WP IP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
checkpoint | 2.9 - HV Cable Terminations
label | Frequency - Each Lot
label | Acceptance Criteria - Relevant cabling can be installed into allocated cubicle. Terminate HV cables in the final position.
label | ○ Confirm cables are installed into correct cubicles.
label | ○ Confirm earth ring cables terminated to relevant earth bar/position.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings, HV Access Permit
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Test results, HV Access Permit, Nilsen ITC
label | WP TP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
checkpoint | 2.10 - Testing of New HV Cables (Before Energized)
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Confirm the following items are constructed in accordance with IFC design and specification.
label | — Type, size, colour, quantities, location
label | — Secure
label | ○ Verify and confirm the following tests as per AS/NZS 3000 (not limited to):
label | — Polarity Check
label | — Cable Loop Resistance (Ohms)
label | — Insulation Resistance (Core-Core& Core to Earth)
label | ○ Ensure HV cable connected are bolted up at both termination ends. Testing to include all testing required as per MAS-ELC-002, including VLF testing etc
label | ○ Ensure new earth cable connected and torqued at both ends. Upload and testing of protection settings into HV and LV CBs. Testing of SCADA Points to EMCS.
label | Reference Documents - ZULU-BECA-001- SPC-00005 Drawings, HV Access Permit, AS/NZS 3000 MAS-ELC-002
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Test results, HV Access Permit Nilsen ITC
label | WP TP
label | Responsibility - Project Engineer / Site Engineer / Principals Representative
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: