## Sheet1
/1 | checklist | Installation of FSMH | itp
| section | SECTION 3 - RECEIVING INSPECTIONS | itp
| checkpoint | 3.1 - Material Delivery | itp
306c0cad-f080-5f4a-8125-bc0a08f3554b | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications | itp
5e5e9327-26c9-59f7-a0c4-99b8a67431c4 | note | Acceptance Criteria - Items are approved as per contract specification | itp
64b73fde-4c6b-5dd9-bf71-c782eac57bc2 | note | ○ DCC approved | itp
9c04f967-2974-5f90-b62d-1ea3b2dfa74c | note | Verifying Document - Photos, delivery docket | itp
5ae2f52f-cf55-51e5-9ce9-595d53c893ba | note | Frequency - On Delivery | itp
1ff3afcb-8a71-5ff8-8164-44363543c4cd | note | Inspection Type (Visual, other) - Visual | itp
d5560565-7f1f-50d6-92ec-1b0164d0f3d9 | note | Inspection: Key - C | itp
28f1a379-17f5-55bd-94fa-db9f689ee862 | note | Inspection: By (Role Key) - SP/QE | itp
| checkpoint | 3.2 - Set out | itp
634560bd-2d69-5708-846d-83e4824de234 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment | itp
36af7152-0ebc-54aa-9fff-72c3aed35f65 | note | Acceptance Criteria - Allignment set out matches drawing C4400 or aggreed with the Engineer | itp
536e8ebd-9bc6-5f46-aea4-f58bff2e201f | note | Verifying Document - Survey marks, photos | itp
210f9cfa-cdb2-55d0-997c-d217bb5208aa | note | Frequency - Prior to commencement of works | itp
f173228a-2625-5da9-8dc3-0f4fe40a5c96 | note | Inspection Type (Visual, other) - Survey | itp
d4dd6ac5-9fe5-5ef8-a262-2019cd8785cc | note | Inspection: Key - H | itp
3489559f-2cce-5044-ac1d-68336808ea4c | note | Inspection: By (Role Key) - SV/SP/QE | itp
| signoff | HOLD POINT | itp
| checkpoint | 3.3 - Backfill / Bedding Material | itp
7d95440b-01a4-5e4c-8197-de8bbd98e036 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329. | itp
8976d22d-ab0c-5693-bc0a-d9731cd1c680 | note | Acceptance Criteria - As per DCC code of subdiviison 10329 | itp
3aaa88cc-82cb-5438-b429-bbe50ab25bce | note | Verifying Document - Delivery dockets, photos | itp
da20e9a3-da29-5395-924b-b0a749585fa1 | note | Frequency - On Delivery | itp
15be0528-629c-5f25-bc78-2861d180a933 | note | Inspection Type (Visual, other) - Visual | itp
dbce0e37-a39c-58db-9199-89fb0acd70c5 | note | Inspection: Key - C | itp
0a7fed2c-e9e2-566d-bcdd-6eee1bd88e1f | note | Inspection: By (Role Key) - SP/QE | itp
| section | SECTION 4 - IN-PROCESS INSPECTIONS | itp
| checkpoint | 4.1 - Trench Excavation | itp
13443767-b171-52bb-9b22-bd26e7ed259f | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4400 | itp
ad0181d3-28d9-5570-98a6-0d95f6e8e56c | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe | itp
4d541dba-2310-534f-991b-bb46d777fdb3 | note | ○ Floor of Trench to be even across width and length | itp
b3273e85-f3a5-5135-848a-f9eccb508a4f | note | Acceptance Criteria - As per 561467-TW-04-DRW-02 | itp
0ab334c8-7193-5835-8747-29e28b6275ce | note | Verifying Document - Photos, measurement checks | itp
f085aa79-2a42-57ae-9a27-e886937a35bf | note | Frequency - During Installation | itp
df162fd0-006e-58a2-8d74-19c37c03037c | note | Inspection Type (Visual, other) - Visual | itp
696eaf74-89b8-5bc2-8526-6312d48fc711 | note | Inspection: Key - V | itp
4fc783ba-64f4-56bc-bb18-f18dc704004e | note | Inspection: By (Role Key) - SP/QE | itp
| checkpoint | 4.2 - Foundation | itp
f6777232-5b7b-5e2d-8491-8fbe2d80d2c1 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench | itp
0c0f24e6-4d36-56f1-8819-85d1e0140505 | note | Acceptance Criteria - Minimum of 2 blows per 100mm | itp
e1f3da71-b730-5e29-8117-8c70b079c7d8 | note | Verifying Document - Test results | itp
49bdc67e-ab4f-5eb7-90fc-6ad8de95fc69 | note | Frequency - During installation, per 20m | itp
d19e9046-4dcf-5b07-a0a5-7f421d037602 | note | Inspection Type (Visual, other) - Visual, On site test | itp
1e37798f-bf41-58d2-9cdd-f54902bea504 | note | Inspection: Key - H | itp
3d0248ad-d4c1-528c-a2e8-7c12a761c22c | note | Inspection: By (Role Key) - SP/QE | itp
| signoff | HOLD POINT | itp
| checkpoint | 4.3 - Bedding | itp
c9d10ab0-acb0-5f97-bd7f-f97d7ca9a448 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material | itp
082d6c91-7e63-548e-a219-6421e0150690 | note | Acceptance Criteria - Bedding to comply with requirements | itp
a4d1cd79-c590-55d1-9c74-b49b624a8f63 | note | Verifying Document - Photo | itp
91821764-9bc8-5643-a7ba-9b166aeed9e9 | note | Frequency - During installation | itp
52b29eea-0222-5f98-b5f6-140ee01632b0 | note | Inspection Type (Visual, other) - Visual, Measurement Check | itp
3beafa43-a480-5e66-9f66-3762362904d0 | note | Inspection: Key - C | itp
9ed966d4-c1d6-5720-bbcc-2acd909bd7e9 | note | Inspection: By (Role Key) - QE/SP | itp
| checkpoint | 4.4 - MH Installation | itp
1a71b3f4-87ff-5889-8dc7-5fbbc4810e6d | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level | itp
517f37f2-80ad-56ca-8279-3debc8ff5fbb | note | Acceptance Criteria - Final levels are in accordance with the C4400 or within tolerance and agreed with the Engineer | itp
bedb719e-fd92-5c4f-962a-cdc24008f4f8 | note | Verifying Document - Photos, As-built | itp
38547d56-e31a-5647-ab1d-05a003ba8501 | note | Frequency - During installation | itp
51beda81-7f79-5608-a8f8-bafffa0b86ee | note | Inspection Type (Visual, other) - Survey | itp
59618335-5b2b-5d04-8b6e-117819aee945 | note | Inspection: Key - H | itp
81f1c5e4-c3e9-53a3-b559-9b502929dd54 | note | Inspection: By (Role Key) - SP/QE | itp
| signoff | HOLD POINT | itp
| checkpoint | 4.5 - Benching | itp
b3219cf7-d612-574b-971d-53e13f88b152 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days. | itp
2dba3673-76bc-5e74-ba92-c79e40b173e3 | note | ○ Benching shape to have smooth transitions at bends and junctions | itp
f94713f1-7653-5a86-aff6-00f68488e81a | note | Acceptance Criteria - Benching built up to the specifications | itp
a15c7bdc-75ff-5482-88c8-28918969046e | note | Verifying Document - Photos | itp
701a26fc-74d5-58c5-80c3-68d493129a9e | note | Frequency - During benching contruction | itp
78af94fa-ff65-556d-9996-995449ae6c45 | note | Inspection Type (Visual, other) - Visual, Test Results | itp
beca31e4-8016-555e-a78d-9d83c98d9a9f | note | Inspection: Key - H | itp
935600ea-3c11-5abf-9089-a67f9fac0cc3 | note | Inspection: By (Role Key) - SP/QE | itp
| signoff | HOLD POINT | itp
| checkpoint | 4.6 - Backfill and Compact | itp
434b4f16-15f1-5e7c-8dc1-58874eb8ef09 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material | itp
c0bc7eda-6fc4-54ea-aa2d-88dc4577719b | note | ○ Compaction testing one test every two layers as required | itp
f807d6cf-c23d-589b-a263-63eeefcc169e | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements | itp
a83baf94-efe2-52e7-9fa3-6f237ee77588 | note | Verifying Document - Photos, Compaction test results | itp
12fec790-3c6b-562e-a35d-89a3dba9f20a | note | Frequency - During Installation | itp
76534213-d26e-5cad-830d-4f9797e48734 | note | Inspection Type (Visual, other) - Visual, On Site test | itp
1d68ec6b-9664-573d-bab2-ff657674e3c1 | note | Inspection: Key - H | itp
c1380e7b-92fc-555b-8249-479f03d650aa | note | Inspection: By (Role Key) - SP/QE | itp
| signoff | HOLD POINT | itp
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER | itp
| checkpoint | 5.1 - Leak Testing | itp
be47134a-6f1d-59c6-b01a-d0e0a9bdf53d | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level. | itp
c8643ad4-11cf-5808-bd3c-3a319ba82fb0 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period | itp
87972f92-4cab-5704-8c7f-57694c7a1128 | note | Verifying Document - Photos, test records | itp
2b8183b0-bde2-5942-b524-973de5852f1e | note | Frequency - For every manhole | itp
b64c4dcb-02c8-5000-a126-7d418f191efd | note | Inspection Type (Visual, other) - Test, visual | itp
edc6ade1-3864-54ae-aa53-2f459b36d81c | note | Inspection: Key - H | itp
d19dd388-ac1e-52c8-9b3f-a26a6cf52c7c | note | Inspection: By (Role Key) - SP/QE/CM/CR | itp
| signoff | HOLD POINT | itp
| checkpoint | 5.2 - Red pen markups | itp
d9233c77-7620-509c-8c4f-1f065171d6de | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings | itp
872447f6-1d4d-5ee4-8faa-18daf6729fdd | note | Acceptance Criteria - Signed ITP | itp
54a0857b-d6bc-5c16-93a8-19b5a3bcfc0a | note | Verifying Document - Red pen markup drawings | itp
e8f25ae1-573f-5de9-9e24-2d614e57d495 | note | Frequency - After installation of FSMH | itp
4a407ac5-1fbf-59df-8133-d74aa41d0afe | note | Inspection Type (Visual, other) - Document | itp
4995ff0f-38f6-54d0-b90a-c90a2e1f44a2 | note | Inspection: Key - H | itp
703d6adf-1136-569e-93bc-253dc285dbad | note | Inspection: By (Role Key) - SP/QE/CM | itp
| signoff | HOLD POINT | itp
itp
/1 | checklist | Installation of PVC FS Pipe - 150 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
61b5bdd8-3580-529d-bbe4-cfc6006e6666 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
219f6f39-e8b8-5f98-891e-d10fa24e67fc | note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
e71eddb9-520e-5749-b769-ce64bbb63db0 | note | ○ Items are approved as per contract specification
3eb04f50-2b38-5061-9a7b-03e1c6873f1e | note | ○ DCC approved
2336e534-66be-574e-b84c-e4fc229f669e | note | Verifying Document - Photos, delivery docket,
853e3f7f-7d21-58bb-8fdb-ec5c5093cf7b | note | Frequency - On Delivery
3e4d05af-f863-58ed-b509-5bb7aa8f5ab1 | note | Inspection Type (Visual, other) - Visual
e7518008-9018-5ca0-ab26-0f93321d8f0a | note | Inspection: Key - C
c6e7f05c-7da1-54db-ae6c-20911f1efc41 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
daf482b9-51b1-5c27-aff1-e81efd5ee6e9 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
0ca88955-0ef6-507a-a4f2-c1404e6f50ae | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
c0e14c1f-d06a-5c08-85e2-8ac7710ba6f8 | note | Verifying Document - Survey marks, photos
87a64616-68ea-5c81-8b89-07812677e106 | note | Frequency - Prior to commencement of works
2fecf6aa-4788-59b8-8547-e6d7f95b7c4b | note | Inspection Type (Visual, other) - Survey
561f1e6c-da2b-5695-a0e3-6a63decfb391 | note | Inspection: Key - H
f4025978-9c32-52c5-8a33-d864e7b3ced3 | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
536071d2-a4e8-52fa-8cdb-bc6b3e7d8736 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
0b3caadc-e9e1-5cfb-ad86-55af3445bafc | note | Acceptance Criteria - As per DCC code of subdiviison 10324
d68e61f2-bd4d-5b47-a2cf-2c8cc2814268 | note | Verifying Document - Delivery dockets, photos
62e62dae-474f-5cae-8604-92334547a76e | note | Frequency - On Delivery
0ad7fc0c-dcaa-5ec0-8feb-628c1ca89684 | note | Inspection Type (Visual, other) - Visual
21f12d96-e038-5544-a4ef-db9cd03b41f3 | note | Inspection: Key - C
5dd358a7-6380-50e2-b1e8-d44aedda26b3 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
9bc9463a-c701-5972-89e4-35bcfa56ffec | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4400
b64c979f-113f-58cd-84d9-09c4ff38ff48 | note | ○ Floor of trench to be even across width and length
3be77e07-51e4-5eb8-a233-b64da0fce4ae | note | Acceptance Criteria - Allow 100mm for bedding
773af6dc-dadd-5664-8746-be490f977080 | note | Verifying Document - Photos, measurement checks
92c61c43-eefd-5353-a8f2-50be6df188d3 | note | Frequency - During Installation
36ed8a86-e322-5de8-a3c1-6993a12290c3 | note | Inspection Type (Visual, other) - Visual
e5d9e884-e177-5dd0-bb11-db4b05965f46 | note | Inspection: Key - C
095c1330-360f-5aaa-ace9-8577541982b5 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
6da1e4a9-4917-57ee-af7f-34a8119c8a0a | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
fa08b9fc-08ff-5f53-a0da-718759cb48cf | note | Acceptance Criteria - minimum of 2 blows per 100mm
afeac26a-84cc-5a82-bc62-11a6a103cae6 | note | Verifying Document - Test results
ee20234f-619d-50ac-a155-e478077fcb47 | note | Frequency - During installation, per 20m
b480bf64-3da6-599a-8e6c-65a6283f99b3 | note | Inspection Type (Visual, other) - On site test
d3d48e5d-fe80-5c5f-be3d-824b6cdc46dc | note | Inspection: Key - H
b60551c7-02f7-586b-abf6-dfe1816a41a9 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
7546c15a-f4ff-5af4-8f1f-afcf14c89e50 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4400
e309f1ee-1a7f-522a-ac15-969c9eb59fab | note | Acceptance Criteria - Pipe not damaged during installation
ea2ac12a-61b7-5f37-9489-a21fbc595de4 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
ebe9206b-d043-5b4a-8df4-49154adb37af | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
99367f9d-d541-5ab6-88fd-37a151eccbd3 | note | Frequency - During installation
b0df8a58-fd24-5bb0-9b6e-bece5a78b21d | note | Inspection Type (Visual, other) - Visual, Survey
bedc309c-7732-5ca9-a2a3-47ec6d4cc1c7 | note | Inspection: Key - C
3e8b8b45-99e4-5e6b-b69d-79ea3817acd0 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
67901df4-d56d-559b-8e7d-5f878c9edf18 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4410
601c17c1-0ea4-5ba4-bdc3-5c9ef8eeed0a | note | Acceptance Criteria - – Lateral connection as per drawing C4410 and DCC standard details and project specs.
2f8e3755-0e10-5fcd-8571-7d3597df42f7 | note | Verifying Document - Photos, measurement checks
de5270c0-4716-531c-b396-11aa12e44d2b | note | Frequency - Every Lateral
a52d0961-fe8d-5e1e-857b-85a3e1c486b1 | note | Inspection Type (Visual, other) - Visual, Survey
146b6d1f-44d2-55dd-a090-a58ebeb296cc | note | Inspection: Key - C
dfebeeba-79c1-5450-a9b6-ffbb20506263 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
724d5bfd-1af8-528a-8193-eb723af36fce | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
c68d70dc-4f9a-50ae-8be3-0fd8f612412b | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
6e449d16-8127-56bf-982a-819e07e9a932 | note | Acceptance Criteria - min 100mm bedding
98aa8e3a-749a-5870-a2ae-e489ff2909ef | note | ○ 100mm overlay
6e130b15-4df7-5ba1-b641-708b1ae47c1f | note | Verifying Document - Photos
66bd14d5-c8f5-5750-adeb-11f4126cb161 | note | Frequency - During Installation
57840eb0-10b6-560c-bcca-12d653135aac | note | Inspection Type (Visual, other) - Visual, measurement check
08a782e4-0077-505b-88f1-523e2e1bdc16 | note | Inspection: Key - C
3fbeea8b-3b24-5991-9bc9-cba304e59a8a | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
28d3f21f-b7cc-5217-a1cb-2a31c14da285 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
7a49152c-59b9-5cab-ad98-fbfd41ac2bb6 | note | ○ Compaction testing one test every two layers as required
d0f0475f-2592-5b41-886a-c48a7f9e7baa | note | ○ Conductive signal strip to be laid at 300mm above pipe
74c7e632-39a2-5b72-a5e2-6c326321be48 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1628e93a-9dac-5928-b69b-c977a3c85ff3 | note | Verifying Document - Photos, Compaction test results
fd86da26-7bf4-5c3a-9451-55f7e2c484aa | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
a44531c6-7130-5caf-88fc-bff9861f75b4 | note | Inspection Type (Visual, other) - Visual, On Site test
4df90d97-80c7-55a3-95ab-3e8c43888f69 | note | Inspection: Key - H
1fbf6dae-4225-59fa-bbb1-95d4acd32440 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
4e7fdd51-c846-5cb3-8c93-46d78f7d8d3d | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
a41d7e65-bba7-5aea-bb5e-6cd6a13fac9c | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
fbcf4ffb-c0f4-5037-ab3b-001955233374 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
a31bc53d-5856-550f-af01-8072c2852630 | note | ○ Dips or ponding of water inside the pipe
3dd50374-105f-5b4a-9181-2915ac4e0d5b | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
e6a9df16-54f0-5cba-90ba-1eb928c3c4e1 | note | Verifying Document - Test Records, CCTV footage
b9c169a8-9e00-52eb-82e1-98cec35ae8cd | note | Frequency - Every section of pipe completed
0b784ad0-5cfc-5e50-b86c-ae20ae220195 | note | Inspection Type (Visual, other) - On-Site Test
321f3b08-95df-5e61-93f9-59fac32fc4fe | note | Inspection: Key - H
3a0a155a-0e6f-525d-add4-60208cd74388 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
a2cfe721-c303-515a-b61a-2730155bdf88 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
c8975b3a-64f0-50b0-93d9-3cbe0119d76c | note | Acceptance Criteria - Engineer Approval
74d1867c-b65b-5697-81d5-d00fa45c02fa | note | Verifying Document - Test Records
c0b0eeee-8795-5553-b3d0-e7aeb6aca8df | note | Frequency - Every section of pipe installed
397f7f31-99a1-5724-b9d2-12cd0ce72898 | note | Inspection Type (Visual, other) - On-Site Test
5ee889a0-053e-551d-b062-ac7e6f3addb8 | note | Inspection: Key - H
c2914af3-e5e7-5f51-9cf1-83f0c7e6da8a | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
c72817ba-6585-5485-8a04-c4aba61e66c8 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
2edebed3-9482-5f47-b389-c54c79f596e2 | note | Acceptance Criteria - Signed ITP
03e79f7d-a9d0-54e9-a25c-90c51e416c53 | note | Verifying Document - Red pen markup drawings
b02ea6fa-f6e1-5031-ade1-9256555b5511 | note | Frequency - After completion of pipe section
89773843-6247-5ff0-9b05-7b7b9bb86993 | note | Inspection Type (Visual, other) - Document
c2106e0a-964c-5e1f-b19e-d1b42d22aadc | note | Inspection: Key - H
5d05a49b-2bd1-5213-9902-a888b9671978 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of PVC SW pipe - 300 zone 5 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
13b74c26-053a-5c39-a586-797f1635c254 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
9284b471-55b6-55de-ac70-2c82ec79bbb0 | note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
84acdc02-e0bb-5491-8dc8-fbe19d9a4207 | note | ○ Items are approved as per contract specification
ceff9359-d81d-546c-97b9-9146c1fbe68f | note | ○ DCC approved
ee4a1268-a257-5491-90d7-27b0c6097961 | note | Verifying Document - Photos, delivery docket,
3ddce36d-5a72-5e71-a9d2-d12d0b5ab0c4 | note | Frequency - On Delivery
646390fd-b681-50f9-bb3c-04063fc27c27 | note | Inspection Type (Visual, other) - Visual
12a1fa5d-0f59-5ef7-a175-eb085b31eae2 | note | Inspection: Key - C
96f84a6f-af0d-509d-89a1-c3a6bb8023c9 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
9bbac671-99d6-5b75-8cc5-57bb6a6203e1 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
90828ae5-9932-5e27-b691-ebd484f2fa30 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
886e4424-41a8-58b2-b90e-f409a49c6617 | note | Verifying Document - Survey marks, photos
421dc5d8-9a75-5422-89a7-1b6f7fba1c1f | note | Frequency - Prior to commencement of works
382706af-0939-5c33-be0b-5a0c6f5d0928 | note | Inspection Type (Visual, other) - Survey
50fb44c8-9d6b-5e3a-a00f-76cb8e505fb8 | note | Inspection: Key - H
a0aa9287-65a0-52b3-84f7-2c56fba7812c | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
f61898e8-e94c-5e3f-b0a8-e0d7120ebc28 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
d2c50cdc-945f-5b34-9dd4-4704219f3052 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
e5a6b4fe-e74d-5588-b5c5-043a1286eb7c | note | Verifying Document - Delivery dockets, photos
e7916375-f798-5fe7-a75d-e6fb4e348f10 | note | Frequency - On Delivery
0b88f83b-5f49-58e9-940a-8ccc0d676686 | note | Inspection Type (Visual, other) - Visual
11a53bf7-7b09-5755-8f10-63c189645560 | note | Inspection: Key - C
1355b01f-5a09-57e6-aa3d-d3d4491f2c27 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
955cd150-f299-5fc2-a187-dd4fc38002ae | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4300
0574bc8d-5024-520d-92fb-c48cf809237a | note | ○ Floor of trench to be even across width and length
37cd7643-d2c7-57fc-aaf6-563cc9c8c266 | note | Acceptance Criteria - As per 561467-TW-04-DRW-02
77a36b85-b9cf-5f94-a60c-4ad6588d756b | note | Verifying Document - Photos, measurement checks
5bfbd410-8a7c-567f-bc85-1b7af0fd51ff | note | Frequency - During Installation
fea66bfa-3997-5fc5-ba7a-df3b67dfc732 | note | Inspection Type (Visual, other) - Visual
6b65a327-1b89-5f76-8f5e-875105628501 | note | Inspection: Key - V
74835963-98f2-5442-b26d-f0809b23c391 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
af8ff430-9933-5231-b7d7-1d95304c0e84 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
a1f8f8f1-7818-5fe0-a5f5-098096b284ce | note | Acceptance Criteria - minimum of 2 blows per 100mm
1492de43-6e99-5185-91f4-32afd4d5532f | note | Verifying Document - Test results
b3082378-39b5-52ca-aea9-15679cc8fcb6 | note | Frequency - During installation, per 20m
90719ac5-625e-5a85-aa4e-98bf5cb52d48 | note | Inspection Type (Visual, other) - On site test
fc78897b-d0b9-5093-8725-5ddd0b035c0a | note | Inspection: Key - H
0756547f-733e-566c-b801-33b9ab940887 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
b7c3f0b6-80d4-5804-8039-b1d423f77516 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4300
71ff12d6-4cf3-5b6f-b0ab-f56350c5c25c | note | Acceptance Criteria - Pipe not damaged during installation
a813294d-4cc9-5de9-8013-acc9af340607 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
b5fa012f-be3c-5636-91d1-fdd80d368537 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
ebb1d923-d0aa-50bd-9dac-f46238764107 | note | Frequency - During installation
db7fd423-ed15-5616-a986-70a71c212cf8 | note | Inspection Type (Visual, other) - Visual, Survey
7159e17e-8d44-5d0d-845c-0e53cca1c85b | note | Inspection: Key - C
ff88a9b0-e928-5d5a-82fa-59dde51d4a4f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
04ab3a9a-384e-5529-84a7-7dea85c86652 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
d54a932b-c8ea-598b-bd5c-157b1440ff54 | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
23d3b260-127a-529b-a3b8-fbf7c3eb16fc | note | Verifying Document - Photos, measurement checks
c702bd62-1125-5801-9085-16a258c893a8 | note | Frequency - Every Lateral
5e5085e9-4c90-521f-bdfc-4a0672c90e85 | note | Inspection Type (Visual, other) - Visual, Survey
bd8ebce9-5fcb-5785-964b-09b0805bdbab | note | Inspection: Key - C
e346e155-5b90-547e-9783-a847beb34fe0 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
09b4b50e-a86b-5a4e-adb4-fa6d337ecd5b | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
8bf890d5-d8bf-5f27-b7d4-2a2ac42d69af | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
40d1536e-0e1b-59be-ba67-0dcb2d6a2776 | note | Acceptance Criteria - min 100mm bedding
72de3943-f47e-55a5-a375-ac3f113827b0 | note | ○ 100mm overlay
105fef89-3a30-57fb-a939-0f69e881b085 | note | Verifying Document - Photos
19855ea0-4dcb-5c2d-ab2b-90c9cf3a3314 | note | Frequency - During Installation
c43bf7e3-70b8-54c6-9cc7-1bed12e01a20 | note | Inspection Type (Visual, other) - Visual, measurement check
3f8dcd5f-c11d-542a-9a87-ef0a50dc3e1d | note | Inspection: Key - C
289a7157-1d60-5d7f-b9f0-9ea020f16ae2 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
6fe0cd67-fbdf-5cad-a738-64b3873ece9e | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
c47c83fa-e5ad-5ece-8c58-c236b63a0ff4 | note | ○ Compaction testing one test every two layers as required
91d46ade-8b54-527f-91ff-111dfddd2ac7 | note | ○ Conductive signal strip to be laid at 300mm above pipe
d4d31b4e-1f6e-54c0-8a8b-42c7fc9f3fc7 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
c18fa8bd-c2a7-5e2f-bb00-a48e929b4b3a | note | Verifying Document - Photos, Compaction test results
7afd1cd2-2693-5ab1-8855-1ab06da78ce8 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
27ef7f76-e5ce-5bf9-8261-6ae426368e14 | note | Inspection Type (Visual, other) - Visual, On Site test
4ea1a684-fc2a-5a63-bd5d-b4697a6256b9 | note | Inspection: Key - H
276e077a-bcc9-5ce5-9d51-5660f4c414ae | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
38d79f98-d667-5c79-92ea-4c5227d2c959 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
b4a1cd80-8933-5082-b7d5-8348a6d1f28c | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
80ac3360-b4da-58d9-8dfc-9094a250c594 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
47ebf879-e8fb-59dd-87e9-82ef53764765 | note | ○ Dips or ponding of water inside the pipe
ad3cad01-3e37-5482-a4ab-47cd8249ca8c | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
56c76dd2-15fb-5820-a544-bf48cc0d5429 | note | Verifying Document - Test Records, CCTV footage
5e8ee003-21ae-58d0-abf7-5e5c049882fe | note | Frequency - Every section of pipe completed
33f19922-04cc-5ee4-a181-a7e91e525fae | note | Inspection Type (Visual, other) - On-Site Test
794a6e13-870a-57f3-a4c5-3d2253f62fe1 | note | Inspection: Key - H
56b3f79c-9ecf-540d-a262-0b6b2b4e1815 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
3319707f-5d8c-562a-8ef3-587361fc043c | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
1c72d0fb-0ba1-548d-8def-cd810a9de009 | note | Acceptance Criteria - Engineer Approval
968c6e86-985e-552c-8bfa-c114d8a95b7a | note | Verifying Document - Test Records
62347b10-5809-5ae0-9d15-01a823ba023c | note | Frequency - Every section of pipe installed
b99d6c44-c36e-554a-8ccf-b76711765467 | note | Inspection Type (Visual, other) - On-Site Test
06f90db4-87bb-5f12-9ef7-24beb195e20a | note | Inspection: Key - H
64588d90-d5f9-577b-9b20-016697b2b094 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
69a8a319-ae3b-572d-a463-f1ca5eca6e7e | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
639fa143-b341-59d6-94b0-687287780f51 | note | Acceptance Criteria - Signed ITP
cff52efc-8af4-5481-8212-26bfd0d3f929 | note | Verifying Document - Red pen markup drawings
6cb9ccd1-f63f-5ec4-bcc3-3aca386ad59c | note | Frequency - After completion of pipe section
4bee6db4-55b7-56d2-b030-c996c4bcd76e | note | Inspection Type (Visual, other) - Document
aa477c00-6014-5d85-905e-108d1d1849a8 | note | Inspection: Key - H
088e458d-d157-5a69-b0f9-e55824f63e68 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of PVC SW pipe - 300 zone 6 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
13b74c26-053a-5c39-a586-797f1635c254 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
9284b471-55b6-55de-ac70-2c82ec79bbb0 | note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
84acdc02-e0bb-5491-8dc8-fbe19d9a4207 | note | ○ Items are approved as per contract specification
ceff9359-d81d-546c-97b9-9146c1fbe68f | note | ○ DCC approved
ee4a1268-a257-5491-90d7-27b0c6097961 | note | Verifying Document - Photos, delivery docket,
3ddce36d-5a72-5e71-a9d2-d12d0b5ab0c4 | note | Frequency - On Delivery
646390fd-b681-50f9-bb3c-04063fc27c27 | note | Inspection Type (Visual, other) - Visual
12a1fa5d-0f59-5ef7-a175-eb085b31eae2 | note | Inspection: Key - C
96f84a6f-af0d-509d-89a1-c3a6bb8023c9 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
9bbac671-99d6-5b75-8cc5-57bb6a6203e1 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
90828ae5-9932-5e27-b691-ebd484f2fa30 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
886e4424-41a8-58b2-b90e-f409a49c6617 | note | Verifying Document - Survey marks, photos
421dc5d8-9a75-5422-89a7-1b6f7fba1c1f | note | Frequency - Prior to commencement of works
382706af-0939-5c33-be0b-5a0c6f5d0928 | note | Inspection Type (Visual, other) - Survey
50fb44c8-9d6b-5e3a-a00f-76cb8e505fb8 | note | Inspection: Key - H
a0aa9287-65a0-52b3-84f7-2c56fba7812c | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
f61898e8-e94c-5e3f-b0a8-e0d7120ebc28 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
d2c50cdc-945f-5b34-9dd4-4704219f3052 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
e5a6b4fe-e74d-5588-b5c5-043a1286eb7c | note | Verifying Document - Delivery dockets, photos
e7916375-f798-5fe7-a75d-e6fb4e348f10 | note | Frequency - On Delivery
0b88f83b-5f49-58e9-940a-8ccc0d676686 | note | Inspection Type (Visual, other) - Visual
11a53bf7-7b09-5755-8f10-63c189645560 | note | Inspection: Key - C
1355b01f-5a09-57e6-aa3d-d3d4491f2c27 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
955cd150-f299-5fc2-a187-dd4fc38002ae | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4301
0574bc8d-5024-520d-92fb-c48cf809237a | note | ○ Floor of trench to be even across width and length
37cd7643-d2c7-57fc-aaf6-563cc9c8c266 | note | Acceptance Criteria - As per 561467-TW-04-DRW-02
77a36b85-b9cf-5f94-a60c-4ad6588d756b | note | Verifying Document - Photos, measurement checks
5bfbd410-8a7c-567f-bc85-1b7af0fd51ff | note | Frequency - During Installation
fea66bfa-3997-5fc5-ba7a-df3b67dfc732 | note | Inspection Type (Visual, other) - Visual
6b65a327-1b89-5f76-8f5e-875105628501 | note | Inspection: Key - V
74835963-98f2-5442-b26d-f0809b23c391 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
af8ff430-9933-5231-b7d7-1d95304c0e84 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
a1f8f8f1-7818-5fe0-a5f5-098096b284ce | note | Acceptance Criteria - minimum of 2 blows per 100mm
1492de43-6e99-5185-91f4-32afd4d5532f | note | Verifying Document - Test results
b3082378-39b5-52ca-aea9-15679cc8fcb6 | note | Frequency - During installation, per 20m
90719ac5-625e-5a85-aa4e-98bf5cb52d48 | note | Inspection Type (Visual, other) - On site test
fc78897b-d0b9-5093-8725-5ddd0b035c0a | note | Inspection: Key - H
0756547f-733e-566c-b801-33b9ab940887 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
b7c3f0b6-80d4-5804-8039-b1d423f77516 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4301
71ff12d6-4cf3-5b6f-b0ab-f56350c5c25c | note | Acceptance Criteria - Pipe not damaged during installation
a813294d-4cc9-5de9-8013-acc9af340607 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
b5fa012f-be3c-5636-91d1-fdd80d368537 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
ebb1d923-d0aa-50bd-9dac-f46238764107 | note | Frequency - During installation
db7fd423-ed15-5616-a986-70a71c212cf8 | note | Inspection Type (Visual, other) - Visual, Survey
7159e17e-8d44-5d0d-845c-0e53cca1c85b | note | Inspection: Key - C
ff88a9b0-e928-5d5a-82fa-59dde51d4a4f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
04ab3a9a-384e-5529-84a7-7dea85c86652 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
d54a932b-c8ea-598b-bd5c-157b1440ff54 | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
23d3b260-127a-529b-a3b8-fbf7c3eb16fc | note | Verifying Document - Photos, measurement checks
c702bd62-1125-5801-9085-16a258c893a8 | note | Frequency - Every Lateral
5e5085e9-4c90-521f-bdfc-4a0672c90e85 | note | Inspection Type (Visual, other) - Visual, Survey
bd8ebce9-5fcb-5785-964b-09b0805bdbab | note | Inspection: Key - C
e346e155-5b90-547e-9783-a847beb34fe0 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
09b4b50e-a86b-5a4e-adb4-fa6d337ecd5b | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
8bf890d5-d8bf-5f27-b7d4-2a2ac42d69af | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
40d1536e-0e1b-59be-ba67-0dcb2d6a2776 | note | Acceptance Criteria - min 100mm bedding
72de3943-f47e-55a5-a375-ac3f113827b0 | note | ○ 100mm overlay
105fef89-3a30-57fb-a939-0f69e881b085 | note | Verifying Document - Photos
19855ea0-4dcb-5c2d-ab2b-90c9cf3a3314 | note | Frequency - During Installation
c43bf7e3-70b8-54c6-9cc7-1bed12e01a20 | note | Inspection Type (Visual, other) - Visual, measurement check
3f8dcd5f-c11d-542a-9a87-ef0a50dc3e1d | note | Inspection: Key - C
289a7157-1d60-5d7f-b9f0-9ea020f16ae2 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
6fe0cd67-fbdf-5cad-a738-64b3873ece9e | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
c47c83fa-e5ad-5ece-8c58-c236b63a0ff4 | note | ○ Compaction testing one test every two layers as required
91d46ade-8b54-527f-91ff-111dfddd2ac7 | note | ○ Conductive signal strip to be laid at 300mm above pipe
d4d31b4e-1f6e-54c0-8a8b-42c7fc9f3fc7 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
c18fa8bd-c2a7-5e2f-bb00-a48e929b4b3a | note | Verifying Document - Photos, Compaction test results
7afd1cd2-2693-5ab1-8855-1ab06da78ce8 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
27ef7f76-e5ce-5bf9-8261-6ae426368e14 | note | Inspection Type (Visual, other) - Visual, On Site test
4ea1a684-fc2a-5a63-bd5d-b4697a6256b9 | note | Inspection: Key - H
276e077a-bcc9-5ce5-9d51-5660f4c414ae | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
38d79f98-d667-5c79-92ea-4c5227d2c959 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
b4a1cd80-8933-5082-b7d5-8348a6d1f28c | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
80ac3360-b4da-58d9-8dfc-9094a250c594 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
47ebf879-e8fb-59dd-87e9-82ef53764765 | note | ○ Dips or ponding of water inside the pipe
ad3cad01-3e37-5482-a4ab-47cd8249ca8c | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
56c76dd2-15fb-5820-a544-bf48cc0d5429 | note | Verifying Document - Test Records, CCTV footage
5e8ee003-21ae-58d0-abf7-5e5c049882fe | note | Frequency - Every section of pipe completed
33f19922-04cc-5ee4-a181-a7e91e525fae | note | Inspection Type (Visual, other) - On-Site Test
794a6e13-870a-57f3-a4c5-3d2253f62fe1 | note | Inspection: Key - H
56b3f79c-9ecf-540d-a262-0b6b2b4e1815 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
3319707f-5d8c-562a-8ef3-587361fc043c | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
1c72d0fb-0ba1-548d-8def-cd810a9de009 | note | Acceptance Criteria - Engineer Approval
968c6e86-985e-552c-8bfa-c114d8a95b7a | note | Verifying Document - Test Records
62347b10-5809-5ae0-9d15-01a823ba023c | note | Frequency - Every section of pipe installed
b99d6c44-c36e-554a-8ccf-b76711765467 | note | Inspection Type (Visual, other) - On-Site Test
06f90db4-87bb-5f12-9ef7-24beb195e20a | note | Inspection: Key - H
64588d90-d5f9-577b-9b20-016697b2b094 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
69a8a319-ae3b-572d-a463-f1ca5eca6e7e | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
639fa143-b341-59d6-94b0-687287780f51 | note | Acceptance Criteria - Signed ITP
cff52efc-8af4-5481-8212-26bfd0d3f929 | note | Verifying Document - Red pen markup drawings
6cb9ccd1-f63f-5ec4-bcc3-3aca386ad59c | note | Frequency - After completion of pipe section
4bee6db4-55b7-56d2-b030-c996c4bcd76e | note | Inspection Type (Visual, other) - Document
aa477c00-6014-5d85-905e-108d1d1849a8 | note | Inspection: Key - H
088e458d-d157-5a69-b0f9-e55824f63e68 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of SW Manhole Zone 2 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
8fa440c1-35c5-5acd-a51d-7b63cb6819ad | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
b0775011-5c47-5478-a743-050b5e4e124f | note | Acceptance Criteria - Items are approved as per contract specification
1916c62f-0d2c-5946-a3c3-4f4e0ecce308 | note | ○ DCC approved
e22c4cf7-ba3b-530d-8827-d51d3fc91e53 | note | Verifying Document - Photos, delivery docket
7f7d3831-7829-581b-84bd-bb78b0212d8c | note | Frequency - On Delivery
edf2c7d9-ab72-5b5b-9799-c53ef40817b4 | note | Inspection Type (Visual, other) - Visual
d27a6a00-b74f-51bf-a1c9-ad9e267ac8ba | note | Inspection: Key - C
9316ddb4-9b6e-5563-9ef8-d03b6230b399 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
f81aa168-e5a8-5538-a502-81dc091b0694 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
b0a97d3e-4763-5a4b-94a9-64472d2198bb | note | Acceptance Criteria - Allignment set out matches drawing C4200 or aggreed with the Engineer
640f6956-0a9b-58cc-b4d8-9c1a0b867556 | note | Verifying Document - Survey marks, photos
dd42f976-425b-5c35-b376-c8b63ce81413 | note | Frequency - Prior to commencement of works
acb47ab2-3426-5196-a9c1-47ed2769912e | note | Inspection Type (Visual, other) - Survey
06ca9a3d-c73f-54f2-96f6-b088047b106f | note | Inspection: Key - H
f4651f5a-5a50-564f-be63-4ed2f6f66d38 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
0a7d577b-71ef-53c0-ab91-cc85d898547d | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
c93739d4-5f81-5b46-a260-ecf26f4749b7 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
0bbcab58-544d-50fb-a6c9-f534c56b42a3 | note | Verifying Document - Delivery dockets, photos
f1737fed-8057-5afa-ac20-e3a058349865 | note | Frequency - On Delivery
4d83e778-7f4f-5ea2-a72b-1fa535b38664 | note | Inspection Type (Visual, other) - Visual
f57f05df-bf6d-5793-a67e-d73780c58490 | note | Inspection: Key - C
ec227945-d25b-5ee2-93b8-9a3af819e859 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
0d3ee789-6114-5abe-96aa-1888cdb5ec60 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
7df35265-64d1-52bd-bf58-0c9c79c1ed70 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4057deb7-13bb-5ee4-90b6-5c658f603d88 | note | ○ Floor of Trench to be even across width and length
c95c216c-dfdf-55a2-baba-7748a0a7068f | note | Acceptance Criteria - As per 561467-TW-04-DRW-002
abf5e034-9e42-5edb-8f4d-e40c9f91913f | note | Verifying Document - Photos, measurement checks
4cc64e1d-a805-5f2c-8520-c3129fee6143 | note | Frequency - During Installation
361e2426-2cca-5b2a-b138-7cfbdfc5ee6d | note | Inspection Type (Visual, other) - Visual
82c31f58-1382-5655-b00b-9e244d20d00f | note | Inspection: Key - V
8ce679d4-7b2e-56cc-bbe5-6aba815c4380 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
db1349e0-c37c-562a-984b-8dd83a107885 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
ebb09bc1-86a4-5db0-9b72-80fa8d68a632 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
49e613a2-9fe9-5bfd-bf85-7de44bde68a6 | note | Verifying Document - Test results
4cc02fab-c9d2-51a2-a782-ad30e38613c1 | note | Frequency - During installation, per 20m
43eed011-7105-52b0-bf4e-8d04815e680c | note | Inspection Type (Visual, other) - Visual, On site test
c08e0479-5b0e-59f6-9983-09693d4ffc63 | note | Inspection: Key - H
be471dab-2f27-5298-89cb-ff668bd7f56f | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
10dcd092-9a4e-52f1-bcca-7afc901a024b | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
b67b94dc-fc4f-5956-ba16-122048ad9dbb | note | Acceptance Criteria - Bedding to comply with requirements
bf01b1e9-1d9e-5f5f-8a13-71af8770afde | note | Verifying Document - Photo
31afb6b1-51c8-55dd-a565-5447ebf59d88 | note | Frequency - During installation
6f291ce0-4ff6-5068-8754-4c877f260982 | note | Inspection Type (Visual, other) - Visual, Measurement Check
c3d2eb8e-0b93-534c-9877-1e74125bb723 | note | Inspection: Key - C
bf6a94f4-628b-5d30-a36c-39a8f6342935 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
9b0db491-a9cb-564c-8c2d-2bad3e0c19d3 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
5bd7b6ef-bd55-53ec-b535-acade7c8379f | note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
00337b51-e286-5684-a097-2c725edf0514 | note | Verifying Document - Photos, As-built
1eadbb7f-3c41-5b2a-ac18-c20fb712da9d | note | Frequency - During installation
ade83643-63f3-5c98-b684-cb78a024ca39 | note | Inspection Type (Visual, other) - Survey
e3812b53-945b-5e99-92b3-d17ac162bb87 | note | Inspection: Key - H
96885560-ae96-5855-b777-211d31919e2c | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
1c6445ad-3259-545e-a1c5-1c527ea49e75 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
a418cdcc-d4c9-5bca-8796-8560a5aef0c5 | note | ○ Benching shape to have smooth transitions at bends and junctions
1b2e754b-1695-52e9-98e8-b0b7d9f85a51 | note | Acceptance Criteria - Benching built up to the specifications
46f57886-66cc-5359-9f92-ac62bb8d0a75 | note | Verifying Document - Photos
81571416-ec56-5f97-a5ba-fef7a53ed24a | note | Frequency - During benching contruction
c0ce49fb-7d55-5d85-ad19-55d04d72dffe | note | Inspection Type (Visual, other) - Visual, Test Results
2899b8cb-27b9-595a-a5ee-a452d8c3f2c3 | note | Inspection: Key - H
247e67d6-4254-580b-b23f-7fb864f0559d | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
50cbb4d8-92ca-54cb-922d-2eefa1d3c222 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
208d99fe-2c94-5475-bca4-f36e9144381f | note | ○ Compaction testing one test every two layers as required
ff634880-7be7-52a4-93b1-c4ddb5e0996f | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
db3078c3-787d-5ec5-bb09-64bb4f014f96 | note | Verifying Document - Photos, Compaction test results
83c16760-a499-53e7-97a7-d468e6ce33b6 | note | Frequency - During Installation
f1f5d583-8224-50b5-88c7-d2972cdfade0 | note | Inspection Type (Visual, other) - Visual, On Site test
7af48950-7658-5d3a-8156-fdbbdda1d11f | note | Inspection: Key - H
70fcba41-5093-5bc7-9eae-4661563cfa7a | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
ba52f972-ce5c-58bd-a3ad-7493fe092f6a | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
ab949f49-d09c-5c0b-813b-b1fbe163c4d3 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
4a5d664a-39c3-5eea-b1ea-f359b1166659 | note | Verifying Document - Photos, test records
481f87fe-004f-5b5f-b1c6-c3bdc2d3636a | note | Frequency - For every manhole
ab33242a-d9cc-5ca6-9095-2739d5fe87ee | note | Inspection Type (Visual, other) - Test, visual
ddf8de6d-7895-5fed-9920-6da42b03d295 | note | Inspection: Key - H
e122a6e1-b2a1-5138-b5e0-2abdd50995bb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
11e93153-0a59-56e2-8bf2-b48e861a1cce | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
8f489c22-9c6e-5a4a-96df-e96cb8ad05b4 | note | Acceptance Criteria - Signed ITP
4f80bbb7-24c7-5cab-a479-a612224c6f59 | note | Verifying Document - Red pen markup drawings
9e7dcbc8-9a00-589f-a41e-ce5a854e2d34 | note | Frequency - After installation of FSMH
dbef015b-f651-5642-8e52-97cc808e1371 | note | Inspection Type (Visual, other) - Document
9ab3b63a-07ed-51f1-93f5-1476d8da1168 | note | Inspection: Key - H
e1186783-7db3-58a0-b527-b39f5242c16b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of SW Manhole Zone 5 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
8fa440c1-35c5-5acd-a51d-7b63cb6819ad | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
b0775011-5c47-5478-a743-050b5e4e124f | note | Acceptance Criteria - Items are approved as per contract specification
1916c62f-0d2c-5946-a3c3-4f4e0ecce308 | note | ○ DCC approved
e22c4cf7-ba3b-530d-8827-d51d3fc91e53 | note | Verifying Document - Photos, delivery docket
7f7d3831-7829-581b-84bd-bb78b0212d8c | note | Frequency - On Delivery
edf2c7d9-ab72-5b5b-9799-c53ef40817b4 | note | Inspection Type (Visual, other) - Visual
d27a6a00-b74f-51bf-a1c9-ad9e267ac8ba | note | Inspection: Key - C
9316ddb4-9b6e-5563-9ef8-d03b6230b399 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
f81aa168-e5a8-5538-a502-81dc091b0694 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
b0a97d3e-4763-5a4b-94a9-64472d2198bb | note | Acceptance Criteria - Allignment set out matches drawing C4300 or aggreed with the Engineer
640f6956-0a9b-58cc-b4d8-9c1a0b867556 | note | Verifying Document - Survey marks, photos
dd42f976-425b-5c35-b376-c8b63ce81413 | note | Frequency - Prior to commencement of works
acb47ab2-3426-5196-a9c1-47ed2769912e | note | Inspection Type (Visual, other) - Survey
06ca9a3d-c73f-54f2-96f6-b088047b106f | note | Inspection: Key - H
f4651f5a-5a50-564f-be63-4ed2f6f66d38 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
0a7d577b-71ef-53c0-ab91-cc85d898547d | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
c93739d4-5f81-5b46-a260-ecf26f4749b7 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
0bbcab58-544d-50fb-a6c9-f534c56b42a3 | note | Verifying Document - Delivery dockets, photos
f1737fed-8057-5afa-ac20-e3a058349865 | note | Frequency - On Delivery
4d83e778-7f4f-5ea2-a72b-1fa535b38664 | note | Inspection Type (Visual, other) - Visual
f57f05df-bf6d-5793-a67e-d73780c58490 | note | Inspection: Key - C
ec227945-d25b-5ee2-93b8-9a3af819e859 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
0d3ee789-6114-5abe-96aa-1888cdb5ec60 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4300
7df35265-64d1-52bd-bf58-0c9c79c1ed70 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4057deb7-13bb-5ee4-90b6-5c658f603d88 | note | ○ Floor of Trench to be even across width and length
c95c216c-dfdf-55a2-baba-7748a0a7068f | note | Acceptance Criteria - As per 561467-TW-04-DRW-002
abf5e034-9e42-5edb-8f4d-e40c9f91913f | note | Verifying Document - Photos, measurement checks
4cc64e1d-a805-5f2c-8520-c3129fee6143 | note | Frequency - During Installation
361e2426-2cca-5b2a-b138-7cfbdfc5ee6d | note | Inspection Type (Visual, other) - Visual
82c31f58-1382-5655-b00b-9e244d20d00f | note | Inspection: Key - V
8ce679d4-7b2e-56cc-bbe5-6aba815c4380 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
db1349e0-c37c-562a-984b-8dd83a107885 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
ebb09bc1-86a4-5db0-9b72-80fa8d68a632 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
49e613a2-9fe9-5bfd-bf85-7de44bde68a6 | note | Verifying Document - Test results
4cc02fab-c9d2-51a2-a782-ad30e38613c1 | note | Frequency - During installation, per 20m
43eed011-7105-52b0-bf4e-8d04815e680c | note | Inspection Type (Visual, other) - Visual, On site test
c08e0479-5b0e-59f6-9983-09693d4ffc63 | note | Inspection: Key - H
be471dab-2f27-5298-89cb-ff668bd7f56f | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
10dcd092-9a4e-52f1-bcca-7afc901a024b | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
b67b94dc-fc4f-5956-ba16-122048ad9dbb | note | Acceptance Criteria - Bedding to comply with requirements
bf01b1e9-1d9e-5f5f-8a13-71af8770afde | note | Verifying Document - Photo
31afb6b1-51c8-55dd-a565-5447ebf59d88 | note | Frequency - During installation
6f291ce0-4ff6-5068-8754-4c877f260982 | note | Inspection Type (Visual, other) - Visual, Measurement Check
c3d2eb8e-0b93-534c-9877-1e74125bb723 | note | Inspection: Key - C
bf6a94f4-628b-5d30-a36c-39a8f6342935 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
9b0db491-a9cb-564c-8c2d-2bad3e0c19d3 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
5bd7b6ef-bd55-53ec-b535-acade7c8379f | note | Acceptance Criteria - Final levels are in accordance with the C4300 or within tolerance and agreed with the Engineer
00337b51-e286-5684-a097-2c725edf0514 | note | Verifying Document - Photos, As-built
1eadbb7f-3c41-5b2a-ac18-c20fb712da9d | note | Frequency - During installation
ade83643-63f3-5c98-b684-cb78a024ca39 | note | Inspection Type (Visual, other) - Survey
e3812b53-945b-5e99-92b3-d17ac162bb87 | note | Inspection: Key - H
96885560-ae96-5855-b777-211d31919e2c | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
1c6445ad-3259-545e-a1c5-1c527ea49e75 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
a418cdcc-d4c9-5bca-8796-8560a5aef0c5 | note | ○ Benching shape to have smooth transitions at bends and junctions
1b2e754b-1695-52e9-98e8-b0b7d9f85a51 | note | Acceptance Criteria - Benching built up to the specifications
46f57886-66cc-5359-9f92-ac62bb8d0a75 | note | Verifying Document - Photos
81571416-ec56-5f97-a5ba-fef7a53ed24a | note | Frequency - During benching contruction
c0ce49fb-7d55-5d85-ad19-55d04d72dffe | note | Inspection Type (Visual, other) - Visual, Test Results
2899b8cb-27b9-595a-a5ee-a452d8c3f2c3 | note | Inspection: Key - H
247e67d6-4254-580b-b23f-7fb864f0559d | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
50cbb4d8-92ca-54cb-922d-2eefa1d3c222 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
208d99fe-2c94-5475-bca4-f36e9144381f | note | ○ Compaction testing one test every two layers as required
ff634880-7be7-52a4-93b1-c4ddb5e0996f | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
db3078c3-787d-5ec5-bb09-64bb4f014f96 | note | Verifying Document - Photos, Compaction test results
83c16760-a499-53e7-97a7-d468e6ce33b6 | note | Frequency - During Installation
f1f5d583-8224-50b5-88c7-d2972cdfade0 | note | Inspection Type (Visual, other) - Visual, On Site test
7af48950-7658-5d3a-8156-fdbbdda1d11f | note | Inspection: Key - H
70fcba41-5093-5bc7-9eae-4661563cfa7a | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
ba52f972-ce5c-58bd-a3ad-7493fe092f6a | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
ab949f49-d09c-5c0b-813b-b1fbe163c4d3 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
4a5d664a-39c3-5eea-b1ea-f359b1166659 | note | Verifying Document - Photos, test records
481f87fe-004f-5b5f-b1c6-c3bdc2d3636a | note | Frequency - For every manhole
ab33242a-d9cc-5ca6-9095-2739d5fe87ee | note | Inspection Type (Visual, other) - Test, visual
ddf8de6d-7895-5fed-9920-6da42b03d295 | note | Inspection: Key - H
e122a6e1-b2a1-5138-b5e0-2abdd50995bb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
11e93153-0a59-56e2-8bf2-b48e861a1cce | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
8f489c22-9c6e-5a4a-96df-e96cb8ad05b4 | note | Acceptance Criteria - Signed ITP
4f80bbb7-24c7-5cab-a479-a612224c6f59 | note | Verifying Document - Red pen markup drawings
9e7dcbc8-9a00-589f-a41e-ce5a854e2d34 | note | Frequency - After installation of FSMH
dbef015b-f651-5642-8e52-97cc808e1371 | note | Inspection Type (Visual, other) - Document
9ab3b63a-07ed-51f1-93f5-1476d8da1168 | note | Inspection: Key - H
e1186783-7db3-58a0-b527-b39f5242c16b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of RCRRJ SW pipe - 750 | itp
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
fd6945ee-161e-528f-a7ba-18671463b1f4 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
30500143-ffbe-5e6f-b61b-3f02c8de8a97 | note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
25a84a91-46b6-5297-bd5a-7c2e359cc295 | note | ○ Items are approved as per contract specification
872e47c9-deec-5ace-9b6e-bf29fab0b698 | note | ○ DCC approved
4cbd8926-a97c-5e69-9c28-12c208e9b94e | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
c638e561-52bc-5cc6-940d-97426bc3270f | note | Frequency - On Delivery
32412e66-96ea-5503-a4bd-fd012de17507 | note | Inspection Type (Visual, other) - Visual
0e3de0f6-fbf7-5689-9c59-a9a488b72514 | note | Inspection: Key - C
37a5d4d0-ae36-5598-b6ae-d0c128a6a6e6 | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
1d025ba7-84f8-5a68-80aa-f546c3e476fe | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
a18a71b7-f5b3-55da-9a42-315f8a3fb085 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
c438f1ca-ca49-573a-a728-98d9b23df8fc | note | Verifying Document - Survey marks, photos
145385a7-3c62-5568-8c18-f5d74aebe421 | note | Frequency - Prior to commencement of works
b53b2af4-9ec3-5597-820f-1b1844e48c44 | note | Inspection Type (Visual, other) - Visual, Instrumental
907002a6-abe7-5234-a401-c5411967045c | note | Inspection: Key - H
5170a963-0ce3-5629-898f-7773978a3e51 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
876c492a-569c-5cad-af49-b1f4a14d0982 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200
f726ae62-5fc4-55d1-b510-9bdece611fba | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
2e968e45-52fd-5eca-91d4-f9f0f9cdbd9b | note | ○ Floor of Trench to be even across width and length
3b577317-9241-5e89-8610-01d9fe1b0b35 | note | Acceptance Criteria - Allow 100mm for bedding
06794c26-132e-5aee-8dc1-d514aead8a3c | note | ○ Allow for minimum cover of 750mm.
57e0e33f-08ae-5ce0-84ca-228614e7049f | note | Verifying Document - Photos, measurement checks
1cb1a6e3-29a6-59ac-8117-1e241067659e | note | Frequency - During Installation
13749fcb-6ec8-5dcb-8f20-5c27a7ca0a79 | note | Inspection Type (Visual, other) - Visual
58cbc2ee-2495-5961-9a85-2385c3b78aff | note | Inspection: Key - C
1bf9adb5-fc40-5a40-af5c-8530adc1e7da | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Geotextile
a01e27da-3e23-5b0d-8e39-cde180bf65b8 | note | Inspection Point: Quality Control Activity - Install Bidim A29 or approved equivalient around bedding, haunch, overlay zone and trench fill up to the subbase.
a4e4ff19-b865-52d0-a713-267a182ce132 | note | Acceptance Criteria - Geotextile not damged during pipe installation and backfilling
0864ed3d-5d0b-55f7-9d86-da2dedd9d448 | note | Verifying Document - photos
f865fed2-061a-549e-b998-657a685eb152 | note | Frequency - During Installation
9d442d0d-e9cf-5a89-a5f9-0bccfa4ca9f2 | note | Inspection Type (Visual, other) - Visual
3c852204-1ad1-5825-8b23-c8338d5c19b8 | note | Inspection: Key - C
fb694baf-9510-5682-9be8-cd6c79bb6041 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Foundation
6c32f554-45a8-5982-b71d-dca3d103fcb3 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
5ec6f3c9-66ec-5521-8443-fe515516bc0d | note | Acceptance Criteria - minimum of 2 blows per 100mm
3fe36b72-c1c3-538d-959b-e45ea6bc8401 | note | Verifying Document - test results
ed36a9ca-a1bc-528e-aa48-9e7e4a9ae34d | note | Frequency - During installation, per 20m
44ef94b6-f5d4-554e-bbf4-5b0310580a0f | note | Inspection Type (Visual, other) - Visual, On site test
d4f55b18-cbcd-5461-aa31-b605fd390874 | note | Inspection: Key - H
bedcb70b-88f8-579c-8759-7988b37c23f7 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.4 - Install Pipe
01774be6-7dc1-5c81-b86a-e4bf082451e0 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
e3885ae4-8036-572c-abc6-f8802c2bd193 | note | Acceptance Criteria - Pipe not damaged during installation
794e737a-2ee8-5ac6-b649-813a5ceab51b | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
005e0fb5-bc55-5c1d-9353-eb2af465a1d4 | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
5f6b8ad9-7595-5489-b523-045227f15a4a | note | Frequency - During installation
0fb163fd-01ae-5e8c-838f-52ef56dbdb84 | note | Inspection Type (Visual, other) - Visual, instrumental
be2be8c5-4579-5558-b01e-23e65b49783d | note | Inspection: Key - C
218d0fd8-0a90-5908-b041-ef93fb4df668 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
635df6bc-2169-5075-9217-3ee8d00a7d28 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
bbd42304-d1c1-5a05-bd03-efb6f7749b8a | note | Acceptance Criteria - min 100mm bedding
9e8031c2-4766-5977-a396-fead57d2b48a | note | ○ 150mm overlay
d8b9e474-727f-5ee5-8691-0bb3131de80c | note | Verifying Document - Photos
2696b515-34d1-5d3e-be54-4061b38c961f | note | Frequency - During Installation
3259ebe2-d38a-531c-824a-f1f258940d2d | note | Inspection Type (Visual, other) - Visual, measurement check
18dbfcc2-4a89-541f-9ea3-9e611a4e10c3 | note | Inspection: Key - C
de3b6d4a-fa11-5e69-9ce7-aae5376e159d | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
5acfd24f-c4b3-5a56-8afa-017a6cd382ce | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
96405d46-6e1a-5c33-86d3-d93a5fbd2dde | note | ○ Compaction testing one test every two layers as required
58f08d5f-b76a-5af5-947b-54470eef25ce | note | ○ Conductive signal strip to be laid at 300mm above pipe
3f878185-066f-5194-88ab-ea20381b2f1d | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1825faef-0a26-55b7-83b1-c69af9b159fa | note | Verifying Document - Photos, Compaction test results
7dc98ecd-1581-5e8f-b7a3-4a0ab66d8a18 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
65acd8ea-4631-5acb-814d-cd26fd5fc915 | note | Inspection Type (Visual, other) - Visual, On Site test
75a8bf67-1ef5-5ac7-87d7-505aacc93b2c | note | Inspection: Key - H
6de8bec6-504c-512a-a402-c398fbe2f3d5 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
626aa881-27ba-59a2-82b1-9365e8b3f93c | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
56d851cd-d52e-5b44-9782-c820003a2728 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
d62af583-43b3-5825-88a9-9e19923c3f2f | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
9c38fdfb-3666-52f4-87a9-9724124be89f | note | ○ Dips or ponding of water inside the pipe
1575af2c-bf99-564a-b95a-643631d0d42d | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
b2ac9c90-0f8d-544c-9b2a-1cf6e61120b8 | note | Verifying Document - Test Records, CCTV footage
1fc07a43-648f-5765-bb1a-fbb32620c000 | note | Frequency - Every section of pipe completed
d4ffe9d1-9cc4-5358-bb32-940fc63a731f | note | Inspection Type (Visual, other) - On-Site Test
670e48e7-7035-584d-a4b7-539ce0478048 | note | Inspection: Key - H
a74729c6-6813-560c-a502-dda72f882b23 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak Testing
d6681634-7294-527f-8e31-05ec4baf8649 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
3b8806c2-3ac1-5058-a26c-02271ab79ba5 | note | Acceptance Criteria - Engineer Approval
fc9740a0-2050-5c5f-9784-b07cd6cd5e42 | note | Verifying Document - Test Records
5db85558-8b9d-57d0-a926-b7bc5887cb60 | note | Frequency - Every section of pipe installed
147407a2-a6a2-5132-8b77-2855588ff1ac | note | Inspection Type (Visual, other) - On-Site Test
bc0bfb46-5276-528d-89cb-6ee202faf965 | note | Inspection: Key - H
f8fad0e0-8e0e-5707-b7a5-654fe9bc88cb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
b7859528-d948-54ce-aeb9-29d8eb672c80 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
bc228714-ca29-537f-9188-731a14e8f7ca | note | Frequency - After completion of pipe section
293a5856-2300-56e3-afef-d9469d25f14f | note | Inspection Type (Visual, other) -
f5f0fc6a-51b8-581e-a72d-7f77e4e2bd84 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 5.4 - As built
a080f463-13fb-547e-ab99-95e877eb407a | note | Acceptance Criteria - Engineer Approval
7629ddab-d5e6-5881-8c26-f38602705d7b | note | Verifying Document - QA records
7a7d1b44-0f34-5b2c-85bb-636589345f36 | note | Frequency - at completion
179452ed-7c4b-5bca-bf88-28a26a8892d8 | note | Inspection Type (Visual, other) - Asbuilt drawings
3ff4bf4d-396e-5457-af8d-359b6a03b7fc | note | Inspection: Key - H
a7da4251-21b4-57ce-b991-01fb006cb615 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT