## Sheet1
DEL-ITP-080
Inspection and Test plan
| Construction Process: |  |  | 66KV CB Foundation | [6 empty] | Prepared By: |  | David R.
[11 empty] | Approved By: |  | Azeen N.
Client: | Powercor Network Services | [10 empty] | Date: | 2024-12-29
Project: | TNA |  |  | Project No. | 27778 | Lote #: | [5 empty] | Version: | 4
Item No. | Task Activity |  | Freq. | Acceptance Criteria |  | Ref Docs, | Method | Type | Resp. | Comments | Client | Applied | Date
1 | Check for current drawings |  |  | Current "For Construction" drawings utilised: |  | Approved Const. Drawings | Confirm current drawings in use | WP | Applied
TNA/350/A2
TNA/365/2
TNA/301/H.1
2 | Setting out |  |  | Surveyor to verify/confirm location |  | Approved Const. Drawings | Survey | WP | Applied
3 | Safety, Traffic & Enviro measures |  |  | Compliance with described measures contained in plans |  | Ops Man Plan | Check and confirm measures | WP | Applied
3 | Excavate foundation |  | Pre concrete pour | Excavate 1800x1800mm. Allow 100mm for blinding and 300mm thick slab |  | Approved Const. Drawings | Confirm depth against approved construction drawings | WP | Applied
4 | Blinding |  | Pre concrete pour | Min. 50mm of 3% cement-stabilised sand |  | Approved Const. Drawings | Confirm depth against approved construction drawings | WP | Applied
5 | Slab reinforcement |  | Pre concrete pour | For slab SL81 mesh top & bottom. N12 U Bars @ 300 CRS |  | Approved Const. Drawings | Confirm REO sizes against approved construction drawings | WP | Applied
6 | Pre Pour Approval |  | Pre concrete pour | Pre pour inspection by Client |  |  | Approval to proceed by Client | HP | Client
7 | Pour Concrete |  |  | Concrete must contain Sika Fibre to comply with IFC drawing (32MPa) |  | Approved Const. Drawing | Visual checks | WP | Applied
8 | Review of As-Built |  |  | Grades, dimensions and thickness recorded on As Built Drawings |  |  | Visual checks | HP | Applied | As built drawings
Legend:
| HP | Hold Point |  | Work will not proceed until released by client,
| WP | Witness Point |  | Work can only proceed after being released by the nominated party,
| TP | Test Point |  | Work can only proceed once the specified test has been undertaken successfully,
Final Inspection:
| Name: | [5 empty] | Position:
| Signature: | [5 empty] | Date: