## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | TNA - ITP - 66KV CB Foundation | itp |  |  |  |  | TNA - ITP - 66KV CB Foundation
section | Details
checkpoint | 1 - Check for current drawings
label | Acceptance Criteria - Current "For Construction" drawings utilised:
label | ○ TNA/350/A2
label | ○ TNA/365/2
label | ○ TNA/301/H.1
label | Ref Docs - Approved Const. Drawings
label | Method - Confirm current drawings in use
label | Type - WP
label | Resp. - Applied
checkpoint | 2 - Setting out
label | Acceptance Criteria - Surveyor to verify/confirm location
label | Ref Docs - Approved Const. Drawings
label | Method - Survey
label | Type - WP
label | Resp. - Applied
checkpoint | 3 - Safety, Traffic & Enviro measures
label | Acceptance Criteria - Compliance with described measures contained in plans
label | Ref Docs - Ops Man Plan
label | Method - Check and confirm measures
label | Type - WP
label | Resp. - Applied
checkpoint | 3 - Excavate foundation
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Excavate 1800x1800mm. Allow 100mm for blinding and 300mm thick slab.
label | Ref Docs - Approved Const. Drawings
label | Method - Confirm depth against approved construction drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 4 - Blinding
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Min. 50mm of 3% cement-stabilised sand
label | Ref Docs - Approved Const. Drawings
label | Method - Confirm depth against approved construction drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 5 - Slab reinforcement
label | Freq. - Pre concrete pour
label | Acceptance Criteria - For slab SL81 mesh top & bottom. N12 U Bars @ 300 CRS
label | Ref Docs - Approved Const. Drawings
label | Method - Confirm REO sizes against approved construction drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 6 - Pre Pour Approval
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Pre pour inspection by Client
label | Method - Approval to proceed by Client
label | Type - HP
label | Resp. - Client
holdpoint | HOLD POINT
checkpoint | 7 - Pour Concrete
label | Acceptance Criteria - Concrete must contain Sika Fibre to comply with IFC drawing (32MPa)
label | Ref Docs - Approved Const. Drawing
label | Method - Visual checks
label | Type - WP
label | Resp. - Applied
checkpoint | 8 - Review of As-Built
label | Acceptance Criteria - Grades, dimensions and thickness recorded on As Built Drawings
label | Method - Visual checks
label | Type - HP
label | Resp. - Applied
label | Comments - As built drawings
holdpoint | HOLD POINT
checkpoint | Final Inspection:
holdpoint | Add Signature:
checklist | TNA - ITP - Typical Pile Foundation F01 - PILES | itp |  |  |  |  | TNA - ITP - Typical Pile Foundation # - REV4
section | Details
checkpoint | 1 - Check for current drawings
label | Acceptance Criteria - Approved IFC Drawings
label | ○ TNA/350/A2
label | ○ TNA/365/2
label | ○ TNA/301/H.1
label | Ref Docs - Approved IFC Drawings
label | Method - Confirm current drawings in use
label | Type - WP
label | Resp. - Applied
checkpoint | 2 - Setting out
label | Acceptance Criteria - Surveyor to verify/confirm location
label | Ref Docs - Approved IFC Drawings
label | Method - Survey
label | Type - WP
label | Resp. - Applied
checkpoint | 3 - Safety, Traffic & Enviro measures
label | Acceptance Criteria - Compliance with described measures contained in plans
label | Ref Docs - Ops Man Plan
label | Method - Check and confirm measures
label | Type - WP
label | Resp. - Applied
checkpoint | 4 - Drill Pile foundation to required depth
label | Acceptance Criteria - Piles drilled to correct depth (750mm dia & min depth 2000mm from FSL). Where rock is encountered before reaching target dept, pile shall be embedded to depth 1 x pile diameter into the bedrock
label | Ref Docs - Approved IFC Drawings
label | Method - Confirm depth against approved IFC drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 5 - PLace the pile cage
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Cages complies with IFC drawings (12-N16, Helix N12 @ 120 (Pitch 1) & 240 (Pitch 2) with 2 additional turns Top, Bottom and 750mm from the bottom)
label | Ref Docs - Approved IFC Drawings
label | Method - Confirm against approved IFC drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 6 - Install Rag bolts
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Rag bolts size, dimensions and alignments are comply with IFC drawings
label | ○ (4-off M30 all thread with 4HDG nuts and 2 washers each) 750 all thread long
label | Ref Docs - Approved IFC Drawings
label | Method - Confirm against approved IFC drawings
label | Type - WP
label | Resp. - Applied
checkpoint | 7 - Pre Pour Approval
label | Freq. - Pre concrete pour
label | Acceptance Criteria - Pre pour inspection by Client
label | Method - Approval to proceed by Client
label | Type - HP
label | Resp. - Client
holdpoint | HOLD POINT
checkpoint | 8 - Pour Concrete
label | Acceptance Criteria - Concrete to comply with IFC drawing (32MPa)
label | Ref Docs - Approved IFC Drawings
label | Method - Visual checks
label | Type - WP
label | Resp. - Applied
checkpoint | 9 - Review of As-Built
label | Acceptance Criteria - Grades, dimensions and thickness recorded on As Built Drawings
label | Method - Visual checks
label | Type - HP
label | Resp. - Applied
label | Resp. - As built drawings
holdpoint | HOLD POINT
checkpoint | Final Inspection:
holdpoint | Add Signature: