## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Awnings & Roofing - GPL-QSE-ITP-FAC 006 (Rev 00) |  | Awnings & Roofing - GPL-QSE-ITP-FAC 006 (Rev 00) | 13f32283-5606-44ec-b40a-67d97f1a1c68
| section | Prior to work
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | All material delivered to site are correct type (colour, thickness, dimensions etc)
| checkpoint | Exclusion zone setup below (if required)
| section | During Works
| checkpoint | Confirm all sub framing as per approved design (spacing, pitch etc)
| checkpoint | Confirm insulation installed as per specification
| checkpoint | All set out and opening sizes for skylights etc correct
| checkpoint | Confirm sheet fixings as per design (i.e. spacing, size, type etc)
| checkpoint | All over flashings and under flashings installed
| checkpoint | All box gutters, sumps and overflows correct size and location
456addb0-e67d-50ed-9308-f9c142fdefe9 | note | Refer Architectural Plans, Elevation, Hydraulic Plans and Shop drawing
| checkpoint | Remove metal filing, off-cuts, dust and other materials which could cause corrosion or blockages
| section | After Works
| checkpoint | Water Test – Hose test entire area for 4hr minimum
ef410b7a-7b2e-5b2a-a926-1d48ce3d8bd4 | note | If failure occurs, rectify issue and retest
| checkpoint | Review to ensure no visible damage or scratches
| checkpoint | Attach subcontractor ITP.
| section | Sign Off
| checkpoint | Orwell Sign Off
cb32fa56-89dc-5745-9efe-ead37be962cc | note | Authorised By: FM
4e0148c2-f0ff-5bf8-931f-889f4b2eedb2 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Balustrades - GPL-QSE-ITP-FAC 005 (Rev 00) |  | Balustrades - GPL-QSE-ITP-FAC 005 (Rev 00) | 616a8aa8-c106-442e-98e9-41c115de2a58
| section | Prior to work
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Waterproof membrane laid and dry prior to install
| checkpoint | All site measures for opening sizes complete prior to manufacture
72138334-9f2e-54cb-8f83-3961b591347c | note | Refer Architectural Clear Opening drawing
| checkpoint | Confirm rebate/hob RL and position correct if required.
| checkpoint | Confirm all balustrades delivered to site are correct type (colour, glass thickness, frame dimensions etc)
| checkpoint | Confirm revised access strategy to/from balcony/scaffold prior to commencing works
| section | During to work
| checkpoint | Confirm base channel fixings have been installed to specified (i.e. spacing, size and embedment of fixing)
| checkpoint | Confirm that adjoining balustrades have common level or line.
| checkpoint | Confirm height of balustrade 1000mm minimum from FFL
| checkpoint | Confirm 125mm maximum distance between end posts and adj walls
| checkpoint | Confirm no foot hold between 150mm and 760mm from FFL
| section | After Work
| checkpoint | Review balustrades to ensure no visible damage or scratches
| checkpoint | All balustrades clean and protection removed
| checkpoint | Attach subcontractor ITP.
| section | Sign Offs
| checkpoint | Orwell Sign Off
bf8d4dd8-0ad0-5447-86b3-b2d837899361 | note | Authorised By: FM
98e8aa29-1608-5618-9630-843100e6f736 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Capping Beam - GPL-QSE-ITP-STRUC-002 (Rev 00) |  | Capping Beam - GPL-QSE-ITP-STRUC-002 (Rev 00) | 4bc21163-5da0-4b8c-b38e-c5feb945f65a
| section | Prior to Works
| checkpoint | Attach markup plan of capping beam covered by this ITP
| checkpoint | Confirm excavation for capping beam has been complete
| checkpoint | Confirm top of piles are clean and free of debris and starter bar detail correct
| checkpoint | Confirm set-out and RL of capping beam has been completed (attached survey plan)
11bdc87d-9697-5f6f-8ede-49fc0e684d2c | note | Refer Architectural concrete outline
| checkpoint | Confirm MPa, slump and agg size of concrete
cc88fe80-7dc4-50a6-8a9a-f61fb19ed1e7 | textbox | MPa:
28b8d563-a488-5c79-958b-f2a3f4ed0250 | textbox | Slump:
fe2b8b57-2482-5eb3-8920-4b9266746509 | textbox | Agg:
| checkpoint | Check quantity of concrete required prior to ordering
355b991e-80d5-5e13-97d7-29eafc5d352a | textbox | m3:
| section | During Works
| checkpoint | Confirm formwork shutters are clean and will provide required class finish
| checkpoint | Attach Formworkers ITP
| checkpoint | Attach Formwork Engineer sign off certificate confirming compliance with design & AS3610
| checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
| checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report and confirm all actions are closed out
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Attach Concreter ITP
| section | After Works
| checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
| checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
82d3c6bb-5e4c-5456-83f1-0ed5f2ba3b48 | note | If not undertake rectification works
| checkpoint | Obtain as-built survey (attach survey)
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
a8e96d0e-916c-5a27-9657-7aa95786649d | tickbox | 6mm +/- from design RL
5ffbc88c-e42e-5e8a-970d-48454ad4d448 | tickbox | 10mm +/- from design position
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
9c5b7982-6082-5933-baa3-92b5241ae1b2 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
1af2b61e-312b-5053-8ee4-9cc68c58cdab | textbox | Test Strength MPa
| section | Sign Off
| checkpoint | Orwell Sign Off
9b9d1645-d540-500b-b201-2a6207d26f63 | note | Authorised By: FM
5a9e1789-31e1-552f-8f5b-c4c3e8e149de | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00) |  | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00) | 633d3d07-877d-4c3d-9281-fa52921a253f
| section | Prior to Works
| checkpoint | Attach markup plan of area/unit covered by this ITP
| section | During Works
| checkpoint | Confirm light layout and switching as per the design
6444b065-e1e5-53c6-9d19-93573743cc0d | note | Refer Architectural RCP NOT Electrical Plan
| checkpoint | Confirm height and location of the following
63411d3e-f1f3-5847-8f1d-58fdd800e076 | textbox | Internal GPOs, TV & data
48b90bc7-c3ad-5f67-85d3-d3d846735fd7 | textbox | Fridge/Freezer GPO
182b5748-5dd3-5c71-bc01-b908096fdc01 | textbox | Kitchen GPOs
b9b4be40-3a59-58cb-a3f7-cd8bc83fa7fe | textbox | Bathroom GPO
28700b60-2738-5ab7-afc6-c57b86111e1b | textbox | Security Intercom
90d8d4d4-cf80-54ac-8021-eb062cc89aad | textbox | External GPO
b2d3b177-8056-5e2d-9cd2-8996e014f216 | note | Refer Architectural Set-out NOT Electrical Plan
| checkpoint | Confirm GPO locations for OTHER (i.e. fans, FCUs, blinds, etc)
| checkpoint | Confirm NBN conduit and draw wire
| checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
e53f0821-377e-54a9-b6c0-0bff00c8928f | note | Authorised By: FM
159f791d-c035-5fc1-91d0-fb5502c77e68 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Excavation - GPL-QSE-ITP-STRUC-003 (Rev 00) |  | Excavation - GPL-QSE-ITP-STRUC-003 (Rev 00) | 4d0f40ef-b2e8-45a5-8788-402591ac83cd
| section | Prior to Works
| checkpoint | Attach markup plan of extent of excavation covered by this ITP
| checkpoint | Confirm Dial-Before-You-Dig has been received (attach plans)
d08559c8-67e0-5db2-b0f9-3d98ff8b48d2 | note | Any services in close proximity to be sprayed/pegged out
| checkpoint | Confirm existing service scan has been completed (attach survey report)
| checkpoint | Confirm if any hand digging excavation is required close to underground services
| checkpoint | Confirm set-out of site boundary, excavation line and RL datum (attach survey plan)
| checkpoint | Confirm existing water table RL
| checkpoint | Confirm dewatering requirements & methodology (if required)
| checkpoint | Obtain approval for temporary anchors outside the site boundary (if required)
18b2856a-9a94-52e7-a946-840435b73ca7 | note | Refer Architectural set out drawings
| checkpoint | Confirm vibration limits and monitoring requirements
| checkpoint | Confirm noise limits and monitoring requirements
| checkpoint | Confirm working hours and equipment limitations
| checkpoint | Confirm soil testing has been undertaken and tipping classification report received (attach report)
| section | During Works
| checkpoint | Collection of tip dockets if required
| checkpoint | Confirm progressive set out of basement line (typically at 3m drops - attach survey plans)
| checkpoint | Confirm progressive Geotech inspections (typically at 3m drops - attach report and associated closeouts)
| checkpoint | Confirm anchor set out and type (if required)
| checkpoint | Confirm anchor depth and angle (if required)
| checkpoint | Confirm anchor grout strength prior to stressing (if required)
| checkpoint | Confirm dowel and reo detail to shotcrete (if required)
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm thickness and finish to shotcrete is as per design
| checkpoint | Confirm RL at bulk excavation level
| checkpoint | Geotech inspection and bearing capacity at bulk excavation level
| checkpoint | Confirm subbase is compliant with engineers requirements
| checkpoint | Civil/Structural Engineer inspection
| section | After Works
| checkpoint | Attach Subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
045e9991-4bad-56b0-b43f-afc75486533f | note | Authorised By: FM
84a3cd4a-4b66-58c8-bfc6-22c373ee9cbb | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | External Masonry - GPL-QSE-ITP-FAC-002 (Rev 00) |  | External Masonry - GPL-QSE-ITP-FAC-002 (Rev 00) | 47a42f3d-d1e4-469e-a41a-846640eb2e01
| section | Prior to Works Commencing
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Confirm wall set-out as per Architectural Drawings
| checkpoint | Confirm that all penetrations as required for services are identified and marked (i.e. mechanical, electrical, fire, hydraulic, etc)
| checkpoint | Confirm requirement for core filling and/or stiffeners
d9444a3f-68f6-5f90-8180-2abb2e277fdc | note | Refer Architectural Wall Set-out drawings and Structural Engineer Masonry Details
| checkpoint | Confirm vermin/insect/ fire protection requirements are compiled to for all masonry sundries (i.e. stainless steel weep hole cassettes, cavity mesh, brick ties, etc)
| checkpoint | Confirm FRL’s and that bricks/blocks will achieve requirements as per specs and relevant fire reports
162c07d3-07b0-5f9d-899a-d3f14883388b | note | Refer Architectural Fire Line drawings
| checkpoint | Confirm bricks/blocks are correct manufacturer, colour and size as per drawings, specs and finishes schedules
| checkpoint | Confirm brick laying pattern (i.e. stretcher bond, stack bond etc) is as per drawings, specs and finishes schedules
| checkpoint | Confirm face brick set out point and RL is as per architectural drawings
| checkpoint | Confirm any specific architectural details (capping's, header courses, etc) are as per architectural drawings
| checkpoint | Confirm mortar and caulking colours are as per specs and finishes schedules
| section | During Works
| checkpoint | Confirm shelf angles are installed as per installation guideline (i.e. spacing, size and embedment of fixing)
| checkpoint | Confirm shelf angle RL’s is correct relative to brick gauge requirement
| checkpoint | All damp proof course and flashings built in
| checkpoint | Ensure weep holes are installed at correct centres
| checkpoint | Confirm that ties and stiffeners are installed at correct centres
60bf5248-f3dc-5ac5-a37c-5069dfc44af1 | note | Refer Structural Engineer Masonry Details
| checkpoint | All cavities clean and clear
fa3c411a-1284-558e-a387-5abac617beca | note | Ensure all damp proof courses/flashings are free of damage and clean and weep holes unblocked (photo evidence)
| checkpoint | Ensure all courses are laid level, all joint sizes are consistent and ironed correctly
| checkpoint | Check verticality between panels and that no steps in face work are present
| checkpoint | Inspect all joints are caulked where required and colour is correct as spec’d
| section | After Works
| checkpoint | Check no chips in bricks/blocks are visible
| checkpoint | Final brick/block clean
31fd1d98-c611-5f8f-b9c0-6735eb535023 | note | Confirm cleaning method complies to manufacturers specs
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
6f35373f-50e6-5ad6-8d1d-9f996af4a8c5 | note | Authorised By: FM
9b3f7feb-8b6a-5157-a9df-f74383a87298 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | External Waterproofing - GPL-QSE-ITP-FAC 007 (Rev 00) |  | External Waterproofing - GPL-QSE-ITP-FAC 007 (Rev 00) | b7dc0d3d-1bbe-4d71-8830-d41faebee156
| section | Prior to Works Commencing
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Floor wastes are flush, free of waste material and in correct location
| checkpoint | Water Test - Confirm concrete has structurally fall to floor wastes
e443fbaf-4ec8-58a3-bdfd-28a31640d4d9 | note | If ponding occurs, top area and retest
| checkpoint | Confirm no ponding of water by completing water testing to slab
| checkpoint | Confirm all concrete defects have been actioned and surface inspected/accepted by subcontractor
| section | During Works
| checkpoint | Confirm product used is as per design
32f51080-d8e2-5f2a-910f-82b6644dc834 | note | Refer Architectural Waterproofing drawing
| checkpoint | Confirm minimum lap (150mm min typical), upturn (150mm min typical) etc dimensions are achieved
| checkpoint | Base membrane inspected for imperfections
| checkpoint | Top membrane inspected for imperfections
| checkpoint | Confirm all penetrations through planter box walls are sealed
| section | After Works
| checkpoint | Spark Test - Subcontractor undertake spark test after minimum drying time
2a635a91-8443-516f-aea4-2d382e06a51c | note | If pinholes failure occurs, rectify issue and retest
| checkpoint | Flood Test - Subcontractor block floors waste and fill water to height of overflow for min 24 hours
c95edb1a-c3a7-5ec5-a061-670b21e8a217 | note | If failure occurs, rectify issue and retest
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
79b9c69a-5162-5e2e-a5ae-a488c76a45b0 | note | Authorised By: FM
13c9d6da-fe39-5e0e-baaf-626140933114 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Façade Cladding - GPL-QSE-ITP-FAC 008 (Rev 00) |  | Façade Cladding - GPL-QSE-ITP-FAC 008 (Rev 00) | 97c98a05-2a35-43dc-b172-8f819b09178a
| section | Prior to work
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Confirm structural supports and openings are as per design
e9c1350d-a914-572e-8175-44d6deb4dfd0 | note | Refer Architectural Plans, Elevation and Shop drawing
| checkpoint | Confirm all required waterproofing to substrate has been completed
| checkpoint | All material delivered to site are correct (size, thickness, fixing detail, as per approved sample etc)
daf84c5e-5d78-52a3-9345-1d8922535428 | textbox | Confirming fixing methodology (exposed/internal/recessed):
| section | During to work
| checkpoint | Confirm cavity set out as per design
ee912ae2-fd12-5086-b7d1-3826f77c9336 | note | Refer Shop drawing
| checkpoint | Confirm sarking has been installed correctly (i.e. overlap, taping of edges)
| checkpoint | Confirm fixings have been installed to specified (i.e. spacing, size)
| checkpoint | Confirm joints are consistent, as per design and at correct RL & spacing
d9ae8586-775b-5ae2-b238-11d30c02ecac | note | Refer Shop drawing
| section | After works
| checkpoint | Review cladding to ensure no visible damage or scratches
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
3009f4ed-3718-5b4c-aedd-d9ceddf4cc97 | note | Authorised By: DL
c51d7ba2-a92b-5d61-84ff-969c853e2496 | note | Issue Date: 12.05.2023
| signoff | Request Sign Off
| checklist | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00) |  | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00) | 6e86a6ce-333d-41a5-b7ee-f169a41e6b1e
| section | Prior to Works
| checkpoint | Attach markup plan of area/unit covered by this ITP
| section | During Works
| checkpoint | Confirm sprinkler pipework installed as per drawings
| checkpoint | Confirm sprinkler heads have been installed as per architectural RCP layout
| checkpoint | Confirm any drenchers required have been installed
| checkpoint | Confirm red cabling installed for fire electrical speakers and detectors
| checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
| checkpoint | Confirm pipework pressure test has been undertaken
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
07c661a7-798f-5906-8ea3-9218aa194c8b | note | Authorised By: FM
036d2b01-fd52-5970-a0b5-9b94b1854c94 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00) |  | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00) | b5313775-969a-4d35-954a-230edaf80805
| section | Prior to Works
| checkpoint | Attach markup plan of footings & bases covered by this ITP
| checkpoint | Confirm set-out of footings & bases has been completed (attach survey plan)
25c8f938-9f85-550f-bce7-bd420642d876 | note | Refer Architectural footing plan
| checkpoint | Confirm RL of underside of footing & bases
| checkpoint | Geotech inspection and bearing capacity of base
| checkpoint | Confirm MPa, slump and agg size of concrete
7b83b84e-851b-5c4c-8244-75da5cd09638 | textbox | MPa:
257da05c-08f8-5753-ab5f-f57ed5f679dc | textbox | Slump:
035af793-c15e-5660-b769-89e3f6c701e1 | textbox | Agg:
| checkpoint | Check quantity of concrete required prior to ordering
f6018920-d813-5ed7-aa4a-e3c49b51a88c | textbox | m3:
| section | During Works
| checkpoint | Confirm waterproofing product and detail is installed as per design (if required)
5eaad204-76b3-51b7-9191-9b8f72396fe6 | note | Refer Architectural waterproofing drawing
| checkpoint | Attach Waterproofers ITP
| checkpoint | Confirm lightning protection installed to footings as per Electricians requirements
| checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
| checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
| checkpoint | Attach Formworkers ITP
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report and confirm all actions are closed out
| checkpoint | Confirm Private Certifier inspection of building foundations completed
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Attach Concreter ITP
| section | After Works
| checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
| checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
147b2867-553b-58c4-abf1-06682cc5e0c3 | note | If not undertake rectification works
| checkpoint | Obtain as-built survey (attach survey)
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
8bc2e0aa-57b4-5c21-af5c-c018bf25014f | tickbox | 6mm +/- from design RL
dc6826e0-ce0d-5736-8a0b-7aebe1e4ddc5 | tickbox | 10mm +/- from design position
| checkpoint | Obtain all concrete tests at 4 days, and attach test results
77a73a4c-9068-5df1-a3a5-ae99cdf64db9 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
d0fb4e61-8a34-5a7d-a86e-3885a2a4c350 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
d97d3647-ae3b-58f9-a23d-6801c867c3cf | textbox | Test Strength MPa
| section | Sign Off
| checkpoint | Orwell Sign Off
00e6c33b-31cd-5220-bf96-14a733a65e00 | note | Authorised By: FM
c1c22125-6d8a-5877-86e7-ba9a8b706706 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Hebel - GPL-QSE-ITP-FIT-001 (Rev00) |  | Hebel - GPL-QSE-ITP-FIT-001 (Rev00) | ca446d14-ddb7-471a-830c-4cc13dd9adb0
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Confirm safe Hebel cutting area and control measures are in place
| section | During Works
| checkpoint | Confirm correct head track used (Slotted angle top track to be used when < 3200mm, standard U deflection top track to be used when > 3200mm)
| checkpoint | Confirm base angle has been fixed to slab at a maximum of 600mm spacings
| checkpoint | Confirm panels do not straddle
| checkpoint | Confirm that Hebel Mortar has been used at base of panels
| checkpoint | Confirm Hebel Panel has been fixed to base angle with hex head screw 50mm from each corner
| checkpoint | Confirm Hebel Panel has been fixed to head track at 900mm spacing and middle of slotted hole where applicable
| checkpoint | Confirm that a maximum of 15mm spacing have been left between top of panel and concrete soffit
| checkpoint | Confirm head has been caulked at junction with concrete soffit with Intumescent & Acoustic Sealant on both sides, ore one side where slotted angle track used
| checkpoint | Ensure that backing rod is used behind Intumescent & Acoustic Sealant.
| checkpoint | Confirm that Hebel Power Panels are glued edge to edge with Hebel adhesive.
| checkpoint | Confirm all fire door frames fixed to Hebel wall panels are filled with TRCO FYREFLEX.
| checkpoint | Confirm that any panel to panel junction detail must be fastened together by thread screw at 900mm maximum centres and be a maximum of 100mm from the panel end.
| checkpoint | Ensure that any exposed cut reinforcement has been coated with the Hebel anti-corrosion protection paint.
| checkpoint | Attach CSR Inspection Report, and confirm that all actions are closed out
| section | After Works
| checkpoint | Review panels to ensure no visible damage/cracks/peons
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
ebb97540-0016-5fc2-825d-5d5a37f30bde | note | Authorised By: FM
c09eebda-05c4-5da2-a54a-99deb748364e | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00) |  | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00) | d3eb0c4c-2df2-4473-af97-25e7127d32fc
| section | Prior to Works
| checkpoint | Attach markup plan of area/unit covered by this ITP
| section | Stacks and Underslung
| checkpoint | Fire collars inspected prior to works. If cast-in, all grout removed, no honeycombing etc. If retrofit, correct number of screws used etc.
| checkpoint | No part of fire collar covered (i.e. painted or Hebel head track etc)
| checkpoint | Underslung PVC pipe installed as per design location. If not, mark up sent to record 'as-built'
7a54c8ce-5c4f-5169-ab3f-2fc13fe00143 | note | Refer Hydraulic drainage plan
| checkpoint | Underslung PVC pipes and traps invert level all contained inside ceiling void
a38e5939-bf38-5db1-8f98-fc8bb86d9926 | note | Refer Architectural RCP
| checkpoint | IO's installed as per design and at change of directions
| checkpoint | All PVC pipe work acoustically lagged and wrapped as required
1e08cade-6a37-5899-a3de-da56322e1c00 | note | Refer Acoustic Report
| checkpoint | Confirm PVC pipes are not bridging against metal studs (Minimum 5mm clearance is required after lagging)
| section | Rough-in
| checkpoint | Confirm rough-in location to kitchen water and gas as per kitchen shop drawing
| checkpoint | Confirm rough-in location of wet area as per design
| checkpoint | Confirm rough-in heights of wet area as per design
442e22b1-fd07-5183-b882-7ef95b09ec2c | textbox | Shower head, mixer, diverter
516d8048-3aca-5730-91b8-0d6e2b77bf2b | textbox | Bath spout, mixer
a3ecc25c-8b32-5113-895d-5239712ca646 | textbox | Basin spout, mixer, waste
| checkpoint | Confirm inbuilt cistern location and framing
| checkpoint | Confirm A/C tundish location
| checkpoint | PEX pipes clipped at required centres (horizontal 600mm, vertical 1200mm) and rubber grommets fitted where running through studs.
| checkpoint | Confirm following test been undertaken (attached sign off)
451540e8-d14e-563e-930e-27b3dfc902dd | tickbox | Pressure test for water and gas
a3b4b533-f421-5d15-aa46-726144b92141 | tickbox | Drainage pipework
| checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
ae53f360-b3ac-5ee1-9e15-bc4cbb39f8ff | note | Authorised By: FM
345d2b96-7a33-57a8-8e15-11b20f2bff0e | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00) |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00) | e4f03612-1a86-467b-9733-a088a3f89aab
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Confirm surveyor 1m mark and gridlines installed
| checkpoint | Confirm wall set-out correct
eee35d75-7099-594b-a5d2-51ec1d739cdb | note | Refer Architectural Wall Partition Set-Out drawing
| checkpoint | Confirm that all penetrations as required for services are identified and marked (i.e. mechanical, electrical, fire, hydraulic, etc)
| checkpoint | Confirm requirement for core filling and/or stiffeners
9b66006a-b60b-53d2-9496-af2801c6aaf4 | note | Refer Architectural Wall Set-out drawings and Structural Engineer Masonry Details
| checkpoint | Confirm FRL’s and that bricks/blocks will achieve requirements as per specs and relevant fire reports
42e1f859-6e34-5934-8da2-e4a6b2781d7d | note | Refer Architectural Fire Line drawings
| checkpoint | Confirm bricks/blocks are correct manufacturer, colour and size as per drawings, specs and finishes schedules
| checkpoint | Confirm brick laying pattern (i.e. stretcher bond, stack bond etc) is as per drawings, specs and finishes schedules
| checkpoint | Confirm mortar and caulking colours are as per specs and finishes schedules
| section | During Works
| checkpoint | Confirm that ties and stiffeners are installed at correct centres
af86d2a2-92d1-5f37-b880-c43c3dd1b114 | note | Refer Structural Engineer Masonry Details
| checkpoint | All cavities clean and clear
| checkpoint | Ensure all courses are laid level, all joint sizes are consistent and ironed correctly
| checkpoint | Check verticality between panels and that no steps in face work are present
| checkpoint | Inspect all joints are caulked where required and colour is correct as spec’d
| section | After Works
| checkpoint | Check no chips in bricks/blocks are visible
| checkpoint | Final brick/block clean
8de44657-e9eb-53ed-a7e6-87c96e090976 | note | Confirm cleaning method complies to manufacturers specs
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
be1cd67d-e864-5c41-9b27-7c47711d3d1b | note | Authorised By: FM
9d7a2c4c-2a46-5227-992b-65c4b3473ff9 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00) |  | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00) | 70bed7ee-030c-472a-94cc-c7d5d3b5f3b1
| section | Prior to Works Commencing
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Floor wastes are flush, free of waste material and in correct location
| checkpoint | Water Test - Confirm concrete has structurally fall to floor wastes
ea48de28-f279-5e15-aa12-c6c32d3b3b2a | note | If ponding occurs, top area and retest
| checkpoint | Confirm no ponding of water by completing water testing to slab
| checkpoint | Confirm all concrete defects have been actioned and surface inspected/accepted by subcontractor
| checkpoint | Confirm position and RL of waterproofing angles
| section | During Works
| checkpoint | Confirm product used is as per design
703eab60-192d-5477-af90-01a8713aed75 | note | Refer Architectural Waterproofing drawing
| checkpoint | Sealant at wall/floor junction and wall/wall junction inspected for imperfections
| checkpoint | Confirm minimum lap (150mm min typical), upturn (150mm min typical) etc dimensions are achieved
| checkpoint | Base membrane inspected for imperfections
| checkpoint | Top membrane inspected for imperfections
| checkpoint | Confirm exposed aluminium angles are not membrane over
| checkpoint | Confirm waterproofing complete around all PC penetrations (i.e. mixer, spouts, shower head etc.)
| section | After Works
| checkpoint | Confirm no pinholes with detector after minimum drying time 24 hours
| checkpoint | Flood Test - Subcontractor block floors waste and fill water to height of overflow for min 24 hours
1abb4fd7-9e14-5af6-96b5-efc5764c629f | note | If failure occurs, rectify issue and retest
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
6e966a8f-76a8-5b05-b3d4-fc0cc560f077 | note | Authorised By: FM
6831b6c5-bf97-53b1-b6aa-e3a2c717d276 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00) |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00) | 81ca3d9d-cf43-4edb-845a-15dfe7e2b0bb
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Confirm structural opening for louvres is as per design
07f95f14-89b9-5387-83ea-917741d083d7 | note | Refer Architectural Elevation and Shop drawing
| checkpoint | All louvers delivered to site are correct type (colour, blade angle/dimensions, function etc)
adb9b47f-093f-56fc-bf9b-0bf198054de6 | note | Refer Architectural/Façade Spec and Shop drawing
| checkpoint | Confirm fixing detail back to main structure (i.e. any additional structural framing required)
16f67342-9122-56b3-9553-120ddd94ec05 | note | Refer Architectural and Shop drawing
| section | During Works
| checkpoint | Confirm louvre fixings are correct centres and type (i.e. material, diameter and embedment)
13bba943-273c-51ef-8bd8-d7935232ac32 | note | Refer Shop drawing
| checkpoint | Confirm louvres in correct location on façade, installed true and plumb
| checkpoint | Confirm any caulking and sealing completed on louvres/brackets
| section | After Works
| checkpoint | Review louvers to ensure no visible damage or scratches
| checkpoint | All louvers clean and protection removed
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
3b534722-7a7c-5665-abc8-905f01bea348 | note | Authorised By: FM
98684b53-4327-5f9a-a337-20f9e6ac4e12 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00) |  | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00) | 6209d2d6-34f2-4311-9588-d79e3f08b193
| section | Prior to Works
| checkpoint | Attach markup plan of area/unit covered by this ITP
| section | During Works
| checkpoint | Confirm FCU and Fan location as per the design and ceiling access panel will work for servicing (i.e. back left hand side of FCU, directly under fan)
d198004e-2233-5624-8269-3eac57c228f5 | note | Refer Architectural RCP for Access Panel location
| checkpoint | Confirm FCUs and Fans are vibration isolated from soffit with in shear rubber mounts
| checkpoint | Confirm minimum 100mm clearance behind FCU for return air path
| checkpoint | Confirm all flexible and sheet metal ducting has been installed as per drawings
| checkpoint | Confirm sealing of flexible connections between kitchen/ toilet exhaust fan and metal ducting (mechanically fixed required)
| checkpoint | Confirm flexible ductwork is not crushed, torn or damaged at any point
| checkpoint | Confirm wiring of AC controls are located as per architectural set-out
| checkpoint | Confirm all refrigerant pipes have been installed, pressure tested and insulated
| checkpoint | Confirm all condensate drains have been installed back to tundish and tested for falls
| checkpoint | Confirm all above ceiling air paths are maintained as per design
| checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
68aae7c3-5f29-51c2-8aa0-c5b1a9bdc01a | note | Authorised By: FM
dd5ab7cb-868d-59ed-b01a-922c183a3523 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Piling - GPL-QSE-ITP-STRUC-001 (Rev 00) |  | Piling - GPL-QSE-ITP-STRUC-001 (Rev 00) | e6666571-978f-4c55-842f-f14520e92804
| section | Prior to Works
| checkpoint | Attach markup plan of piles covered by this ITP
| checkpoint | Confirm Dial-Before-You-Dig has been received (attach plans)
603b3777-6004-548d-a477-ef9978f2dd6f | note | Any services in close proximity to be sprayed/pegged out
| checkpoint | Confirm existing service scan has been completed (attach survey report)
| checkpoint | Obtain certification for the piling mat from Geotech (attach certificate)
| checkpoint | Confirm vibration limits and monitoring requirements
| checkpoint | Confirm RL’s of top of piles
| checkpoint | Confirm set-out of piles and/or recovery marks has been completed (attach survey plan)
104008b5-1441-5727-affe-a05c94705adf | note | Refer Architectural footing plan
| checkpoint | Confirm MPa, slump and agg size of concrete
b32d9bf0-d9ce-535c-ba16-57d3a6a18690 | textbox | MPa:
7b9cf046-a314-5cb7-afa1-40293b14fb18 | textbox | Slump:
43d62bfa-ad87-5db8-bf4a-7995b21b57f7 | textbox | Agg:
| checkpoint | Ensure that adequate exclusion zones are setup during piling operations as per SWMS
| section | During Works
| checkpoint | Confirm pile diameters are correct as per plan
147d2812-c7ed-5be3-a5d0-cfa50e48b49d | note | Refer Structural Engineer footing plan
| checkpoint | Confirm pile cages installed are correct as per design
a402727a-43be-565d-8a51-4b96d81b6d28 | note | Refer Structural Engineer pile details
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Ensure reo cage has sufficient cover and starter bars are of sufficient length
26404f6a-d93d-5d5a-9b6f-03bd6b975f7f | note | Refer Structural Engineer pile details
| section | After Works
| checkpoint | Obtain as-built survey of piling positions and top of piles RL (attach survey)
| checkpoint | Confirm tolerance of piles are as follows:
e7fb80e6-d283-5079-a472-6575245fa5c7 | tickbox | 10mm +/- from design RL
66f8a2bc-ef6b-53a2-a82f-a4ddbb0374f8 | tickbox | 25mm +/- from design position
| checkpoint | Obtain 7 day concrete crush tests results (attach)
9cc46fa7-60ff-55aa-824b-96fabb06a612 | textbox | Test Strength MPa
| checkpoint | Obtain 28 day concrete crush tests results (attach)
85b311f1-4402-5418-914c-d8d8d11e93ab | textbox | Test Strength MPa
| checkpoint | Attach Piling Subcontractor ITP
| section | Sign-Off
| checkpoint | Orwell Sign Off
b1085774-e78b-5109-9e41-5ae7e9a4654a | note | Authorised By: FM
2e5facf8-d436-5489-93bd-886749793a07 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00) |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00) | 52864f0c-8825-4f63-9358-6916feae87a5
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Confirm surveyor 1m mark and gridlines installed
| checkpoint | Attach Acoustic Consultant Inspection Report, and confirm that all actions are closed out
| checkpoint | Attach Fire Penetration Inspection Report, and confirm that all actions are closed out
| section | During Works
| checkpoint | Confirm ceiling framing flat and at correct RL to achieve FTC height
| checkpoint | Confirm ceiling framing bulkheads are square and level
| checkpoint | Confirm ceiling interface with door frames correct
| checkpoint | Confirm access panel set-out correct and AC equipment, fire dampers etc are accessible
06d097bf-b62d-5d70-8022-9d8cfd4c95ef | note | Refer Architectural RCP drawing
| checkpoint | Confirm all noggins are installed
1c4b386d-a83d-5b20-ac64-59ebf6aaf3ce | tickbox | Blind Pelmets
4d2ee745-5aeb-5602-be89-a283173fa6da | tickbox | Ceiling Fans
2153e2b6-a3fc-5d89-ab8b-422c43d9c554 | tickbox | Pivot Doors
| checkpoint | Confirm all grill inserts are installed to bulkhead framing (where applicable)
| checkpoint | Confirm ceiling insulation complete (where applicable)
| checkpoint | Confirm ceiling framing do not clash with other services (e.g. downlights, access panels, mechanical exhaust, sprinkler heads)
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
db0160a0-dd93-5c00-b947-bada6df2543e | note | Authorised By: FM
9bd831c6-66f0-5c5f-bac4-f68bb61c1726 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00) |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00) | 447fabd9-0dc3-48f6-b08c-bb578a1e9008
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Confirm surveyor 1m mark and gridlines installed
| section | During Framing Works
| checkpoint | Confirm wall set-out correct
7302fa28-8982-5038-a1e0-4431ecbd287f | note | Refer Architectural Wall Partition and Wall Type drawing
| checkpoint | Confirm framing gauge and stud spacing to external walls as per design
71cd5694-ae08-56da-bf8a-90a77fd886de | note | Refer CSR or similar facade stud design
| checkpoint | Confirm framing is straight and plumb
| checkpoint | Confirm door frames are correct RL, plumb and installed at correct orientation
| checkpoint | Confirm corners are square (notably wet areas)
| checkpoint | Confirm minimum cavities achieved between Hebel and stud
b8246d4a-97cc-5410-8c4e-eb0083379909 | note | Refer Acoustic reports
| checkpoint | Confirm that joinery openings are correct
| checkpoint | Confirm all noggins are installed
a390d65f-d335-5e46-be56-d770f94de726 | tickbox | Bathroom Accessories and Grab Rails
19190c50-e900-5380-a58a-4a4f5538d9a3 | tickbox | Bathroom Vanities and Shavers
f487dd4f-b716-555b-aa4e-f41adacd7c65 | tickbox | Kitchen Joinery
50931e0c-0dda-5c44-816c-7dbf8525c508 | tickbox | Laundry Washer/Dryers
f7bc08fb-2881-537d-bb6e-c27adb65cf08 | tickbox | Wall-fixed Joinery etc
| section | During Sheeting Works
| checkpoint | Confirm all service ITPs have been received
| checkpoint | Attach Fire Penetration Inspection Report, and confirm that all actions are closed out
| checkpoint | Confirm acoustic and thermal insulation installed
b290b66c-790c-50c3-a39f-6d9ecb581077 | note | Refer Acoustic and Section J reports
| checkpoint | Confirm correct board type has been used (FC, Blue Board, Aqua check etc)
| checkpoint | Confirm sheeting to intertenancy and wet areas are full height and sealed to concrete soffit on both sides of wall (or as required)
4cde5489-1d9b-5fa9-bff6-830276d44493 | note | Refer Acoustic reports
| checkpoint | Confirm all penetrations through wet area walls adjacent to habitable rooms are sealed and caulked
| checkpoint | Confirm skirting fixed level and at correct RL at joinery/window interfaces
| section | After Works
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
e09f465e-cdf3-5829-ab19-dbeb0f8e2c4d | note | Authorised By: FM
4ad2a07e-782c-534e-925f-6b77e12db0b3 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Precast GPL-QSE-ITP-STRUC-09(Rev00) |  | Precast GPL-QSE-ITP-STRUC-09(Rev00) | f741fca6-381c-4e48-9820-fdbc7d8fa50f
| section | Prior to Works
| checkpoint | Confirm set-out of grids, verticals, RL on slab below (attach survey plan)
ff965c4d-fe99-5725-a0c6-8383286d7fab | note | Refer Architectural Concrete Outline
| checkpoint | Attach manufacturer ITP for panels
| checkpoint | Attach Principal Structural Engineer review and acceptance of ITP
| checkpoint | Confirm cast-in dowel & starter bars are correct & verified against structural drawings
| checkpoint | Confirm that minimum concrete slab strength (typically 20mPa) has been reached for temporary bracing install
| checkpoint | Attach manufacturer Design Certificate for panels
| checkpoint | Confirm that exclusion zones are set up prior to lifting
| checkpoint | Confirm all precast panels have been inspected for damage prior to lifting off truck
| section | During Works
| checkpoint | Confirm panels are installed in correct & final position. Check alignment with adjacent elements
| checkpoint | Confirm bracing installed as per design
86044fa6-9eac-5998-8a09-9b6b274e3f2d | note | Refer Precast shop drawing
| checkpoint | Attach Precast installation certificate
| section | After Works
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
87dedd65-34d2-5d47-8d42-0d44e6e54f2b | tickbox | 6mm +/- from design RL
7f40c6a5-f082-5049-b16e-bd88b04d9da2 | tickbox | 6mm +/- from 3m straight edges
| section | Sign Offs
| checkpoint | Orwell Sign Off
59665a90-a753-51ba-88f8-2984ae22d083 | note | Authorised By: FM
8d7509de-fed0-582f-8a9b-531625fc936f | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Sandwich Panels - GPL-QSE-ITP-FIT-011 (Rev00) |  | Sandwich Panels - GPL-QSE-ITP-FIT-011 (Rev00) | 1e132df7-b2c1-4ab2-85e2-b86847a829eb
| section | Prior to Works
| checkpoint | Attach sandwich panel manufacturer ITP
| checkpoint | Sandwich panel material certification from supplier
| checkpoint | Collate individual dockets for facility validation
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
4e0c3763-e759-53b3-9b0f-07bcbc5d7ab4 | textbox | Confirm joint direction (horizontal/vertical):
8a545472-1181-5d34-998f-5565805efd12 | textbox | Confirm installation methodology (panel lifting tool/craneage/etc):
| checkpoint | All panels delivered to site are correct (size, thickness, openings)
5e8fefcf-4952-579e-b9a3-9b770436f63c | note | Refer Shop Drawings
| section | During Works
| checkpoint | Confirm correct head track and bottom plinth
| checkpoint | Confirming spacing of fixings
| checkpoint | Confirm bottom U channel and horizontal insulation installed
| checkpoint | Confirm sealing tape and/or flashing installed
| checkpoint | Check for panel alignment, joints, interfaces, sealing
| checkpoint | Confirm perimeter ceiling track installed
| checkpoint | Confirm insulation installed at perimeter
| checkpoint | Confirm ceiling panel supports & spacing
e9004625-6d86-57fb-b026-e5bae5e504d2 | tickbox | Confirm ceiling panels are complete & OK for foot traffic
| checkpoint | Confirm sealing works are completed correctly
| checkpoint | Attach Cleanroom Consultant Inspection Report, and confirm all actions are closed out
| section | After Works
| checkpoint | Review panels to ensure no visible damage/cracks/misalignments
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
05130fec-8fd9-5b05-b597-e87c78135522 | note | Authorised By: DL
b8fe2c88-8454-5c37-9cbd-0a9b67fdb6ac | note | Issue Date: 12.05.2023
| signoff | Request Sign Off
| checklist | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00) |  | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00) | b2644b3d-002b-4612-af93-d3825a5ce839
| section | Prior to Works
| checkpoint | Confirm RL of bulk excavation
| checkpoint | Confirm RL of bulk slab thickenings
| checkpoint | Confirm set-out of edge boards/set-downs/drains/pits etc (attach survey plan)
237acb6d-7a94-54fc-9fa9-1b646c4b87b0 | note | Refer Architectural concrete outline
| checkpoint | Confirm MPa, slump and agg size of concrete
c3efd361-818b-5d80-bc55-e1a3006ef205 | textbox | MPa:
1a14fb4f-fd11-51e2-8f92-b51e2763530b | textbox | Slump:
af208733-488c-558e-a376-141f010f58c3 | textbox | Agg:
| checkpoint | Check quantity of concrete required prior to ordering
bd80c8b7-f654-5906-8529-2913df18740e | textbox | m3:
| section | During Works
| checkpoint | Confirm hydraulic pits and line installed
| checkpoint | Attach Hydraulic ITP
| checkpoint | Confirm vapour barrier installed over correct subbase
| checkpoint | Confirm formwork edge boards is adequately braced and square
| checkpoint | Confirm set down heights are correct
| checkpoint | Confirm all cast in elements to construction joints are installed (key joints, construction joints, expansion joints etc)
| checkpoint | Confirm bond breaker has been applied to key joints
| checkpoint | Attach Formworkers ITP
| checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
| checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Confirm falls to drainage points in slab
| checkpoint | Attach Concreter ITP
| section | After Works
| checkpoint | Confirm saw joints installed
| checkpoint | Confirm stripping is complete and all set-downs/strip drains are clear of formwork
| checkpoint | Obtain as-built survey (attached survey)
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
47a111e9-00ee-528c-b83a-0d97a8ebcc48 | tickbox | 6mm +/- from design RL
bfec311e-1d7a-5633-a7af-5b7a0fed7870 | tickbox | 10mm +/- from design position
| checkpoint | Obtain all concrete tests at 4 days, and attach test results
9a2f6e4e-1069-58b7-90a9-c2bd8211b318 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
45dafe9d-e630-52e2-a907-3021b317d10b | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
69a4959a-8b78-5e8e-af7c-28ac6b9de84c | textbox | Test Strength MPa
| section | Sign Offs
| checkpoint | Orwell Sign Off
a63f7c8c-abd2-57ac-901e-e163fc58969a | note | Authorised By: FM
f3a3f74e-ae0e-5dae-85e4-fe3b11f0f280 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Stairs - GPL-QSE-ITP-STRUC-08 (Rev 00) |  | Stairs - GPL-QSE-ITP-STRUC-08 (Rev 00) | b330ac78-3213-49e5-b34f-3822c601104f
| section | Prior to Works
| checkpoint | Confirm bottom of stair RL's on Architectural Concrete Outlines
80d91c96-6915-54af-9c64-22c45670e755 | textbox | Bottom of Stair SSL:
36932479-5c61-5559-bd95-920717b36a01 | textbox | Bottom of Stair FFL:
| checkpoint | Confirm top of stair RL's on Architectural Concrete Outlines
13e4d63a-b9b1-5f0e-b690-6e6f1aa59a00 | textbox | Top of Stair SSL:
93e4c817-89f1-5fbf-b8a5-e8320ebbe8b5 | textbox | Top of Stair FFL:
| checkpoint | Confirm mid landing RL's on Architectural Concrete Outlines
5098db41-11a4-5cbf-b5b9-ebfe06244bf2 | textbox | Mid Landing SSL:
6afb8373-7b8d-581c-b7ba-6ed0fe34552d | textbox | Mid Landing FFL:
| checkpoint | Check quantity of concrete required prior to ordering
1daa84de-816c-5283-bb6f-5d5d7650c6a0 | textbox | Total m3:
| checkpoint | Confirm MPa, slump and agg size of concrete prior to ordering
8e4ed019-44fd-574a-a758-d9de844e8e32 | textbox | MPa:
961cc9af-c1cb-5677-9eac-fff48a53e049 | textbox | Slump:
5341f4ba-4546-5949-9dfe-a28cd2ec6c91 | textbox | Agg:
| section | During Works
| checkpoint | Confirm all formwork is clean and free of debris
| checkpoint | Confirm all cast in elements installed (i.e stair handrails), cross-check with stair shop drawings
| checkpoint | Attach Formworkers ITP
| checkpoint | Confirm position of block outs or penetrations installed for services (eg; fire hydrant, lighting, etc…)
| checkpoint | Confirm cast-in and/or post fix starter bars are installed as per design at landings
| checkpoint | Check for reinforcement lapping from landing into throat of stair as per Structural Details
| checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover confirm with Concreter
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Confirm cast-in of anti-slip items (eg, carborundum powder, stair nosings, etc…);
| checkpoint | Attach Concreter ITP
| checkpoint | Confirm Form Worker labour is available to clean up any slurry runs at bottom of walls, immediately after pour
| section | After Works
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
beb884fd-e00a-597c-b8e8-74a2b06ce5f3 | tickbox | 6mm +/- from design RL
69f57d22-d45d-5b30-8f05-9a921d3c1ba7 | tickbox | 6mm +/- from 3m straight edges
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
ff449d39-7422-5fe0-8a74-d6081b96b776 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
3bb72db7-8366-5b7f-aec5-e37c4d3df99a | textbox | Test Strength MPa
| section | Sign Offs
| checkpoint | Orwell Sign Off
a35933a7-2656-53e2-af71-08fd472801c2 | note | Authorised By: FM
b6c35aa3-4a9e-552f-802b-45346a5e8c09 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Stone Cladding - GPL-QSE-ITP-FAC 004 (Rev 00) |  | Stone Cladding - GPL-QSE-ITP-FAC 004 (Rev 00) | f4332e65-cbab-440d-8398-b1dc07ee9d96
| section | Prior to work
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Confirm structure and openings are as per design
68ae2a6b-0a8b-59c2-adb2-81a45480b1f7 | note | Refer Architectural Plans, Elevation and Shop drawing
| checkpoint | Confirm all required waterproofing to substrate has been completed
| checkpoint | All material delivered to site are correct (size, thickness, edge detail/mitre, as per approved sample etc)
| section | During to work
| checkpoint | Confirm cavity set out as per design
bfb1a8b8-9ea4-5a39-81db-2d3aa698808a | note | Refer Shop drawing
| checkpoint | Confirm pin fixings have been installed to specified (i.e. spacing, size and embedment of fixing)
| checkpoint | Confirm pin fixings have been pull tested
| checkpoint | Attach test results
| checkpoint | Confirm joints are consistent, as per design and at correct RL
9b20f029-178a-5a8e-9cfc-e07c2e9fc939 | note | Refer Shop drawing
| checkpoint | All cavities clean and clear
| section | After works
| checkpoint | Review sandstone to ensure no visible damage or scratches
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
d2286a84-cb58-592d-8e0e-58ae710fca06 | note | Authorised By: FM
ee523530-ad42-5ca6-9c5b-77deac595969 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Structural Steel - GPL-QSE-ITP-STRUC-011 (REV 00) |  | Structural Steel - GPL-QSE-ITP-STRUC-011 (REV 00) | 3cd06dea-1808-413b-90da-b30b8295fe1a
| section | Prior to Works
| checkpoint | Confirm set-out of grids, and benchmark RL on slab below. Attach survey plan.
e8858fa1-c8c5-52f4-9d48-b492fbb950a0 | note | Refer Architectural Concrete Outline
86f0bd48-00be-563d-9b29-128620ca438f | note | Refer Structural Steel Marking Plan
| checkpoint | Attach structural steel manufacturer ITP
34714e8f-3bba-5b75-84c3-79c7e5d7e94b | tickbox | Steel assembly and material certification from supplier
94324fae-e38e-5a8f-af31-124c7d993d76 | tickbox | Welding certification from supplier as per AS1554.1
3cd76014-effd-5cc5-9979-97da477600b4 | tickbox | Paint certification from supplier
| checkpoint | Attach Principal Structural Engineer review and acceptance of structural steel manufacture
| checkpoint | Confirm cast-in and/or base plate details are correct & verified against structural drawings
| checkpoint | Confirm exclusion zones are set up prior to lifting
| checkpoint | Confirm all steel members have been inspected for damage prior to lifting off truck
| section | During Works
| checkpoint | Confirm Steel members are correct size.
ab4f24c4-eee3-5545-9c3a-9096ad3fe91f | note | Refer Structural Steel Marking Plan
| checkpoint | Confirm Steel columns are installed in correct & final position. Check plumbness. Check RL. Check alignment with adjacent elements.
| checkpoint | Check Flange / Web direction in correct position.
| checkpoint | Confirm Steel beams are installed as per design.
86f943d7-ae21-59a1-94b9-f1b74677f54a | note | Refer Structural Steel assembly drawing
1bf47e5a-a6c2-521e-8a58-437aa772f1ef | textbox | Bolt type & quantity:
fba29d6c-3db4-5b06-ba48-b4b9543574a8 | textbox | Bolt direction:
| checkpoint | Confirm connection detail installed as per design
| checkpoint | Confirm on-site welding completed as per design, attach ITP
34b61e01-29e3-573b-811d-56cb551c98ed | note | Welds require 10% mag testing, 100% visual testing
| checkpoint | Attach Structural Steel installation certificate
| section | After Works
| checkpoint | Attach Surveyor As-Built & Verticality Check.
| checkpoint | Confirm tolerance of structural steel elements are as follows:
537aafa6-b3bc-5ddb-8fb2-a0a00ac49e0f | tickbox | 10mm +/- from design RL
c4ad3cd8-cd67-55a8-b0e1-e4515a94471e | tickbox | 6mm +/- from position
| section | Sign Offs
| checkpoint | Orwell Sign Off
35010c1c-6f34-5f67-b6f5-047b7dbd9d8f | note | Authorised By: DL
855a6326-39a4-5b43-8519-7740a0cc0fe2 | note | Issue Date: 24.04.2023
| signoff | Request Sign Off
| checklist | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00) |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00) | 3b87c80d-815b-4da8-a8ff-ec823b2811e6
| checkpoint | Confirm all materials have been removed from level
| checkpoint | Confirm that all slabs have been swept and cleaned of debris.
| checkpoint | Confirm all fillets and nails have been removed from slab soffits
| checkpoint | Confirm that all formwork has been removed from penetrations
| checkpoint | Confirm that all structural defects are rectified and signed off by Principal Structural Engineer
| checkpoint | Confirm that surveyor benchmark and grid lines are visible on slab
| checkpoint | Confirm that all set downs have been reviewed and rectified due to incorrect setouts or issues of depth
| checkpoint | Confirm grouting of PT ducts are completed and grout tubes cut flush
| checkpoint | Confirm all pans have been filled and/or edge stress pockets filled
| checkpoint | Orwell Sign Off
2b6f1b11-79da-5b69-ab3f-3f734541046e | note | Authorised By: FM
bab02b72-b852-55c7-87bb-365df8a547bc | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00) | 4926f011-fe9c-42d6-b48c-e4e6daa968f5
| section | Prior to Works
| checkpoint | Confirm set-out of grids, verticals, RL on slab below (attach survey plan)
998b24df-bd4c-5759-9dae-fa82c38a58de | note | Refer Architectural Concrete Outline
| checkpoint | Confirm formwork shop drawings and certificate has been received
| checkpoint | Confirm scaffold top-up complete
| checkpoint | Confirm safe means of access to new deck
| checkpoint | Confirm MPa, slump and agg size of concrete
2adfbe62-6c80-5c24-8b7d-3262ab7cec16 | textbox | MPa:
9f0eaa77-1f37-53ca-8ac9-8a7fb64eb0da | textbox | Slump:
7e706f25-4094-5ebf-8554-4e82daa56ade | textbox | Agg:
| checkpoint | Check quantity of concrete required prior to ordering
90bd0940-423d-55f4-8f73-91bd64a582bd | textbox | m3:
| section | During Works
| checkpoint | Confirm deck is safe, handrails installed and edge protection is provided to full perimeter of deck
| checkpoint | Confirm formwork deck is suitable to achieve required finish to concrete.
eb5f22a2-d364-5050-9c86-43108f9de793 | tickbox | Formwork is clean and free of debris, rubbish or sawdust
cf54bcb5-f14d-582b-82fd-4885813a6f5f | tickbox | No lipping of formwork between sheets
fbb35068-7f57-5dd5-baa3-40656c21ba3e | tickbox | Fillets, drip grooves installed at all corners
| checkpoint | Confirm as-built survey of deck is complete (attach survey plan)
| checkpoint | Confirm tolerance of deck, edgeboard, setdown, penos etc are as follows:
bbd2e343-9dba-5160-aeed-c9d995f01c6b | tickbox | 6mm +/- from design RL
146f0e4a-dd37-5742-8cae-a0ef1b10201d | tickbox | 10mm +/- from design position
| checkpoint | Attach Formworkers ITP
| signoff | Attach Formworkers Deck Handover Certificate
| checkpoint | Attach Formwork Engineer sign off certificate, Confirm that certificate references props, braces and compliance with design & AS3610
| checkpoint | Install slip joints to all load bearing walls and corbels where required
| checkpoint | Attach Hydraulic ITP (for cast-in elements), include relevant mark-ups
| checkpoint | Attach Electricians ITP (for cast-in elements), include relevant mark-ups
| checkpoint | Attach Fire Services ITP (for cast-in elements), include relevant mark-ups
| checkpoint | Attach Mechanical ITP (for cast-in elements), include relevant mark-ups
| checkpoint | Confirm that sufficient plastic bar chairs are used everywhere
| checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
| checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover confirm with Concreter
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Confirm that PT end condition (pan/edge stress) are correct and as per design
| checkpoint | Confirm that correct size chairs are used under PT
| checkpoint | Attach Post Tensioner ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Attach Post Tensioning Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Confirm falls to drainage points in slab
| checkpoint | Attach Concreter ITP
| checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
d122daf5-1d59-5e13-b9cf-7fcc4411f069 | tickbox | Form Worker
587f6a9a-4302-58d2-8e60-aad94f9cade0 | tickbox | Electrician
5b153720-312d-5743-baac-b5b7418e66d3 | tickbox | Plumber
047a831c-3937-5926-935f-3ea04c26c5a1 | tickbox | Post Tensioner
| checkpoint | Confirm Form Worker has labour below deck inspecting all joints (particularly at columns & walls) and is immediately cleaning any slurry
| section | After Works
| checkpoint | Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610
| checkpoint | Confirm stripping is complete and all edgeboard, setdowns etc are clear of formwork
| checkpoint | Obtain as-built survey and set-out for next level (attach survey plan)
| checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
53c3e88a-591b-536f-9158-7733233563e8 | tickbox | 6mm +/- from design RL
af7279f9-2e8f-5c7b-861d-dcadda934343 | tickbox | 10mm +/- from design position
| checkpoint | Confirm initial stress is conducted, after concrete has reached 9 MPa
| checkpoint | Confirm final stress is conducted, after concrete has reached 22 MPa
| checkpoint | Obtain all concrete tests at 1 days, and attach test results
96a6defc-0458-58dd-ac15-d1d3601f47b1 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 4 days, and attach test results
25ada92f-0a8c-5bf7-920f-f637175731e0 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
157906a9-2eb0-5c96-adce-8e68d08b4820 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
f0b89417-1e49-598b-bdaf-4a5ab07d9890 | textbox | Test Strength MPa
| section | Sign Offs
| checkpoint | Orwell Sign Off
6d6b9665-0d59-5a8f-a1e7-8cc01e342aa6 | note | Authorised By: FM
c30c7af5-e2e1-5bd4-b2bc-d1b009433861 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Tiling External - GPL-QSE-ITP-FAC 007 (Rev 00) |  | Tiling External - GPL-QSE-ITP-FAC 007 (Rev 00) | 928430c1-5954-4a75-881c-0302557891c3
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark installed
| checkpoint | Waterproof membrane laid and dry prior to install
| checkpoint | Confirm tile type, size and thickness and grout colour is correct
32123749-9c78-51c5-950c-9e9e72833add | note | Refer approved sample & apartment finishes matrix
| checkpoint | Confirm tile set-out point
f84c4aca-e728-57b4-a705-9458536a9129 | note | Refer Architectural Plans, Finishes Schedule
| checkpoint | Confirm if acoustic mat or similar is required
7db6b14d-ab29-5401-95bd-a293715288b4 | note | Refer Architectural RCP, Acoustic Report
| checkpoint | Confirm drainage is installed as per design.
2be93bc0-e170-5efb-8fbc-2a81fb39ec27 | note | Refer to Architectural & Hydraulic Plan
| section | During Works
| checkpoint | Confirm that all floor wastes are plugged during tiling works
| checkpoint | Confirm minimum bedding thickness is achieved
| checkpoint | Confirm installation of floor wastes is flush with or 1mm below floor tile level
| checkpoint | Floor tiles laid to falls – minimum 1:100 or as documented
| checkpoint | Grouting checked for uniformity and quality
| checkpoint | Ensure quality of tile installation is maintained, i.e. alignment of joints, joint thickness
| section | After Works
| checkpoint | Review to ensure no visible damage or scratches
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
d11a4e95-28d1-5051-9ba2-6cb2f46d7516 | note | Authorised By: FM
2c845ac2-491a-59d2-a04a-d1a5035e5148 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Tiling Internal - GPL-QSE-ITP-FIT-010 (Rev 00) |  | Tiling Internal - GPL-QSE-ITP-FIT-010 (Rev 00) | 6cbf1fa1-3604-4d5c-a7c0-265328199fab
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark installed
| checkpoint | Waterproof membrane laid and dry prior to install
| checkpoint | Confirm tile type, size and thickness and grout colour is correct
13d96a85-70bf-5e4e-9cf8-d6f5742af426 | note | Refer approved sample & apartment finishes matrix
| checkpoint | Confirm tile set-out point
cee9e4c4-cd72-5b7b-a9f0-f68c57d46321 | note | Refer Architectural Plans, Finishes Schedule
| checkpoint | Confirm if acoustic mat or similar is required
975ffe7e-2b08-544e-99eb-95aab08ea08d | note | Refer Architectural RCP, Acoustic Report
| checkpoint | Confirm drainage is installed as per design.
7ab9da7e-86af-581c-b8a9-3d381e3d86fa | note | Refer to Architectural & Hydraulic Plan
| checkpoint | Confirm aluminium angle is not damaged or misaligned
| checkpoint | Confirm top of aluminium angle is at the correct RL, and check against external floor finished level
| section | During Works
| checkpoint | Confirm that all floor wastes are plugged during tiling works
| checkpoint | Confirm minimum bedding thickness is achieved
| checkpoint | Confirm installation of floor wastes is flush with or 1mm below floor tile level
| checkpoint | Floor tiles laid to falls – minimum 1:100 or 1:80 inside showers
| checkpoint | Stop wall and floor tiles 2-3mm short of edges and fill with resilient caulking compound
| checkpoint | Grouting checked for uniformity and quality
| checkpoint | Ensure quality of tile installation is maintained, i.e. alignment of joints, joint thickness
| section | After Tiling
| checkpoint | Review to ensure no visible damage or scratches
| checkpoint | Confirm all excess silicon is removed from tiles and adjoining surfaces
| checkpoint | Attach subcontractor ITP
| section | Sign Off
| checkpoint | Orwell Sign Off
b8fea914-1d21-5a9a-92c1-1778fb35651a | note | Authorised By: FM
0d0b8c9d-b2ab-515d-be15-6c91d686a608 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00) | 10af8d00-5bde-475c-9469-61658a0e24b8
| section | Prior to Works
| checkpoint | Confirm set-out of verticals (attach survey plan)
bd1249a3-2e68-5ed2-90e9-8d1c7c69a735 | note | Refer Architectural concrete outline
| checkpoint | Confirm cast-in starter bars are in correct location
| checkpoint | Confirm MPa, slump and agg size of concrete
7c2224d7-839d-5f8a-a89e-6b424f8414e9 | textbox | MPa:
ec7cb882-c0fe-5c16-87a0-ac1c6aa59ab4 | textbox | Slump:
79d0c850-2345-5b88-9374-93949c60fd68 | textbox | Agg:
| checkpoint | Check quantity of concrete required prior to ordering
934bcaea-5313-59e6-9e99-377312cd2972 | textbox | m3:
| section | During Works
| checkpoint | Check reinforcement to ensuring adequate cover
| checkpoint | Confirm vertical and horizontal starter bars are installed in correct location
| checkpoint | Attach Reo Fixers ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
| checkpoint | Confirm all hydraulic cast-in services are installed (i.e. downpipes)
| checkpoint | Attach Hydraulic ITP
| checkpoint | Confirm position of block outs, penetrations etc are installed, as noted on:
84401be0-4670-50c7-a162-2e1406028644 | tickbox | Architectural Drawings
ed801592-e73a-5f0e-8974-d07fa18abc87 | tickbox | Structural Drawings
a5224000-83a9-51b7-ba5f-0eaef0cc24a8 | tickbox | Lift Drawings
fd62d9f0-f3c2-5992-91b5-60bc62508d9d | tickbox | Mechanical Drawings
356bf23e-25b8-513d-b02d-fd287d368529 | tickbox | Electrical Drawings
c55a72c8-e928-5515-b036-5fa51d913afd | tickbox | Fire Drawings
071eef45-118d-5da4-b766-a54b001b8fa3 | tickbox | Hydraulic Drawings
| checkpoint | Confirm formwork shutters are clean and will provide required class finish
2c6e91e5-e1fa-5e02-9396-2a3700417d9d | tickbox | Formwork is clean and free of debris
3f896ac1-8b71-5512-809b-5e300776dfcd | tickbox | Lipping of formwork between sheets
e8999af3-09c8-5c8b-ba53-e80d7242b901 | tickbox | Fillets installed at all corners
bac65c8f-d07d-5bd2-bbb7-243ce2e5dabf | tickbox | Ties are installed at even spacing
52170f59-59ad-5257-9b67-fd027f9b1cdf | tickbox | Bottom of wall/column is clean, free from debris, rubbish or sawdust
| checkpoint | Attach Formworkers ITP
| checkpoint | Attach Formwork Engineer sign off certificate confirming compliance with design & AS3610
| checkpoint | Confirm RL to top of vertical is acknowledged by Formworkers and Concrete Placer
| checkpoint | Confirm correct concrete supplied (attach docket)
| checkpoint | Confirm concrete tester onsite to take samples
| checkpoint | Confirm vibrating is occurring evenly
| checkpoint | Attach Concreter ITP
| checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
f9d26c27-1832-5832-abea-a221d8ebcb28 | tickbox | Formworkers
4307eabc-d2a7-5703-beae-20465414fdf5 | tickbox | Plumber
| checkpoint | Ensure Formworkers clean any slurry runs at bottom of walls immediately after pour
| section | After Works
| checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
| checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
a756a3c9-77c2-5585-ba3a-5952f319bad5 | note | If not undertake rectification works
| checkpoint | Obtain as-built survey (attach survey)
| checkpoint | Obtain all concrete tests at 1 days, and attach test results
a727f650-2bad-5dcc-9f80-b332554f216d | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 4 days, and attach test results
9cb99fe4-539b-57fc-bf8b-c02e60e20c15 | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 7 days, and attach test results
1441ca17-bedf-5904-8d19-888167181a8c | textbox | Test Strength MPa
| checkpoint | Obtain all concrete tests at 28 days, and attach test results
3f8866de-cec4-5222-a36b-4401b97baf54 | textbox | Test Strength MPa
| section | Sign Off
| checkpoint | Orwell Sign Off
febfa9ba-6ba9-5c1f-b244-0016f5f0a5a2 | note | Authorised By: FM
b13dc99b-7f97-5733-a5fe-9d009f1854f0 | note | Issue Date: 21.09.2022
| signoff | Request Sign Off
| checklist | Windows - GPL-QSE-ITP-FAC-001 (Rev 00) |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00) | 7b157df2-c70c-4b8f-9659-fc2867a056c9
| section | Prior to Works
| checkpoint | Work area and surfaces clean and clear ready to commence work
| checkpoint | Surveyor 1m mark and gridlines installed
| checkpoint | Confirm rebate/hob RL and position correct
345b4a78-798c-50a1-ad4f-0330a3fdc606 | note | Refer Architectural Concrete Outline drawings
| checkpoint | Waterproof membrane laid and dry prior to install
| checkpoint | All site measures for opening sizes complete prior to manufacture
e4fde8d9-a274-5a7f-9708-2ce3ca75c905 | note | Refer Architectural Window Clear Opening drawing
| checkpoint | All windows and doors delivered to site are correct type (colour, glass type & thickness, frame dimensions, function etc)
822fa019-26f2-5415-8fe1-8be0ab47d496 | note | Refer Architectural/Façade Spec and Shop drawing
| section | During Works
| checkpoint | All windows and doors fixed plumb and level
| checkpoint | All windows and door are in alignment with adj windows, and heads align
| checkpoint | All relevant windows and doors align with windows on the floor below
| checkpoint | Confirm RL of window sill against surveyor 1m mark
| checkpoint | All sills flashings installed
| checkpoint | Flyscreens installed where required
| checkpoint | All gaps caulked not in excess of 25mm
| section | After Works
| checkpoint | Review windows to ensure no visible damage to glass or aluminium components, and protection installed
| checkpoint | All window and door hardware and locks installed and keyed alike
| checkpoint | All glass and sliding tracks clean and clear
| checkpoint | Plywood ramps installed for access where required
| checkpoint | Attach subcontractor ITP
| section | Sign Offs
| checkpoint | Orwell Sign Off
938a296a-2405-50dd-9dc4-6b4f26598c35 | note | Authorised By: FM
43c7abda-486d-5f46-9878-05f5269cafdf | note | Issue Date: 21.09.2022
| signoff | Request Sign Off