## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GAJV-ITP-00184_5.0 - Concrete Work Diversion Chamber & Confluence Chamber | itp |  |  |  |  | GAJV-ITP-00184_5.0 - Concrete Work Diversion Chamber & Confluence Chamber
section | 1.0 - Preliminaries
checkpoint | 1.1 - Check - Drawings are IFC and current
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure the latest IFC drawings are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
holdpoint | HOLD POINT
checkpoint | 1.2 - Check - CEP, SWMS, TMP and ESCP in place and signed off by personnel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure latest IFC plans are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of plans
label | METHOD - Retain plans
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Plan register with the revision used
holdpoint | HOLD POINT
section | 2.0 - Materials (approval)
checkpoint | 2.1 - Steel reinforcing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 4671/ 3109 GC-C4P – 4.1 and 4.1.1.10
label | CONFORMANCE CRITERIA - Grade 500E
label | ○ Produced using micro-alloy process
label | ○ GRP 16
label | ○ Chemical Anchor
label | METHOD - Review mill certificate Reinforcing ID
label | FREQUENCY/PROCESS HELD - Each batch
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Mill Certificates
checkpoint | 2.2 - Concrete Mix Design (base, wall, benching)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS3104, MS-41P – 5P, 5.2P DWG 2012036.861
label | CONFORMANCE CRITERIA - Grade 45 MPa OPC
label | METHOD - Review mix design
label | FREQUENCY/PROCESS HELD - Each mix design
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Aconex approval mail
checkpoint | 2.3 - Block out infill concrete
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 201236.862
label | CONFORMANCE CRITERIA - Infill concrete to be S45/10
label | ○ Additional dosage of shrink reduction admixture as per drawing to be Sika control plus as or approved equivalent at 2.25% by weight of cement mass and shall comply with manufacturers requirements.
label | ○ Additional dosage of admixture as per drawing to be Xypex admix C-5000 additive or approved equivalent at 0.6% by weight of cementitious content and shall comply with manufacturers requirements.
label | METHOD - Review dockets
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - S
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.4 - Epoxy grout
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.908, DWG 2012036.863 GC-C4P
label | CONFORMANCE CRITERIA - As per manufacturers data sheet
label | ○ 25W x 20 NITOSEAL SC600 SEALANT
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.6 - Concrete pipe DN2100
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - DWG 2012034.183 MS-03
label | CONFORMANCE CRITERIA - RCRRJ Class 4
label | METHOD - Review shop drawings
label | FREQUENCY/PROCESS HELD - Each Delivery
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - QA from supplier
checkpoint | 2.7 - Hydrophilic Strip
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.873, DWG 2012036.908
label | CONFORMANCE CRITERIA - CJ-0725-3K or approved equivalent
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.8 - PE Liner & filler rod
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - CG-C27P - Table 5-1
label | CONFORMANCE CRITERIA - Technical data sheets
label | ○ Manufacturers certificates of compliance
label | METHOD - Manufacturers certificate of compliance
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
checkpoint | 2.9 - Approved Curing compounds
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P 11.3P
label | CONFORMANCE CRITERIA - Curing to be accepted by the engineer
label | ○ Curing to meet the requirements of MS-41P
label | ○ E-cure As per GAJV-MAR-000035
label | METHOD - Review technical data
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
checkpoint | 2.10 - Materials for Concrete Repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P
label | CONFORMANCE CRITERIA - Technical data sheets
label | METHOD - Review technical data
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material data sheet and aconex mail approval
checkpoint | 2.11 - Manhole Covers
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series, NZS 3996 CG-
label | CONFORMANCE CRITERIA - PAMREX DN700
label | ○ Gatic GM302C1212D, GM309C66D, GM303C6122D
label | ○ Class D400 HN-HO-72 rated
label | ○ Manufacturers certificates of compliance
label | ○ Shop drawings.
label | METHOD - Manufacturers certificate of compliance
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - S
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Dockets
checkpoint | 2.12 - Stainless Steel Safety Grille
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012034.161, NZS 3996
label | CONFORMANCE CRITERIA - Manufacturers certificates of compliance
label | ○ Shop drawings.
label | METHOD - Final design and detail to be submitted to Watercare for review and approval
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material Approval
checkpoint | 2.13 - Water stop
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P 4.1.2P DWG 2012036.862
label | CONFORMANCE CRITERIA - Supercast Rearguard R or approved equivalent
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.14 - Backfill Material – 7/3
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - Table C2-1 - Behind walls or chambers, CG_1, GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Approved DM7/3
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Before procurement
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
checkpoint | 2.15 - Backfill Material – Flowable Fill
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Min 5 MPa flowable fill
label | METHOD - Review mix design
label | FREQUENCY/PROCESS HELD - Each mix design
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Aconex approval mail
section | 3.0 - Construction: Reinforcing Cages
checkpoint | 3.1 - Reinforcement Placement
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series
label | ○ DWG 2012036.861
label | ○ DWG 2012036.909
label | ○ DWG 2012036.907
label | ○ DWG 2012036.906
label | ○ DWG 2012036.903
label | ○ DWG 2012036.902
label | ○ DWG 2012036.900
label | ○ DWG 2012036.893
label | ○ DWG 2012036.891
label | ○ DWG 2012036.890
label | ○ DWG 2012036.889
label | ○ DWG 2012036.888
label | ○ DWG 2012036.887
label | ○ DWG 2012036.886
label | ○ DWG 2012036.883
label | ○ DWG 2012036.882
label | ○ DWG 2012036.881
label | ○ DWG 2012036.880
label | ○ DWG 2012036.879
label | ○ DWG 2012036.878
label | ○ DWG 2012036.877
label | ○ DWG 2012036.876
label | ○ DWG 2012036.875
label | ○ DWG 2012036.872
label | ○ DWG 2012036.871
label | ○ DWG 2012036.870
label | ○ CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109
label | CONFORMANCE CRITERIA - Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification
label | ○ Minimum cover over reinforcement shall be as noted on the Design Drawings
label | ○ Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861
label | ○ Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered.
label | METHOD - Visual Inspection and measurement on site
label | FREQUENCY/PROCESS HELD - During and after steel placement
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
holdpoint | HOLD POINT
checkpoint | 3.2 - Chemical Anchors/ Chem Set Bars
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.909, DWG 2012036.861
label | CONFORMANCE CRITERIA - SAF2507 Stainless Steel Anchors.
label | ○ HILTI RE-500-SD Injection Adhesive
label | METHOD - Review product data sheet. Manufacturers certificate of compliance.
label | FREQUENCY/PROCESS HELD - Prior to and after installation.
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Installation checklist
holdpoint | HOLD POINT
checkpoint | 3.3 - Rebar Couplers
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS 3101, DWG 2012036.862
label | CONFORMANCE CRITERIA - ReidBar Steel coupler
label | ○ Use EPCON C8 XTREME as per manufactures instructions.
label | ○ RB25CS instead.
label | METHOD - Review product data sheet. Visual inspection.
label | FREQUENCY/PROCESS HELD - During and after placement
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
holdpoint | HOLD POINT
checkpoint | 3.4 - Construction Joints and Water Stop Placement
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P
label | ○ NZS 3109, Clause 5.6.3
label | ○ DWG 2012036 Series
label | ○ DWG 2012036.861
label | ○ DWG 2012036.862
label | ○ DWG 2012036.863
label | ○ DEG 2012036.873
label | ○ DWG 2012036.903
label | CONFORMANCE CRITERIA - Construction joints shall conform to NZS 3109, Clause 5.6.3, type B
label | ○ Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer
label | ○ Water stops shall be placed as indicated on the drawings
label | ○ Installed as per manufacturer’s specification
label | ○ and care taken to prevent damage during concrete placement.
label | METHOD - Visual inspection with reference to DWGS
label | FREQUENCY/PROCESS HELD - Before concrete pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
section | 4.0 - Construction: Formwork
checkpoint | 4.1 - Formwork
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series CG-C4P - 4.5P, NZS 3109 Section 5
label | CONFORMANCE CRITERIA - Formwork adequately supported and restrained – Design approved if necessary.
label | ○ Formwork to be treated with release agent where in direct contact with concrete.
label | ○ Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
checkpoint | 4.2 - Cast in items
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-P, DWG 2012034.185, DWG 2012036.863
label | CONFORMANCE CRITERIA - Carry out inspection and confirm correct position prior to concrete pour.
label | ○ Ensure correct cover is achieved around the item.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
holdpoint | HOLD POINT
checkpoint | 4.3 - Block-out infill pipe penetration (if required)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P-4, DWG 2013036.862
label | CONFORMANCE CRITERIA - Ensure all reinforcement is to be continuous through block-outs during construction.
label | ○ Ensure correct cover is achieved prior to concrete pour.
label | METHOD - Visual Inspection, Construction methodology and associated reinforcement curtailment details for approval before construction
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour Checklist
holdpoint | HOLD POINT
section | 5.0 - Post Construction: Concrete Works
checkpoint | 5.1 - Concrete Testing (Consistency, 28-day compressive strength, Shrinkage, Permeability, Water absorption, Sulphite content, Alkali content, Chloride content, Temperature rise)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P, MS-41P – table 6.1P
label | ○ Consistency: NZS 3109 and NZS 3112
label | ○ 28-day compressive strength: NZS 3109, Section 9 and NZS 3112
label | ○ Shrinkage: AS 1012.13
label | ○ Permeability: DIN 1048
label | ○ Water absorption: AS 4058, Appendix F
label | ○ Sulphite content: AS 1012.14
label | ○ Alkali content: Chloride content: AS 1012.14
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | CONFORMANCE CRITERIA - Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109
label | ○ 28-day compressive strength: 45 MPa
label | ○ Shrinkage: 430mS at 21 days, 600 mS at 56 days with variance 10% precast & 15% for cast in-situ
label | ○ Permeability: <20mm
label | ○ Water absorption: <6.5%
label | – Sulphite content: <4% by mass
label | – Alkali content: <2.5kg/m3
label | – Chloride content: As per table 5-1 of MS-41P
label | – Temperature rise: The lesser of: Thermal Control Plan limits
label | • <70°C maximum
label | • <40°C temperature rise from its fresh concrete casting temperature
label | METHOD - IANZ Lab tests
label | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent.
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
checkpoint | 5.2 - Concrete Curing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS 3109 Clause 7.8 MS-41P 11P
label | CONFORMANCE CRITERIA - Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification
label | METHOD - Visually monitored on site as per thermal control plan
label | FREQUENCY/PROCESS HELD - Hourly during peak sun hours and as required elsewhere
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 5.3 - Concrete finishes
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P DWG 2012036.900
label | CONFORMANCE CRITERIA - Concrete finishes to be in line with the design drawings and specification.
label | ○ Concrete finish to be U3/ F3 or approved finish where not PE lined.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 5.4 - Concrete Benching
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012034.161, DWG 2012034.183 CG-C4.2.1
label | CONFORMANCE CRITERIA - Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.
label | ○ Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.
label | ○ Should have the same grade as walls and base slab.
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Post-pour check sheet
checkpoint | 5.5 - Concrete Grouting lid panel joints
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.908
label | CONFORMANCE CRITERIA - Ensure joint details are as per the drawings
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - Before epoxy
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - QA Check sheet
checkpoint | 5.6 - Post Pour Inspection
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P
label | CONFORMANCE CRITERIA - Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
holdpoint | HOLD POINT
checkpoint | 5.7 - Concrete Repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P-4.6.1.4P
label | CONFORMANCE CRITERIA - Concrete repair using resin as per concrete structures specification.
label | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
label | METHOD - Visual Inspections
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
holdpoint | HOLD POINT
section | 6.0 - Construction: Construction PE Liner
checkpoint | 6.1 - PE Liner shop drawing
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Shop drawing to be submitted to WSL
label | METHOD - Submission
label | FREQUENCY/PROCESS HELD - 4 weeks prior to installation
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Shop drawing submission
holdpoint | HOLD POINT
checkpoint | 6.2 - Extrusion weld certificates
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Welders’ certificates for welding
label | METHOD - Copy of certificates
label | FREQUENCY/PROCESS HELD - All welders
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Copy of certificates
checkpoint | 6.3 - PE Liner Prior To Pour
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all joints on the liner are adequately secured.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-Pour Inspection
holdpoint | HOLD POINT
checkpoint | 6.4 - Extrusion weld testing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P, ASTM D4437, ASTM D5641, DVS 2227-1
label | CONFORMANCE CRITERIA - As a minimum all site welds shall be tested.
label | METHOD - Either vacuum box testing or high voltage spark testing. Visual inspection.
label | FREQUENCY/PROCESS HELD - All welds
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - As recommended by the manufacturer. Checklist for visual inspection.
checkpoint | 6.5 - Tapping Survey
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P
label | CONFORMANCE CRITERIA - Tapping survey to identify voids
label | ○ Voids to be repaired as recommended by the manufacturer.
label | ○ Pages 24 & 34 of Design & Installation handbook.
label | METHOD - As recommended by the manufacturer. Rubber mallet delamination survey.
label | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 6.6 - Liner repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P, DVS 2227-1
label | CONFORMANCE CRITERIA - As recommended by the manufacturer
label | ○ Clearly mark out areas for repair
label | ○ Extrusion welding
label | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
label | METHOD - Visual Inspection. Surfacing welds. Blanks. Panel strips.
label | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - PE Liner Checklist
holdpoint | HOLD POINT
section | 7.0 - Post Construction
checkpoint | 7.1 - Final As built including PE membrane
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings – 2012036 series, 2012034 series
label | CONFORMANCE CRITERIA - Survey
label | METHOD - Survey
label | FREQUENCY/PROCESS HELD - At completion
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - As built drawings
checkpoint | 7.2 - Hydrostatic testing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GC_1 10.5.2 D)
label | CONFORMANCE CRITERIA - Infiltration test for manholes over 3.5m deep
label | ○ There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints.
label | METHOD - Infiltration test
label | FREQUENCY/PROCESS HELD - At completion
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Test record sheet
holdpoint | HOLD POINT
checkpoint | 7.3 - Backfilling – 7/3
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Compacted to 90% of Maximum Dry Density
label | METHOD - NDM Test
label | FREQUENCY/PROCESS HELD - 1 Test per 500mm layer surrounding chamber
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM Test Results
holdpoint | HOLD POINT
checkpoint | 7.4 - Concrete Testing – Flowable Fill (Consistency, 28-day compressive strength)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | ○ Consistency: NZS 3109
label | ○ 28-day compressive strength: NZS 3109, Section 9 and NZS 3112
label | CONFORMANCE CRITERIA - Consistency: +/- 40mm - NZS 3109
label | ○ 28-day compressive strength: 5 MPa
label | METHOD - IANZ Lab tests
label | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch
label | ○ 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE