## Sheet1
2.4 | Epoxy grout | SEIPP | DWG 2012036.908 DWG 2012036.863 GC-C4P |  As per manufacturers data sheet  25W x 20 NITOSEAL SC600 SEALANT | Review product data sheet | Each delivery | MAR | GAJV | Material dockets | 2.4 - Epoxy grout | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036.908 DWG 2012036.863 GC-C4P | CONFORMANCE CRITERIA -  As per manufacturers data sheet  25W x 20 NITOSEAL SC600 SEALANT | METHOD - Review product data sheet | FREQUENCY/PROCESS HELD - Each delivery | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material dockets | 2.4 - Epoxy grout
2.6 | Concrete pipe DN2100 | GAJV | DWG 2012034.183 MS-03 |  RCRRJ Class 4 | Review shop drawings | Each Delivery | MAR | GAJV | QA from supplier | 2.6 - Concrete pipe DN2100 | RESPONSIBILITY - GAJV | REQUIREMENTS / REFERENCE - DWG 2012034.183 MS-03 | CONFORMANCE CRITERIA -  RCRRJ Class 4 | METHOD - Review shop drawings | FREQUENCY/PROCESS HELD - Each Delivery | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - QA from supplier | RESPONSIBILITY - SEIPP
2.7 | Hydrophilic Strip | SEIPP | DWG 2012036.873 DWG 2012036.908 |  CJ-0725-3K or approved equivalent   | Review product data sheet | Prior to commencement of work | MAR | GAJV | Material dockets | 2.7 - Hydrophilic Strip | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036.873 DWG 2012036.908 | CONFORMANCE CRITERIA -  CJ-0725-3K or approved equivalent   | METHOD - Review product data sheet | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material dockets | REQUIREMENTS / REFERENCE - DWG 2012036.908 DWG 2012036.863 GC-C4P
2.8 | PE Liner CHAR(AMP) filler rod | GAJV | CG-C27P - Table 5-1 |  Technical data sheets  Manufacturers certificates of compliance | Manufacturers certificate of compliance | Prior to commencement of work | MAR | GAJV | Material certificate and aconex mail approval | 2.8 - PE Liner CHAR(AMP) filler rod | RESPONSIBILITY - GAJV | REQUIREMENTS / REFERENCE - CG-C27P - Table 5-1 | CONFORMANCE CRITERIA -  Technical data sheets  Manufacturers certificates of compliance | METHOD - Manufacturers certificate of compliance | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval | CONFORMANCE CRITERIA -  As per manufacturers data sheet  25W x 20 NITOSEAL SC600 SEALANT
2.9 | Approved Curing compounds | SEIPP | MS-41P 11.3P |  Curing to be accepted by the engineer  Curing to meet the requirements of MS-41P  E-cure As per GAJV-MAR-000035 | Review technical data | Prior to commencement of work | MAR | GAJV | Material certificate and aconex mail approval | 2.9 - Approved Curing compounds | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - MS-41P 11.3P | CONFORMANCE CRITERIA -  Curing to be accepted by the engineer  Curing to meet the requirements of MS-41P  E-cure As per GAJV-MAR-000035 | METHOD - Review technical data | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval | METHOD - Review product data sheet
2.1 | Materials for Concrete Repairs | SEIPP | MS-41P |  Technical data sheets | Review technical data | Prior to commencement of work | MAR | GAJV | Material data sheet and aconex mail approval | 2.1 - Materials for Concrete Repairs | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - MS-41P | CONFORMANCE CRITERIA -  Technical data sheets | METHOD - Review technical data | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material data sheet and aconex mail approval | FREQUENCY/PROCESS HELD - Each delivery
2.11 | Manhole Covers | SEIPP | DWG 2012036 Series NZS 3996 CG- |  PAMREX DN700  Gatic GM302C1212D, GM309C66D, GM303C6122D  Class D400 HN-HO-72 rated  Manufacturers certificates of compliance  Shop drawings. | Manufacturers certificate of compliance | Prior to commencement of work | S | GAJV | Dockets | 2.11 - Manhole Covers | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 3996 CG- | CONFORMANCE CRITERIA -  PAMREX DN700  Gatic GM302C1212D, GM309C66D, GM303C6122D  Class D400 HN-HO-72 rated  Manufacturers certificates of compliance  Shop drawings. | METHOD - Manufacturers certificate of compliance | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - S | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Dockets | TYPE - MAR
2.12 | Stainless Steel Safety Grille | SEIPP | DWG 2012034.161 NZS 3996 |  Manufacturers certificates of compliance  Shop drawings. | Final design and detail to be submitted to Watercare for review and approval | Prior to commencement of work | MAR | GAJV | Material Approval | 2.12 - Stainless Steel Safety Grille | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012034.161 NZS 3996 | CONFORMANCE CRITERIA -  Manufacturers certificates of compliance  Shop drawings. | METHOD - Final design and detail to be submitted to Watercare for review and approval | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material Approval | ATTENDANCE REQUIRED - GAJV
2.13 | Water stop | SEIPP | CG-C4P 4.1.2P DWG 2012036.862 |  Supercast Rearguard R or approved equivalent | Review product data sheet | Prior to commencement of work | MAR | GAJV | Material dockets | 2.13 - Water stop | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C4P 4.1.2P DWG 2012036.862 | CONFORMANCE CRITERIA -  Supercast Rearguard R or approved equivalent | METHOD - Review product data sheet | FREQUENCY/PROCESS HELD - Prior to commencement of work | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Material dockets | RECORDS OR CHECKLISTS - Material dockets
2.14 | Backfill Material – 7/3 | SEIPP | Table C2-1 - Behind walls or chambers, CG_1 GAJV-RFI-002719 |  Approved DM7/3 | Material order review | Before procurement | MAR | GAJV | Delivery dockets Quarry material test results for PSD, MDD | 2.14 - Backfill Material – 7/3 | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - Table C2-1 - Behind walls or chambers, CG_1 GAJV-RFI-002719 | CONFORMANCE CRITERIA -  Approved DM7/3 | METHOD - Material order review | FREQUENCY/PROCESS HELD - Before procurement | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Delivery dockets Quarry material test results for PSD, MDD | 2.6 - Concrete pipe DN2100
2.15 | Backfill Material – Flowable Fill | SEIPP | GAJV-RFI-002719 |  Min 5 MPa flowable fill | Review mix design | Each mix design | MAR | GAJV | Aconex approval mail | 2.15 - Backfill Material – Flowable Fill | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - GAJV-RFI-002719 | CONFORMANCE CRITERIA -  Min 5 MPa flowable fill | METHOD - Review mix design | FREQUENCY/PROCESS HELD - Each mix design | TYPE - MAR | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Aconex approval mail | RESPONSIBILITY - GAJV
3.1 | Reinforcement Placement | SEIPP | DWG 2012036 Series DWG 2012036.861 DWG 2012036.909 DWG 2012036.907 DWG 2012036.906 DWG 2012036.903 DWG 2012036.902 DWG 2012036.900 DWG 2012036.893 DWG 2012036.891 DWG 2012036.890 DWG 2012036.889 DWG 2012036.888 DWG 2012036.887 DWG 2012036.886 DWG 2012036.883 DWG 2012036.882 DWG 2012036.881 DWG 2012036.880 DWG 2012036.879 DWG 2012036.878 DWG 2012036.877 DWG 2012036.876 DWG 2012036.875 DWG 2012036.872 DWG 2012036.871 DWG 2012036.870 CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109 |  Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification  Minimum cover over reinforcement shall be as noted on the Design Drawings  Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861  Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered. | Visual Inspection and measurement on site | During and after steel placement | HP | WSL/GAJV | Pre-pour checklist Photographs | 3.1 - Reinforcement Placement | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036 Series DWG 2012036.861 DWG 2012036.909 DWG 2012036.907 DWG 2012036.906 DWG 2012036.903 DWG 2012036.902 DWG 2012036.900 DWG 2012036.893 DWG 2012036.891 DWG 2012036.890 DWG 2012036.889 DWG 2012036.888 DWG 2012036.887 DWG 2012036.886 DWG 2012036.883 DWG 2012036.882 DWG 2012036.881 DWG 2012036.880 DWG 2012036.879 DWG 2012036.878 DWG 2012036.877 DWG 2012036.876 DWG 2012036.875 DWG 2012036.872 DWG 2012036.871 DWG 2012036.870 CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109 | CONFORMANCE CRITERIA -  Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification  Minimum cover over reinforcement shall be as noted on the Design Drawings  Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861  Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered. | METHOD - Visual Inspection and measurement on site | FREQUENCY/PROCESS HELD - During and after steel placement | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs | REQUIREMENTS / REFERENCE - DWG 2012034.183 MS-03
CONFORMANCE CRITERIA -  RCRRJ Class 4
3.2 | Chemical Anchors/ Chem Set Bars | SEIPP | DWG 2012036.909 DWG 2012036.861 |  SAF2507 Stainless Steel Anchors.  HILTI RE-500-SD Injection Adhesive | Review product data sheet. Manufacturers certificate of compliance. | Prior to and after installation. | HP | WSL/GAJV | Installation checklist | 3.2 - Chemical Anchors/ Chem Set Bars | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036.909 DWG 2012036.861 | CONFORMANCE CRITERIA -  SAF2507 Stainless Steel Anchors.  HILTI RE-500-SD Injection Adhesive | METHOD - Review product data sheet. Manufacturers certificate of compliance. | FREQUENCY/PROCESS HELD - Prior to and after installation. | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Installation checklist | METHOD - Review shop drawings
3.3 | Rebar Couplers | SEIPP | NZS 3101 DWG 2012036.862 |  ReidBar Steel coupler  Use EPCON C8 XTREME as per manufactures instructions.  RB25CS instead. | Review product data sheet. Visual inspection. | During and after placement | HP | WSL/GAJV | Pre-pour checklist | 3.3 - Rebar Couplers | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - NZS 3101 DWG 2012036.862 | CONFORMANCE CRITERIA -  ReidBar Steel coupler  Use EPCON C8 XTREME as per manufactures instructions.  RB25CS instead. | METHOD - Review product data sheet. Visual inspection. | FREQUENCY/PROCESS HELD - During and after placement | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Pre-pour checklist | FREQUENCY/PROCESS HELD - Each Delivery
3.4 | Construction Joints and Water Stop Placement | SEIPP | CG-C4P - 4.1.2P NZS 3109, Clause 5.6.3 DWG 2012036 Series DWG 2012036.861 DWG 2012036.862 DWG 2012036.863 DEG 2012036.873 DWG 2012036.903 |  Construction joints shall conform to NZS 3109, Clause 5.6.3, type B  Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer  Water stops shall be placed as indicated on the drawings  Installed as per manufacturer’s specification  and care taken to prevent damage during concrete placement. | Visual inspection with reference to DWGS | Before concrete pour | WP | GAJV | Pre-pour checklist | 3.4 - Construction Joints and Water Stop Placement | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P NZS 3109, Clause 5.6.3 DWG 2012036 Series DWG 2012036.861 DWG 2012036.862 DWG 2012036.863 DEG 2012036.873 DWG 2012036.903 | CONFORMANCE CRITERIA -  Construction joints shall conform to NZS 3109, Clause 5.6.3, type B  Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer  Water stops shall be placed as indicated on the drawings  Installed as per manufacturer’s specification  and care taken to prevent damage during concrete placement. | METHOD - Visual inspection with reference to DWGS | FREQUENCY/PROCESS HELD - Before concrete pour | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Pre-pour checklist | TYPE - MAR
4.1 | Formwork | SEIPP | DWG 2012036 Series CG-C4P - 4.5P NZS 3109 Section 5 |  Formwork adequately supported and restrained – Design approved if necessary.  Formwork to be treated with release agent where in direct contact with concrete.  Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete. | Visual Inspection | Prior to concrete pour | WP | GAJV | Pre-pour checklist Photographs | 4.1 - Formwork | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036 Series CG-C4P - 4.5P NZS 3109 Section 5 | CONFORMANCE CRITERIA -  Formwork adequately supported and restrained – Design approved if necessary.  Formwork to be treated with release agent where in direct contact with concrete.  Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete. | METHOD - Visual Inspection | FREQUENCY/PROCESS HELD - Prior to concrete pour | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs | ATTENDANCE REQUIRED - GAJV
4.2 | Cast in items | SEIPP | CG-P DWG 2012034.185 DWG 2012036.863 |  Carry out inspection and confirm correct position prior to concrete pour.  Ensure correct cover is achieved around the item. | Visual Inspection | Prior to concrete pour | HP | WSL/GAJV | Pre-pour checklist | 4.2 - Cast in items | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-P DWG 2012034.185 DWG 2012036.863 | CONFORMANCE CRITERIA -  Carry out inspection and confirm correct position prior to concrete pour.  Ensure correct cover is achieved around the item. | METHOD - Visual Inspection | FREQUENCY/PROCESS HELD - Prior to concrete pour | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Pre-pour checklist | RECORDS OR CHECKLISTS - QA from supplier
4.3 | Block-out infill pipe penetration (if required) | SEIPP | CG-C4P-4 DWG 2013036.862 |  Ensure all reinforcement is to be continuous through block-outs during construction.  Ensure correct cover is achieved prior to concrete pour. | Visual Inspection Construction methodology and associated reinforcement curtailment details for approval before construction | Prior to concrete pour | HP | WSL/GAJV | Pre-pour Checklist | 4.3 - Block-out infill pipe penetration (if required) | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C4P-4 DWG 2013036.862 | CONFORMANCE CRITERIA -  Ensure all reinforcement is to be continuous through block-outs during construction.  Ensure correct cover is achieved prior to concrete pour. | METHOD - Visual Inspection Construction methodology and associated reinforcement curtailment details for approval before construction | FREQUENCY/PROCESS HELD - Prior to concrete pour | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Pre-pour Checklist | 2.7 - Hydrophilic Strip
5.1 | Concrete Testing  Consistency  28-day compressive strength  Shrinkage  Permeability  Water absorption  Sulphite content  Alkali content  Chloride content  Temperature rise | SEIPP | MS-41P - 5P MS-41P - 12P MS-41P – table 6.1P Consistency: NZS 3109 and NZS 3112 28-day compressive strength: NZS 3109 Section 9 and NZS 3112 Shrinkage: AS 1012.13 Permeability: DIN 1048 Water absorption: AS 4058 Appendix F Sulphite content: AS 1012.14 Alkali content: Chloride content: AS 1012.14 Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan) |  Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109  28-day compressive strength: 45 MPa  Shrinkage: 430mS at 21 days, 600 mS at 56  days with variance 10% precast CHAR(AMP) 15% for cast  in-situ  Permeability: CHAR(LESS)20mm  Water absorption: CHAR(LESS)6.5%  • Sulphite content: CHAR(LESS)4% by mass  • Alkali content: CHAR(LESS)2.5kg/m3  • Chloride content: As per table 5-1 of MS-41P  • Temperature rise: The lesser of: Thermal Control Plan limits  CHAR(LESS)70°C maximum  CHAR(LESS)40°C temperature rise from its fresh concrete casting temperature | IANZ Lab tests | Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent. Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan) | WP | WSL/GAJV | Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests | 5.1 - Concrete Testing  Consistency  28-day compressive strength  Shrinkage  Permeability  Water absorption  Sulphite content  Alkali content  Chloride content  Temperature rise | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P MS-41P – table 6.1P Consistency: NZS 3109 and NZS 3112 28-day compressive strength: NZS 3109 Section 9 and NZS 3112 Shrinkage: AS 1012.13 Permeability: DIN 1048 Water absorption: AS 4058 Appendix F Sulphite content: AS 1012.14 Alkali content: Chloride content: AS 1012.14 Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan) | CONFORMANCE CRITERIA -  Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109  28-day compressive strength: 45 MPa  Shrinkage: 430mS at 21 days, 600 mS at 56  days with variance 10% precast CHAR(AMP) 15% for cast  in-situ  Permeability: CHAR(LESS)20mm  Water absorption: CHAR(LESS)6.5%  • Sulphite content: CHAR(LESS)4% by mass  • Alkali content: CHAR(LESS)2.5kg/m3  • Chloride content: As per table 5-1 of MS-41P  • Temperature rise: The lesser of: Thermal Control Plan limits  CHAR(LESS)70°C maximum  CHAR(LESS)40°C temperature rise from its fresh concrete casting temperature | METHOD - IANZ Lab tests | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent. Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan) | TYPE - WP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests | RESPONSIBILITY - SEIPP
5.2 | Concrete Curing | SEIPP | NZS 3109 Clause 7.8 MS-41P 11P |  Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification | Visually monitored on site as per thermal control plan | Hourly during peak sun hours and as required elsewhere | WP | SEIPP | Post pour check sheet | 5.2 - Concrete Curing | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - NZS 3109 Clause 7.8 MS-41P 11P | CONFORMANCE CRITERIA -  Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification | METHOD - Visually monitored on site as per thermal control plan | FREQUENCY/PROCESS HELD - Hourly during peak sun hours and as required elsewhere | TYPE - WP | ATTENDANCE REQUIRED - SEIPP | RECORDS OR CHECKLISTS - Post pour check sheet | REQUIREMENTS / REFERENCE - DWG 2012036.873 DWG 2012036.908
5.3 | Concrete finishes | SEIPP | CG-C4P - 4.1.6P DWG 2012036.900 |  Concrete finishes to be in line with the design drawings and specification.  Concrete finish to be U3/ F3 or approved finish where not PE lined. | Visual Inspection | Post pour | WP | SEIPP | Post pour check sheet | 5.3 - Concrete finishes | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P DWG 2012036.900 | CONFORMANCE CRITERIA -  Concrete finishes to be in line with the design drawings and specification.  Concrete finish to be U3/ F3 or approved finish where not PE lined. | METHOD - Visual Inspection | FREQUENCY/PROCESS HELD - Post pour | TYPE - WP | ATTENDANCE REQUIRED - SEIPP | RECORDS OR CHECKLISTS - Post pour check sheet | CONFORMANCE CRITERIA -  CJ-0725-3K or approved equivalent  
5.4 | Concrete Benching | SEIPP | DWG 2012034.161 DWG 2012034.183 CG-C4.2.1 |  Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.  Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.  Should have the same grade as walls and base slab. | Visual inspection | Post pour | WP | GAJV | Post-pour check sheet | 5.4 - Concrete Benching | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012034.161 DWG 2012034.183 CG-C4.2.1 | CONFORMANCE CRITERIA -  Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.  Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.  Should have the same grade as walls and base slab. | METHOD - Visual inspection | FREQUENCY/PROCESS HELD - Post pour | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Post-pour check sheet | METHOD - Review product data sheet
5.5 | Concrete Grouting lid panel joints | SEIPP | DWG 2012036.908 |  Ensure joint details are as per the drawings | Visual inspection | Before epoxy | WP | SEIPP | QA Check sheet | 5.5 - Concrete Grouting lid panel joints | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - DWG 2012036.908 | CONFORMANCE CRITERIA -  Ensure joint details are as per the drawings | METHOD - Visual inspection | FREQUENCY/PROCESS HELD - Before epoxy | TYPE - WP | ATTENDANCE REQUIRED - SEIPP | RECORDS OR CHECKLISTS - QA Check sheet | FREQUENCY/PROCESS HELD - Prior to commencement of work
5.6 | Post Pour Inspection | SEIPP | MS-41P |  Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances. | Visual Inspection | Post pour | HP | WSL/GAJV | Post pour check sheet | 5.6 - Post Pour Inspection | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - MS-41P | CONFORMANCE CRITERIA -  Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances. | METHOD - Visual Inspection | FREQUENCY/PROCESS HELD - Post pour | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Post pour check sheet | TYPE - MAR
5.7 | Concrete Repairs | SEIPP | CG-C4P-4.6.1.4P |  Concrete repair using resin as per concrete structures specification.  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure | Visual Inspections | Post Pour | HP | WSL/GAJV | Post pour check sheet | 5.7 - Concrete Repairs | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C4P-4.6.1.4P | CONFORMANCE CRITERIA -  Concrete repair using resin as per concrete structures specification.  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure | METHOD - Visual Inspections | FREQUENCY/PROCESS HELD - Post Pour | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Post pour check sheet | ATTENDANCE REQUIRED - GAJV
6.1 | PE Liner shop drawing | GAJV | CG-C27P |  Shop drawing to be submitted to WSL | Submission | 4 weeks prior to installation | HP | GAJV | Shop drawing submission | 6.1 - PE Liner shop drawing | RESPONSIBILITY - GAJV | REQUIREMENTS / REFERENCE - CG-C27P | CONFORMANCE CRITERIA -  Shop drawing to be submitted to WSL | METHOD - Submission | FREQUENCY/PROCESS HELD - 4 weeks prior to installation | TYPE - HP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Shop drawing submission | RECORDS OR CHECKLISTS - Material dockets
6.2 | Extrusion weld certificates | SEIPP | CG-C27P |  Welders’ certificates for welding | Copy of certificates | All welders | WP | GAJV | Copy of certificates | 6.2 - Extrusion weld certificates | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C27P | CONFORMANCE CRITERIA -  Welders’ certificates for welding | METHOD - Copy of certificates | FREQUENCY/PROCESS HELD - All welders | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Copy of certificates | 2.8 - PE Liner CHAR(AMP) filler rod
6.3 | PE Liner Prior To Pour | SEIPP | CG-C27P |  Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all  joints on the liner are adequately secured. | Visual Inspection | Each pour | HP | WSL/GAJV | Pre-Pour Inspection | 6.3 - PE Liner Prior To Pour | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C27P | CONFORMANCE CRITERIA -  Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all  joints on the liner are adequately secured. | METHOD - Visual Inspection | FREQUENCY/PROCESS HELD - Each pour | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Pre-Pour Inspection | RESPONSIBILITY - GAJV
6.4 | Extrusion weld testing | SEIPP | CG-C27P ASTM D4437, ASTM D5641 DVS 2227-1 |  As a minimum all site welds shall be tested. | Either vacuum box testing or high voltage spark testing Visual inspection | All welds | WP | WSL/GAJV | As recommended by the manufacturer Checklist for visual inspection | 6.4 - Extrusion weld testing | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - CG-C27P ASTM D4437, ASTM D5641 DVS 2227-1 | CONFORMANCE CRITERIA -  As a minimum all site welds shall be tested. | METHOD - Either vacuum box testing or high voltage spark testing Visual inspection | FREQUENCY/PROCESS HELD - All welds | TYPE - WP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - As recommended by the manufacturer Checklist for visual inspection | REQUIREMENTS / REFERENCE - CG-C27P - Table 5-1
6.5 | Tapping Survey | SEIPP | AGRU Design CHAR(AMP) Installation Handbook. CG-C27P |  Tapping survey to identify voids  Voids to be repaired as recommended by the manufacturer.  Pages 24 CHAR(AMP) 34 of Design CHAR(AMP) Installation handbook. | As recommended by the manufacturer. Rubber mallet delamination survey. | As recommended by the manufacturer | WP | WSL/GAJV | Post pour check sheet | 6.5 - Tapping Survey | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - AGRU Design CHAR(AMP) Installation Handbook. CG-C27P | CONFORMANCE CRITERIA -  Tapping survey to identify voids  Voids to be repaired as recommended by the manufacturer.  Pages 24 CHAR(AMP) 34 of Design CHAR(AMP) Installation handbook. | METHOD - As recommended by the manufacturer. Rubber mallet delamination survey. | FREQUENCY/PROCESS HELD - As recommended by the manufacturer | TYPE - WP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Post pour check sheet | CONFORMANCE CRITERIA -  Technical data sheets  Manufacturers certificates of compliance
6.6 | Liner repairs | SEIPP | AGRU Design CHAR(AMP) Installation Handbook. CG-C27P DVS 2227-1 |  As recommended by the manufacturer  Clearly mark out areas for repair  Extrusion welding  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure | Visual Inspection. Surfacing welds. Blanks. Panel strips. | As recommended by the manufacturer | HP | WSL/GAJV | PE Liner Checklist | 6.6 - Liner repairs | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - AGRU Design CHAR(AMP) Installation Handbook. CG-C27P DVS 2227-1 | CONFORMANCE CRITERIA -  As recommended by the manufacturer  Clearly mark out areas for repair  Extrusion welding  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure | METHOD - Visual Inspection. Surfacing welds. Blanks. Panel strips. | FREQUENCY/PROCESS HELD - As recommended by the manufacturer | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - PE Liner Checklist | METHOD - Manufacturers certificate of compliance
7.1 | Final As built including PE membrane | GAJV | IFC Drawings – 2012036 series 2012034 series |  Survey | Survey | At completion | WP | GAJV | As built drawings | 7.1 - Final As built including PE membrane | RESPONSIBILITY - GAJV | REQUIREMENTS / REFERENCE - IFC Drawings – 2012036 series 2012034 series | CONFORMANCE CRITERIA -  Survey | METHOD - Survey | FREQUENCY/PROCESS HELD - At completion | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - As built drawings | FREQUENCY/PROCESS HELD - Prior to commencement of work
7.2 | Hydrostatic testing | SEIPP | GC_1 10.5.2 D) |  Infiltration test for manholes over 3.5m deep  There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints. | Infiltration test | At completion | HP | WSL/GAJV | Test record sheet | 7.2 - Hydrostatic testing | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - GC_1 10.5.2 D) | CONFORMANCE CRITERIA -  Infiltration test for manholes over 3.5m deep  There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints. | METHOD - Infiltration test | FREQUENCY/PROCESS HELD - At completion | TYPE - HP | ATTENDANCE REQUIRED - WSL/GAJV | RECORDS OR CHECKLISTS - Test record sheet | TYPE - MAR
7.3 | Backfilling – 7/3 | SEIPP | GAJV-RFI-002719 |  Compacted to 90% of Maximum Dry Density | NDM Test | 1 Test per 500mm layer surrounding chamber | HP | GAJV | NDM Test Results | 7.3 - Backfilling – 7/3 | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - GAJV-RFI-002719 | CONFORMANCE CRITERIA -  Compacted to 90% of Maximum Dry Density | METHOD - NDM Test | FREQUENCY/PROCESS HELD - 1 Test per 500mm layer surrounding chamber | TYPE - HP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - NDM Test Results | ATTENDANCE REQUIRED - GAJV
7.4 | Concrete Testing – Flowable Fill  Consistency  28-day compressive strength | SEIPP | GAJV-RFI-002719 Consistency: NZS 3109 28-day compressive strength: NZS 3109 Section 9 and NZS 3112 |  Consistency: +/- 40mm - NZS 3109  28-day compressive strength: 5 MPa | IANZ Lab tests | Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift | WP | GAJV | Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests | 7.4 - Concrete Testing – Flowable Fill  Consistency  28-day compressive strength | RESPONSIBILITY - SEIPP | REQUIREMENTS / REFERENCE - GAJV-RFI-002719 Consistency: NZS 3109 28-day compressive strength: NZS 3109 Section 9 and NZS 3112 | CONFORMANCE CRITERIA -  Consistency: +/- 40mm - NZS 3109  28-day compressive strength: 5 MPa | METHOD - IANZ Lab tests | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift | TYPE - WP | ATTENDANCE REQUIRED - GAJV | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
2.9 - Approved Curing compounds
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - MS-41P 11.3P
CONFORMANCE CRITERIA -  Curing to be accepted by the engineer  Curing to meet the requirements of MS-41P  E-cure As per GAJV-MAR-000035
METHOD - Review technical data
FREQUENCY/PROCESS HELD - Prior to commencement of work
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
2.1 - Materials for Concrete Repairs
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - MS-41P
CONFORMANCE CRITERIA -  Technical data sheets
METHOD - Review technical data
FREQUENCY/PROCESS HELD - Prior to commencement of work
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Material data sheet and aconex mail approval
2.11 - Manhole Covers
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 3996 CG-
CONFORMANCE CRITERIA -  PAMREX DN700  Gatic GM302C1212D, GM309C66D, GM303C6122D  Class D400 HN-HO-72 rated  Manufacturers certificates of compliance  Shop drawings.
METHOD - Manufacturers certificate of compliance
FREQUENCY/PROCESS HELD - Prior to commencement of work
TYPE - S
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Dockets
2.12 - Stainless Steel Safety Grille
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012034.161 NZS 3996
CONFORMANCE CRITERIA -  Manufacturers certificates of compliance  Shop drawings.
METHOD - Final design and detail to be submitted to Watercare for review and approval
FREQUENCY/PROCESS HELD - Prior to commencement of work
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Material Approval
2.13 - Water stop
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C4P 4.1.2P DWG 2012036.862
CONFORMANCE CRITERIA -  Supercast Rearguard R or approved equivalent
METHOD - Review product data sheet
FREQUENCY/PROCESS HELD - Prior to commencement of work
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Material dockets
2.14 - Backfill Material – 7/3
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - Table C2-1 - Behind walls or chambers, CG_1 GAJV-RFI-002719
CONFORMANCE CRITERIA -  Approved DM7/3
METHOD - Material order review
FREQUENCY/PROCESS HELD - Before procurement
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Delivery dockets Quarry material test results for PSD, MDD
2.15 - Backfill Material – Flowable Fill
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - GAJV-RFI-002719
CONFORMANCE CRITERIA -  Min 5 MPa flowable fill
METHOD - Review mix design
FREQUENCY/PROCESS HELD - Each mix design
TYPE - MAR
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Aconex approval mail
3.1 - Reinforcement Placement
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012036 Series DWG 2012036.861 DWG 2012036.909 DWG 2012036.907 DWG 2012036.906 DWG 2012036.903 DWG 2012036.902 DWG 2012036.900 DWG 2012036.893 DWG 2012036.891 DWG 2012036.890 DWG 2012036.889 DWG 2012036.888 DWG 2012036.887 DWG 2012036.886 DWG 2012036.883 DWG 2012036.882 DWG 2012036.881 DWG 2012036.880 DWG 2012036.879 DWG 2012036.878 DWG 2012036.877 DWG 2012036.876 DWG 2012036.875 DWG 2012036.872 DWG 2012036.871 DWG 2012036.870 CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109
CONFORMANCE CRITERIA -  Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification  Minimum cover over reinforcement shall be as noted on the Design Drawings  Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861  Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered.
METHOD - Visual Inspection and measurement on site
FREQUENCY/PROCESS HELD - During and after steel placement
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
3.2 - Chemical Anchors/ Chem Set Bars
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012036.909 DWG 2012036.861
CONFORMANCE CRITERIA -  SAF2507 Stainless Steel Anchors.  HILTI RE-500-SD Injection Adhesive
METHOD - Review product data sheet. Manufacturers certificate of compliance.
FREQUENCY/PROCESS HELD - Prior to and after installation.
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Installation checklist
3.3 - Rebar Couplers
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - NZS 3101 DWG 2012036.862
CONFORMANCE CRITERIA -  ReidBar Steel coupler  Use EPCON C8 XTREME as per manufactures instructions.  RB25CS instead.
METHOD - Review product data sheet. Visual inspection.
FREQUENCY/PROCESS HELD - During and after placement
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Pre-pour checklist
3.4 - Construction Joints and Water Stop Placement
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P NZS 3109, Clause 5.6.3 DWG 2012036 Series DWG 2012036.861 DWG 2012036.862 DWG 2012036.863 DEG 2012036.873 DWG 2012036.903
CONFORMANCE CRITERIA -  Construction joints shall conform to NZS 3109, Clause 5.6.3, type B  Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer  Water stops shall be placed as indicated on the drawings  Installed as per manufacturer’s specification  and care taken to prevent damage during concrete placement.
METHOD - Visual inspection with reference to DWGS
FREQUENCY/PROCESS HELD - Before concrete pour
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Pre-pour checklist
4.1 - Formwork
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012036 Series CG-C4P - 4.5P NZS 3109 Section 5
CONFORMANCE CRITERIA -  Formwork adequately supported and restrained – Design approved if necessary.  Formwork to be treated with release agent where in direct contact with concrete.  Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete.
METHOD - Visual Inspection
FREQUENCY/PROCESS HELD - Prior to concrete pour
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
4.2 - Cast in items
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-P DWG 2012034.185 DWG 2012036.863
CONFORMANCE CRITERIA -  Carry out inspection and confirm correct position prior to concrete pour.  Ensure correct cover is achieved around the item.
METHOD - Visual Inspection
FREQUENCY/PROCESS HELD - Prior to concrete pour
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Pre-pour checklist
4.3 - Block-out infill pipe penetration (if required)
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C4P-4 DWG 2013036.862
CONFORMANCE CRITERIA -  Ensure all reinforcement is to be continuous through block-outs during construction.  Ensure correct cover is achieved prior to concrete pour.
METHOD - Visual Inspection Construction methodology and associated reinforcement curtailment details for approval before construction
FREQUENCY/PROCESS HELD - Prior to concrete pour
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Pre-pour Checklist
5.1 - Concrete Testing  Consistency  28-day compressive strength  Shrinkage  Permeability  Water absorption  Sulphite content  Alkali content  Chloride content  Temperature rise
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P MS-41P – table 6.1P Consistency: NZS 3109 and NZS 3112 28-day compressive strength: NZS 3109 Section 9 and NZS 3112 Shrinkage: AS 1012.13 Permeability: DIN 1048 Water absorption: AS 4058 Appendix F Sulphite content: AS 1012.14 Alkali content: Chloride content: AS 1012.14 Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
CONFORMANCE CRITERIA -  Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109  28-day compressive strength: 45 MPa  Shrinkage: 430mS at 21 days, 600 mS at 56  days with variance 10% precast CHAR(AMP) 15% for cast  in-situ  Permeability: CHAR(LESS)20mm  Water absorption: CHAR(LESS)6.5%  • Sulphite content: CHAR(LESS)4% by mass  • Alkali content: CHAR(LESS)2.5kg/m3  • Chloride content: As per table 5-1 of MS-41P  • Temperature rise: The lesser of: Thermal Control Plan limits  CHAR(LESS)70°C maximum  CHAR(LESS)40°C temperature rise from its fresh concrete casting temperature
METHOD - IANZ Lab tests
FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent. Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Shrinkage: Every 1,500m3 of concrete Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
TYPE - WP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests
5.2 - Concrete Curing
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - NZS 3109 Clause 7.8 MS-41P 11P
CONFORMANCE CRITERIA -  Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification
METHOD - Visually monitored on site as per thermal control plan
FREQUENCY/PROCESS HELD - Hourly during peak sun hours and as required elsewhere
TYPE - WP
ATTENDANCE REQUIRED - SEIPP
RECORDS OR CHECKLISTS - Post pour check sheet
5.3 - Concrete finishes
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P DWG 2012036.900
CONFORMANCE CRITERIA -  Concrete finishes to be in line with the design drawings and specification.  Concrete finish to be U3/ F3 or approved finish where not PE lined.
METHOD - Visual Inspection
FREQUENCY/PROCESS HELD - Post pour
TYPE - WP
ATTENDANCE REQUIRED - SEIPP
RECORDS OR CHECKLISTS - Post pour check sheet
5.4 - Concrete Benching
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012034.161 DWG 2012034.183 CG-C4.2.1
CONFORMANCE CRITERIA -  Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.  Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.  Should have the same grade as walls and base slab.
METHOD - Visual inspection
FREQUENCY/PROCESS HELD - Post pour
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Post-pour check sheet
5.5 - Concrete Grouting lid panel joints
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - DWG 2012036.908
CONFORMANCE CRITERIA -  Ensure joint details are as per the drawings
METHOD - Visual inspection
FREQUENCY/PROCESS HELD - Before epoxy
TYPE - WP
ATTENDANCE REQUIRED - SEIPP
RECORDS OR CHECKLISTS - QA Check sheet
5.6 - Post Pour Inspection
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - MS-41P
CONFORMANCE CRITERIA -  Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances.
METHOD - Visual Inspection
FREQUENCY/PROCESS HELD - Post pour
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Post pour check sheet
5.7 - Concrete Repairs
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C4P-4.6.1.4P
CONFORMANCE CRITERIA -  Concrete repair using resin as per concrete structures specification.  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
METHOD - Visual Inspections
FREQUENCY/PROCESS HELD - Post Pour
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Post pour check sheet
6.1 - PE Liner shop drawing
RESPONSIBILITY - GAJV
REQUIREMENTS / REFERENCE - CG-C27P
CONFORMANCE CRITERIA -  Shop drawing to be submitted to WSL
METHOD - Submission
FREQUENCY/PROCESS HELD - 4 weeks prior to installation
TYPE - HP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Shop drawing submission
6.2 - Extrusion weld certificates
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C27P
CONFORMANCE CRITERIA -  Welders’ certificates for welding
METHOD - Copy of certificates
FREQUENCY/PROCESS HELD - All welders
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Copy of certificates
6.3 - PE Liner Prior To Pour
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C27P
CONFORMANCE CRITERIA -  Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all  joints on the liner are adequately secured.
METHOD - Visual Inspection
FREQUENCY/PROCESS HELD - Each pour
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Pre-Pour Inspection
6.4 - Extrusion weld testing
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - CG-C27P ASTM D4437, ASTM D5641 DVS 2227-1
CONFORMANCE CRITERIA -  As a minimum all site welds shall be tested.
METHOD - Either vacuum box testing or high voltage spark testing Visual inspection
FREQUENCY/PROCESS HELD - All welds
TYPE - WP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - As recommended by the manufacturer Checklist for visual inspection
6.5 - Tapping Survey
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - AGRU Design CHAR(AMP) Installation Handbook. CG-C27P
CONFORMANCE CRITERIA -  Tapping survey to identify voids  Voids to be repaired as recommended by the manufacturer.  Pages 24 CHAR(AMP) 34 of Design CHAR(AMP) Installation handbook.
METHOD - As recommended by the manufacturer. Rubber mallet delamination survey.
FREQUENCY/PROCESS HELD - As recommended by the manufacturer
TYPE - WP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Post pour check sheet
6.6 - Liner repairs
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - AGRU Design CHAR(AMP) Installation Handbook. CG-C27P DVS 2227-1
CONFORMANCE CRITERIA -  As recommended by the manufacturer  Clearly mark out areas for repair  Extrusion welding  As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
METHOD - Visual Inspection. Surfacing welds. Blanks. Panel strips.
FREQUENCY/PROCESS HELD - As recommended by the manufacturer
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - PE Liner Checklist
7.1 - Final As built including PE membrane
RESPONSIBILITY - GAJV
REQUIREMENTS / REFERENCE - IFC Drawings – 2012036 series 2012034 series
CONFORMANCE CRITERIA -  Survey
METHOD - Survey
FREQUENCY/PROCESS HELD - At completion
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - As built drawings
7.2 - Hydrostatic testing
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - GC_1 10.5.2 D)
CONFORMANCE CRITERIA -  Infiltration test for manholes over 3.5m deep  There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints.
METHOD - Infiltration test
FREQUENCY/PROCESS HELD - At completion
TYPE - HP
ATTENDANCE REQUIRED - WSL/GAJV
RECORDS OR CHECKLISTS - Test record sheet
7.3 - Backfilling – 7/3
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - GAJV-RFI-002719
CONFORMANCE CRITERIA -  Compacted to 90% of Maximum Dry Density
METHOD - NDM Test
FREQUENCY/PROCESS HELD - 1 Test per 500mm layer surrounding chamber
TYPE - HP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - NDM Test Results
7.4 - Concrete Testing – Flowable Fill  Consistency  28-day compressive strength
RESPONSIBILITY - SEIPP
REQUIREMENTS / REFERENCE - GAJV-RFI-002719 Consistency: NZS 3109 28-day compressive strength: NZS 3109 Section 9 and NZS 3112
CONFORMANCE CRITERIA -  Consistency: +/- 40mm - NZS 3109  28-day compressive strength: 5 MPa
METHOD - IANZ Lab tests
FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift
TYPE - WP
ATTENDANCE REQUIRED - GAJV
RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests