## Checklist Templates
Id | Type | Name | Values | Prompting Name | Prefix | Resource Id
| checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS |  | 9eca8bf4-9616-427d-bf93-0c156542c6f1
| checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
| signoff | By signing I confirm I have completed the Principal Contractors induction.
| checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
| signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
| checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checklist | 010SAF_08 SWMS - AIDP Ripley |  | 010SAF_08 SWMS - AIDP Ripley |  | 67672d9d-a568-4095-8ff2-d42dda20549c
| section | Details
| checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
| signoff | By signing I confirm I have completed the Principal Contractors induction.
| checkpoint | 2. ALL STAFF
e10de068-098a-54e4-9ca5-367664a0021d | note | GM FIRE 001 Working with Elevated Work Platforms
15671497-ad54-5d32-afa4-04d3f3c4b7b8 | note | GM FIRE 007 Manual Handling
520f9407-d01a-5995-b868-f3de1b60147e | note | GM FIRE 008 Working at Heights
fd6856ce-5fcf-5581-a5f9-83f42ae44906 | note | GM FIRE 051 Using Platform Ladders
98e081c0-c0f2-5647-a6e5-e314220d57ab | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
| signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
| checkpoint | 3. WET FIRE TECHNICIANS
12aa4e47-69ce-583a-99b5-9ec6063e0430 | note | GM FIRE 009 Pressure Testing of Pipework
68ec500e-a59b-5b0b-b97e-769b3dde3619 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
f9b74e32-e4b3-583e-91f9-e7b3e7f28716 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
96e187af-4508-5796-814d-edf71d430753 | note | GM FIRE 002 Wiring Rough In Minor
edf53965-a075-57b6-9e59-ee1f53c5eea8 | note | GM FIRE 003 Fit Off Fire Alarm System
6d09c463-be7a-5e4e-bf48-f312657a39db | note | GM FIRE 006 Installation of Pipe and Fittings
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checklist | 010SAF_08 SWMS - ODYSSEY |  | 010SAF_08 SWMS - ODYSSEY |  | 8120818f-1d0a-470f-9c01-ba60960983a5
| section | Details
| checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
| signoff | By signing I confirm I have completed the Principal Contractors induction.
| checkpoint | 2. ALL STAFF
92bb9af3-0b3c-58d5-af01-dcaa3f0b56f9 | note | GM FIRE 001 Working with Elevated Work Platforms
16ddb0bd-0fc5-58c9-8947-d15f08b642d0 | note | GM FIRE 007 Manual Handling
5ed13011-b997-5fb6-859a-409c9dfd8397 | note | GM FIRE 008 Working at Heights
f233adc5-9ce8-5fa1-ae06-8bb9ae69b156 | note | GM FIRE 049 Working At Heights Rescue Plan
aa74eefc-fb81-571a-bef1-13ae5835d8a4 | note | GM FIRE 051 Using Platform Ladders
5194bef9-5c15-5d9f-861a-2f5c3e600e75 | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
| signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
| checkpoint | 3. WET FIRE TECHNICIANS
c78fac4a-5239-5f18-9a7a-73a9ec3e70e6 | note | GM FIRE 009 Pressure Testing of Pipework
9f860354-0af2-5f62-ad21-86c78c194f74 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
4fc9cf05-94c2-5778-94c6-e190eb249ca1 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
de972ceb-44c7-57f4-b5da-0399766270af | note | GM FIRE 002 Wiring Rough In Minor
d9228552-ac2e-5900-8cc2-e99ea5a3530a | note | GM FIRE 003 Fit Off Fire Alarm System
9ba02a88-ad12-53e3-98b8-aa4b8159636c | note | GM FIRE 006 Installation of Pipe and Fittings
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checklist | 010SAF_08 SWMS - Wacol |  | 010SAF_08 SWMS - Wacol |  | ce4b28a6-c405-445a-846e-8eb276046598
| section | Details
| checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
| signoff | By signing I confirm I have completed the Principal Contractors induction.
| checkpoint | 2. ALL STAFF
e5f4983c-79f9-5d2c-aa86-19628d97bca4 | note | GM FIRE 001 Working with Elevated Work Platforms
cb97e826-81ed-5498-a1ce-8026ccaa34ad | note | GM FIRE 007 Manual Handling
3b53ae2d-a214-5919-8837-5ff53a686f11 | note | GM FIRE 008 Working at Heights
ad6ae2e0-0d48-5ac4-ab38-827dbaaad25f | note | GM FIRE 049 Working at Heights Rescue Plan
addf5555-e97e-5e0f-a3ae-e0bdc7cb00d5 | note | GM FIRE 051 Using Platform Ladders
29dc9e88-4534-5045-931b-379ccf48318e | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
| signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
| checkpoint | 3. WET FIRE TECHNICIANS
f1b0bb87-0310-5266-aeba-e3557c2bc226 | note | GM FIRE 009 Pressure Testing of Pipework
aeb50cbd-b592-59f9-889d-b43dcaf721bd | note | GM FIRE 031 Sprinkler System and Associated Pump Test
afab2c86-7bc8-5186-b3b3-7364105642c4 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
c22eb604-a543-55e8-a9bc-009aa41cad12 | note | GM FIRE 002 Wiring Rough In Minor
f0a3092c-62a3-588f-ae43-2a09e0cbbfe5 | note | GM FIRE 003 Fit Off Fire Alarm System
666707d9-d1a3-5bb1-800c-46a33c145d82 | note | GM FIRE 006 Installation of Pipe and Fittings
| signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
| checklist | ASSESS-001 Risk |  | ASSESS-001 Risk |  | 65d54658-00c9-41c3-b950-1b008e1ceb5b
| section | Details
| checkpoint | Assessment Details
2737dda7-0da8-5350-a990-3c75e95a2887 | note | Use this form to document the risk management process for a single generic hazard.
289128ce-f3c7-536a-8723-4c70cd69bfce | textbox | Work Area:
ae1c42b6-c657-5e4d-9209-2bad75870138 | date | Date of Assessment:
8a53b641-9f68-5989-8d44-4cf1ba1926bb | textbox | Name of Assessor(s):
caa8797b-e08d-52e2-8736-115154cf3705 | textbox | Position(s):
f6ba4789-5bd0-5594-9b1c-010bc61db611 | textbox | Incident Ref. No:
| checkpoint | Hazard Identification
68274c54-05ce-5ce6-86e9-ca232bb22a04 | textbox | Describe the Hazard:
| checkpoint | Risk Assessment
8a96e579-e757-52cd-aac7-c2595bbe497f | textbox | What harm could the hazard cause?
403ab9f6-98ce-5c66-868e-2679ce633da0 | textbox | What is the likelihood of this happening?
5bd4779e-96af-50dd-9f6a-99a1d0cdff0d | textbox | Persons at risk:
e51e81a4-bb38-5350-a32e-178abbc64320 | textbox | Existing control measure:
711cba2d-b126-5349-aaf1-f13b90a0bfe9 | textbox | Consequence:
df1c1362-d4be-51c7-97a0-196760254788 | textbox | Likelihood:
43c9bc56-3d31-5b6b-88d9-be99de6d3ef5 | textbox | Outcome:
| checkpoint | Control Measures
26bc5138-30eb-58e0-9a12-54885a1212d4 | textbox | Elimination:
dc594457-3299-539f-8a27-727188b7aaf7 | textbox | Substitution:
809c790a-705f-5659-94a9-63c4e630e13d | textbox | Isolation:
a9c2b50c-045f-5fd6-bab9-52e76acc984a | textbox | Engineering:
fb6bc54d-9c0a-5f84-8964-f0f46bfd349a | textbox | Administrative or PPE:
e4d91219-de55-500e-ae36-937ccddb4ff0 | textbox | Preferred control option:
| checkpoint | Implementation
ad41fa7a-48fb-500a-9607-b49a60e29f86 | textbox | Associated activities:
4534f779-9710-5858-94f9-d6ce7fef84be | textbox | Resources Required:
9ea6d005-499c-56f7-974b-aa0ef858cb30 | textbox | Person(s) Responsible:
52b2f865-6543-582a-bf9f-e8a527fb4846 | date | Scheduled Review Date:
| signoff | Signature
| checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk |  | bb63b64e-244f-4189-a8f3-64ba8e0a0d61
| section | Details
| checkpoint | Assessment Details
490c172b-529e-535d-95e8-e5ad2fb72267 | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
ab900e56-77e5-5805-9997-0d1dfe555ee7 | date | Date of Assessment:
2aec5e0b-8872-5011-9421-48854f44e051 | textbox | Name of Assessor(s):
5e55219b-583f-56f3-bfdd-5dea292dd57c | textbox | Position(s):
e9a03c42-ce41-510c-81f9-6726eabba5a7 | textbox | Incident Ref. No:
| checkpoint | STEP 1 What is the Manual Task?
d8a88177-159b-582e-9b31-2a129c8d8287 | textbox | Relevant worker(s) to consult:
e232891b-c7c3-5c4f-8710-9e25a80167ba | textbox | Name of task or activity:
037244fe-8b0c-5516-b956-b112323b670e | textbox | Location where task occurs:
7ad89bb6-a5b4-5328-a0e3-bc256710943c | textbox | Who performs the task:
d3180965-d2b6-5838-8138-4fd1533da7f7 | textbox | General Description:
| checkpoint | STEP 2 Is the Manual Task hazardous?
aab5e53a-b884-5772-9678-39989f5669f7 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
aea3be1b-890b-5d5c-a299-8bddf9f945cf | note | 1. Does the task involve any of the following risk factors?
2f77bbb9-7a7b-580a-810e-83fa27e840a9 | button | Repetitive movement | Yes, No
74ead498-3c45-5e04-ad4b-502bba13a14c | button | Sustained or awkward postures | Yes, No
fb28a310-8cb2-561e-bf72-d57a019c6402 | button | Repetitive or sustained forces | Yes, No
34214a95-3841-51a1-bf4e-63eb1481bc91 | note | 2. Does the task occur over a long time?
6c8da810-d8ee-5e6c-b376-44d52748c8ed | button | More than a total of two hours over a whole shift? | Yes, No
82340f3d-6d46-59a9-861a-14429e99d1e2 | button | Continuously for more than 30 mins? | Yes, No
9c3dad32-e3f8-5cd9-b455-e6d7311e5e10 | button | 3. Does the task occur over a long time? | Yes, No
a7af4a9a-52ff-5f1e-8dfd-0ce660580656 | button | 4. Does the task involve vibration? | Yes, No
125544aa-735e-506b-a178-319eeb48e499 | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
b5eda523-6c02-5219-b69a-213dd43893f0 | tickbox | Question 1 and 2 (above)
1b6414b1-311c-5add-b3eb-36ffeffa0a86 | tickbox | Question 3 (above)
56e36077-34d7-5a5e-aed9-15ce5695b159 | tickbox | Question 4 (above)
0cd16434-4ea6-590f-a9d8-22c8120046dc | note | If you ticked anything in question in Question 5, continue to Step 3.
08ad31b6-03ac-561f-942e-c8e3166bd958 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
| checkpoint | STEP 3 - What is the source of the risk?
8d1e9cf7-f475-53a5-90ab-16d167860176 | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
b73be6fb-033a-5d07-b7fe-3c85624d7282 | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
33e5a4bb-1125-5f9c-9b67-c0ca918b214f | tickbox | The nature, size, weight or number of things handled in performing the manual task.
4b2e8d21-43fb-5539-8e97-b79a576d9999 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
68abb300-f394-5a9a-9ce0-557ece1da760 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
| checkpoint | STEP 4 - How do I control the risk?
398a9051-c14e-516e-9e62-3cf13abe5e71 | button | Can the task be eliminated? | Yes, No
368f597c-006e-5a4c-9622-48d5c1e579a3 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
9bffc518-e600-563f-83ee-b46609ceeb6f | textbox | If 'Yes', provide detail:
c4d0d777-07a6-5a79-8614-ff5925bd7cd2 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
6a5b0a4b-fa33-5a1b-a349-4b1922bd8324 | textbox | If 'Yes', provide detail:
| checkpoint | Implementing Controls
2af5e740-8b0e-52a2-a6b3-9e5ba22dcc64 | textbox | Name of Responsible Person:
5fa58af3-1606-5f22-bd13-ee000d4bac34 | button | Responsible for: | Approving, Implementing
e1b9ffd7-6efd-5f3c-9c53-1acc8e453440 | textbox | Name of Responsible Person:
59827434-9895-5505-8e76-8e811858ed18 | button | Responsible for: | Approving, Implementing
9cd466bd-5a1e-5a06-acf9-a0f373c775d6 | textbox | Name of Responsible Person:
c475ab63-1681-519d-b90f-20724591aaa6 | button | Responsible for: | Approving, Implementing
6052a159-cbde-544d-979f-ab6b78557e36 | textbox | Name of Responsible Person:
60efcd64-d526-5420-aed2-141bb0678c2a | button | Responsible for: | Approving, Implementing
| signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
| checkpoint | STEP 5 - Review the Controls
05cc12f9-13ba-5a46-851b-3ffa3889999b | date | Evaluated on(date):
aa933b5d-a414-56fb-9593-349817c6cb58 | textbox | Name of Assessor(s):
de2d6041-2451-56c8-a1b0-8123bb1f5ec2 | button | Consultation undertaken with relevant workers and others? | Yes, No
09a25e1d-447b-5703-a1a7-cf4cb0ccdd3f | button | Have any other risks been created by the controls? | Yes, No
62630e4b-1b37-507c-a268-7018937bb888 | button | Have the controls implemented reduced the risks? | Yes, No
8363f20e-bbe2-58a1-bdf2-6d6ec2000b64 | button | Can further controls be implemented to minimise the risk? | Yes, No
| checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | d95259bd-aa59-4600-a2b4-a021b0735158
| checkpoint | Details
d64f9e12-a8d1-572d-b52d-a264f7fe2c21 | textbox | Hazardous Chemical (product name):
61131b33-b900-5454-a839-bacf04fddc09 | textbox | Hazardous Chemical Reg Item No:
fa30c358-8185-53ab-a3e5-7a89d93b620c | textbox | Use:
| checkpoint | Nature of Hazard:
c3865074-534e-5e92-8183-abb02d5e0f45 | tickbox | Toxic (Poisonous)
73380fb3-2daa-58dd-a27c-fd92c28cc19e | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1a4cca2b-c7c6-582e-8872-a69b23f4f996 | tickbox | Carcinogenic (Cancerous)
8448ff25-8567-56c9-bc8d-c65b7be067c3 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
fbc7d650-c863-5438-88c0-b6801548cf7f | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
0a973027-0604-5fd1-8e33-1f6843068a0d | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
0c23b16f-1a98-579a-a5cd-b10341a3c93e | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
26e95726-3d59-5326-a5cf-7952dba23427 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
42fedfa0-4abe-5559-9a9d-3293d48b513b | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
6b6b9d2f-ae5d-51b8-a33a-bc4e0582efd9 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
72b4fd57-ee4c-528b-9346-3cc09a71a26c | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
65ff1186-86dc-5bc0-9441-f7cda9142a6b | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1488ffce-4246-526d-8862-2701ca976c59 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
fb8d25c9-0361-5fc2-992a-c8ac54018ced | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
| checkpoint | Risk of Injury
d5a297e5-61f4-58ff-b1b1-c8ca2eadf8ba | button | Risk of Acute (Short term) Injury: | High, Medium, Low
39a06ae2-da96-5801-a080-9de8bb9bd02a | button | Risk of Chronic (long term) Injury: | High, Medium, Low
| checkpoint | Controls and Requirements
dff33aea-d864-5296-85a7-3c3d89a4dbd8 | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
89612ad9-31eb-5b1b-b34f-25be2eacadf9 | textbox | First Aid Requirements and Storage Requirements:
| checkpoint | Signoff
| signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
| checkpoint | Assessor Signoff
| signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
| checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk |  | d445afbc-863d-430e-adaf-b1955ad468a6
| section | Details
| checkpoint | 1. Competent Peron(s)
9a9b3958-e0c2-5268-aaf5-3e077666511d | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
421913a6-005a-5bfe-b708-440417ab5d27 | textbox | Your Name:
3d439d05-c639-5ad1-ab00-1ba3920a9817 | note | Your Licences / Tickets:
11d866e9-f084-5b26-843b-254282a6c100 | tickbox | WP High Risk
5e54de38-508f-50a3-ab0e-e0c8679f8a1a | tickbox | Boom Lift
ea68eb1f-321e-5e02-a622-a3508facf2c4 | tickbox | Scissor Lift
f33fdee4-d517-591b-8e36-9e836bd3d6e1 | tickbox | Vertical Lift
81a98fa0-20d0-5274-9330-e937fa7e313e | tickbox | Other
c7f781a4-a73b-5d49-9565-093b617aba7c | textbox | If 'Other" please specify:
| checkpoint | 2. Plant/ MEWP Details
90819d9c-8041-58fa-925f-ff4173355404 | textbox | Make and Model:
72d506d5-4e56-5ec5-8c93-b3f7d99536ce | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
| checkpoint | 3. Employee Competency
283fe821-9465-5997-884a-e53b824195ee | textbox | Name:
fe2792fe-88fa-5cc7-822e-859e2506a067 | note | Role:
0cae945b-d039-5202-9dc1-c1f31d837e92 | tickbox | Operator
6e501ba1-23dc-5885-a740-dcb403ba9400 | tickbox | Spotter
ab7d246c-0564-52d1-8da5-f8432c1bffa9 | note | Licences/Tickets Held:
51471574-24e5-57a8-9d87-1ad1fd20269c | tickbox | WP High Risk
c8680c7b-abeb-52c1-b43d-450b4de8fcf8 | tickbox | Boom Lift
fe824038-2fe3-59bc-8a08-d3570fef7ac3 | tickbox | Scissor Lift
52a4e5af-5299-5c5e-a60e-0e296500ce88 | tickbox | Vertical Lift
| checkpoint | 4. Employee Competency
73351cee-c380-5c96-b1c7-82c4bdc7793a | textbox | Name:
47b977ce-db23-5091-9181-d12522014aeb | note | Role:
4115b285-0dab-509b-b78c-6b3fe3068366 | tickbox | Operator
af2cc185-f772-5a03-969d-bf46bb86577a | tickbox | Spotter
ffc930ab-59a8-5e18-afb0-da251ac3661c | note | Licences/Tickets Held:
eee9b880-b7b4-5f05-9f45-44bc188ceb0a | tickbox | WP High Risk
32033229-269f-5e26-9a26-6024c4bced51 | tickbox | Boom Lift
8f37f26d-6637-5101-b032-1e34a248d86d | tickbox | Scissor Lift
47dfed81-5cfe-5cd8-84b7-d113b35adc16 | tickbox | Vertical Lift
| checkpoint | 5. Employee Competency
70f78733-b0b1-5c22-a6ee-c84eb8cd5382 | textbox | Name:
e47caed1-7c4a-5091-84e9-87591d2a2fb9 | note | Role:
c84eba4f-6301-5058-96b5-2fdca6bc206c | tickbox | Operator
7f109594-56af-5ef1-b67b-b1e88673aa41 | tickbox | Spotter
5f1cc387-8b6d-5d5f-a08a-fb01a2b0d557 | note | Licences/Tickets Held:
b4dc56cf-627f-5e84-92e2-81be2c729e0f | tickbox | WP High Risk
ad5efe5c-cc66-52e7-9f33-9be813518ded | tickbox | Boom Lift
f3db69b0-11a3-5ff7-ae41-5bea8ceb8ed8 | tickbox | Scissor Lift
22049df2-afa1-534d-82b8-767d6e6e2636 | tickbox | Vertical Lift
| checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
f2766483-04cb-5da7-890e-dcc4e17777bd | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
5031b2eb-1c9c-55f6-a5cc-e63e9cfc76b5 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
12f920b1-81aa-59e1-a68c-e7269492885e | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
e2c18959-6e5b-562c-b9a5-4dac9408d32a | button | All Ground Support understand the emergency functions | Yes, No
925a0673-c38f-5fb4-b952-0246d6d57ff0 | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
58559eb2-25f7-513c-9294-7fac027dbbb9 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
| signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
| checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk |  | e3a26303-34a4-4b21-8a63-c0ce6f715e4c
| checkpoint | Details
130a7940-3935-5253-8ae5-82b1055dfd14 | note | Use this form to document the risk management process for a Confined Space.
5ca532df-2d29-581b-82a2-afa02f372b39 | date | Date of Assessment:
efa51e91-77f1-5628-a232-99f3c48b4020 | textbox | Name of Assessor(s):
faca6a3e-c6b2-569d-a658-055a4b1164db | textbox | Position(s):
| checkpoint | Hazard Identification
fad4c4f5-7e3d-5c24-add3-b36005494c89 | textbox | What Hazard/ Risk is associated with the task?
3caf8aa5-c5e5-5180-abaa-0a9a28dd8bda | textbox | Planned control measure to remove/ minimize hazards/ risks
80dd6f73-8abb-5f6e-b96d-a003c0862604 | textbox | What Hazard/ Risk is associated with the task?
d9d61964-0aa1-59dd-b417-a00130fda9f1 | textbox | Planned control measure to remove/ minimize hazards/ risks
2d8973bd-68de-5078-a649-d84eb5324735 | textbox | What Hazard/ Risk is associated with the task?
ad6a71eb-3672-50d8-bb44-58040405bb6f | textbox | Planned control measure to remove/ minimize hazards/ risks
beed0557-db27-53c9-b4fc-4106fb1a89e1 | textbox | What Hazard/ Risk is associated with the task?
e51d3210-35ea-5cdb-87eb-76a364960c2e | textbox | Planned control measure to remove/ minimize hazards/ risks
d291aadf-b45c-58c8-9abb-102b9ccd401c | textbox | What Hazard/ Risk is associated with the task?
9dcad28e-a5ed-5bcf-8b09-877284ed48f2 | textbox | Planned control measure to remove/ minimize hazards/ risks
| checkpoint | Review
a5bad4ff-4c84-55b4-979f-864d1d649e12 | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
ba7cd854-f374-50a0-bfdb-ccbcc4196d6d | note | If YES the Confined Space Work Permit MUST be completed
6cec88c8-2282-5790-9d56-16331bfb102c | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
| checkpoint | Assessor Signoff
a9d78622-1c5c-5ef7-96e7-636ddd7d9229 | date | Scheduled review date:
| signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
| checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety |  | 1334fc9e-4bc6-4da4-8df3-a747a59bcdd3
| checkpoint | Client Details
bf83fa46-22f9-52ba-80ce-a37529230034 | textbox | Client: i.e. Principal Contractor
589f8e09-feec-5403-88ff-194eb59adbe6 | textbox | Client Contact Name: Responsible Person(s)
eaeb3e60-e653-5a94-92f4-d3b629923fc7 | textbox | Client Contact Phone:
a7aa3b37-be9e-5945-8920-278208dee51a | textbox | Client Contact Email:
| checkpoint | Job Safety Analysis Details
e0472b52-555b-578f-9b0d-10ca185460a1 | textbox | Work Activity:
7755fbc5-1db4-5c6a-9eb9-1a50b1b4f39b | textbox | Location:
9c4ccf3a-dc0f-5789-a749-3b3c139a461c | textbox | Who is involved in the activity?
3ff18e9a-8a0b-505d-a5ad-334bf588fe4f | textbox | Plant and Equipment used:
8fc90058-6ecc-5824-be76-439a2920b450 | textbox | Maintenance checks required:
503c2e9e-0cf2-5780-83bb-17e8b8e8cd20 | textbox | Tools used:
b474c44b-9350-5cb0-88c6-309a83224ea6 | textbox | Materials used:
3a661dd6-8651-5a9a-abd9-54ae562e3b84 | textbox | PPE used:
62d2facf-fd51-5926-9608-32ef95c4748f | textbox | Certificates, permits and/approvals required:
538da0a8-b2aa-517d-b88c-85e029139a90 | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
| signoff | This JSA has been authorized by:
| checkpoint | Job Safety Assessment
ab741e71-0e49-5969-b5c0-f1c3f4db8a43 | note | Refer to the attached Risk Ratings table to complete the following..
3e4c920e-6e44-5089-aebe-027b3d41e2f5 | textbox | Job Step Details:
76039bd0-3c61-57c9-8744-263d7e249743 | textbox | Potential Hazards:
ff90c12e-9264-5ec9-bcfb-3809ecc00f80 | textbox | Name of Person(s) Responsible for work:
079e5ac5-4175-5234-8d36-7fe10d966313 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
f64d3e6b-5e0f-5c3b-a0b3-1c3a80d8b0fe | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
c8538ff2-0ff0-578b-aeef-883e852d2656 | textbox | Job Step Details:
6fa25bbc-560c-5b99-a629-cdc256177219 | textbox | Potential Hazards:
305af7ce-90b2-53c3-ac23-31c07c5e76a9 | textbox | Name of Person(s) Responsible for work:
f921fa6f-7fcd-5f5e-97a3-4c987bd12dff | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
278e01f2-0559-54a4-8c20-ae06c6fb8a94 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
8c34d454-01a5-5eca-9ee8-bfbf2fc6de79 | textbox | Job Step Details:
7bf50a7e-e54a-51b1-a340-1e56e1576981 | textbox | Potential Hazards:
e422d336-150e-51a7-94cd-4ab59a8286a4 | textbox | Name of Person(s) Responsible for work:
e2e1fd0c-62ed-50c9-b80d-fd9141eae82f | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
bfcca39f-b561-5f72-9ea8-3ee3779e362a | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
| checkpoint | Signoff
| signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
| checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection |  | 2f813446-4b4d-4034-8d01-092638082845
| section | 1. Administrative, training and risk management requirements
| checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
| checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
| checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
| checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
| checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
| section | 2. Safe work method statements
| checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
| checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
| checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
| section | 3. The work environment
| checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
| checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
| checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
| checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
| checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
| checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
| checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
| checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
| checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
| checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
| section | 4. Confined spaces
| checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
| checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
| checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
| checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
| checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
| section | 5. Working at heights
| checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
| checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
| checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
| checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
| checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
| checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
| checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
| checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
| checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
| checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
| checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
| checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
| checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
| checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
| section | 6. Electrical
| checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
| checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
| section | 7. Hazardous substances and dangerous goods
| checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
| checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
| checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
| checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
| section | 8. Corrective actions
| checkpoint | Corrective actions
| section | 9. Inspection sign off
| checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
| signoff | Signature
| checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
| signoff | Signature
| checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment |  | d08c98f1-cd66-42cd-8498-ee96b3e837f3
| section | Details
| checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
| checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
| checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
| checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
| checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
| checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
| checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
| checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
| checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
| checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
| checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
| checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
| checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
| signoff | PM Signature
| checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment |  | e9a2a334-4db6-4437-84f3-1551354b13cd
| checkpoint | Details
0e841671-e894-5ff8-8c03-82b5d38ebca8 | date | Date:
c1d0f4b3-7c9a-5132-9202-97a201ea48ef | textbox | Time:
bb60eefc-fad6-507f-945f-d1ad16fbf517 | textbox | Location:
24067169-41ae-5b98-ad46-2642b05d62e7 | textbox | Supervisor Name:
| checkpoint | Plant or Equipment
f5a882c2-e981-51c1-b81b-ea1e16eb70bc | textbox | What Plant/ Equipment is being used?
f2431a16-e799-5a6c-80c2-763dddad7637 | textbox | Person operating today:
dd154f8d-3d7b-5f2c-88c3-251fe510498d | button | Is this person competent and licenced (if required)? | Yes, No
70fb33c4-1f70-5ac0-942b-6a10ea85acdb | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
cc81ce2f-8bc8-5749-80fd-06fb563d3672 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
63617e94-873e-5e03-9f60-862196254f6a | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
a7d9973d-01b6-5c61-bcc7-8234615b507b | button | Have all relevant SWMS been completed? | Yes, No
| checkpoint | Plant and Equipment Checks
e3c467e9-a510-5e56-beed-49a3f8877e1a | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
546a8afd-7693-55a2-914a-54e7c90d72ae | tickbox | Electrical switches, traffic indicators, front and rear lights are working
e5b78bd6-d41e-528e-9746-0c62c2c527e7 | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
8b9ff6ad-23d7-57de-9e48-14a9253d2139 | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
5806d6c3-2813-50a0-a427-7fa9935957a4 | tickbox | Tyre pressure is as per manufacturers recommendations
d39fe1f4-ba21-5239-8ecc-7f4573210e83 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
54704e4f-9089-5ee6-ae7f-46a0727eac60 | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
f6e7258f-adb6-541d-b22a-ed50132853e8 | tickbox | Seatbelts are available
5d47353b-22df-563b-a9ca-2faccbdb89e6 | tickbox | There is no damage to switch gear and controls and that controls can be locked off
58c4f0bd-8df6-524c-a238-af2983501734 | tickbox | Emergency stop controls are marked, accessible and coloured red
3ad0b909-d61c-507a-a372-2aec69aa39af | tickbox | Warning devices are positioned to work effectively
4ccae013-80b5-5161-9761-e7028e449e0c | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
f7a4206a-0f8f-5a90-863e-6dc75e30731c | tickbox | There is no hazard or risk that could caused the plant to overturn
cf1206a0-2d7e-5f3f-be6c-0f9e888638ec | tickbox | Maintenance and inspections have been carried out
| checkpoint | General Notes
| checkpoint | Operator Signoff
| signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
| checkpoint | Supervisor Signoff
| signoff | By signing I confirm I have conducted this prestart with the operator (above).
| checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD |  | 26baf597-1e7f-4534-8f00-00a613126395
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | KPIs
ef28294d-80e7-5a97-9797-47eab0412edd | textbox | What area did you work on today? Specify level(s)
8bac133b-8e7b-54d3-bd45-213c754c0666 | tickbox | Detection - In Slab Conduits
df315065-d10d-5309-a137-f96b6957f3ca | tickbox | Detection - Rough In
79d811d4-f9b3-5356-8c5c-282608faae28 | tickbox | Detection - Fit Off
bd243762-5500-5cc3-863e-a5089b537b11 | tickbox | Sprinkler - Rough In
b32b2f5d-1593-5094-8ac0-574540448662 | tickbox | Sprinkler - Fit Off
| checkpoint | Productivity
935439a4-16d9-54f5-94c7-76368fef5f00 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
5eb767e9-2d9b-5650-9148-f8d6eacb88e9 | button | If 'no', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
e94f5534-5646-540d-aa79-e9ebca99d6ea | textbox | If 'other' provide detail:
| checkpoint | Clean Up
ff4b227b-9ed7-503b-a008-a24d64c82a30 | button | Is your work area tidy? | Yes, No
2685c8cb-e50d-53b0-81fc-2140a66dc922 | button | Have Chemicals used today been returned to secure storage? | Yes, No
63aa0fac-8064-5883-8936-a62b7a9bec47 | button | Have all tools been returned to toolbox? | Yes, No
ec167b87-5679-50a0-88b1-36f8dbca244d | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
95ffe66b-b5ad-53bb-9648-f5d931f2f4c0 | button | Have you completed all necessary QA paperwork for today? | Yes, No
bb4bba5b-d0e8-5fdb-a13b-dbc423aaee5a | button | Are all employees aware of where they are working tomorrow? | Yes, No
db72225a-9b45-5d2c-9afa-e9dfb88f7dd0 | note | If 'No' contact management now
a11f6f9a-2853-505a-b6fc-46a0fac484e1 | button | Were there any incidents, injuries or near misses on site today? | Yes, No
2b76a127-74df-54eb-92bd-c06e1d1e92d7 | note | If 'Yes' complete the necessary reports
| section | Employee 1 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
bedd8579-ce73-5d51-bd89-442431356264 | textbox | Employee Name:
f15bbad2-2e0f-5c91-8a01-59c5ec19aa4d | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
efa8fe75-3f2d-5025-a8a7-509f38b8be8e | textbox | Is there anything Management do to assist you?
| section | Employee 2 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
c51cff95-a51c-53e1-b602-b8450d896fb4 | textbox | Employee Name:
d1ce30c2-10c8-5eeb-85c1-594152bb9964 | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
31a56ca2-78a7-5551-bd8e-85855da6c83f | textbox | Is there anything Management do to assist you?
| section | Employee 3 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
8688e911-daa7-5e8f-89ea-d3b68df285f6 | textbox | Employee Name:
c8fb5699-3df7-56ac-b4c7-8696964a230a | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
33bbda92-da27-5107-9eb7-ac45717784f5 | textbox | Is there anything Management do to assist you?
| section | Employee 4 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
515e69d9-6ade-5f6d-8f85-3ab963960bb3 | textbox | Employee Name:
2d78bb6b-3fe6-5c26-9811-3d8545c68c2a | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
f22896f7-58d2-533f-89ba-4d8b07a4d187 | textbox | Is there anything Management do to assist you?
| section | Employee 5 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
7230fa38-9ea4-58af-bdd7-d6845db51c3e | textbox | Employee Name:
123b01b7-152b-59f9-8494-726e45845cbd | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
cb9bb095-1f57-593e-b5d0-46a63ad53c85 | textbox | Is there anything Management do to assist you?
| section | Employee 6 - Mental Health Check-in (Not Compulsory)
| checkpoint | Mental Health Check-in
afe83bd3-cd32-585d-946d-851d51281355 | textbox | Employee Name:
71444d64-4c30-55aa-a3d8-7a9230f64883 | button | How did you feel today? | Happy, OK, Sad, Frustrated, Tired
953199e7-d14a-59c9-abc3-b456c4d795a6 | textbox | Is there anything Management do to assist you?
| section | Sign Off
| checkpoint | Signoff
| signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
| checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart |  | beb07143-3243-4983-bf1f-2319e16d1748
| checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
| checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
| checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK |  |  | Specify the daily work task/s:
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
| checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
| checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
| checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
| checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
| checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
| checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
| checkpoint | General Notes
| checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
| signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
| checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks |  | 0c1a6e03-704f-4b04-8840-79a3fa0fa0fd
| checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: Odyssey
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
| checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
| checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
| signoff | Signatures
| checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders |  | fb3230ac-a3f8-47d3-9a01-1b12f4769b76
| checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: Odyssey
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
| checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
| checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
| checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
| checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
| signoff | By signing I confirm I atteneded this ToolBox Talk.
| checklist | ITPS-001 Fire Alarm and EWIS Design | itp | ITPS-001 Fire Alarm and EWIS Design |  | f28484bb-5ba1-4dcc-ae59-abf1c5adbb12
| section | Details
| checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER - IN HOUSE
92e68273-1a07-5da3-b052-9cf8cbfae874 | textbox | Drawing Reference Number:
6b4ae65c-17b8-54ed-900b-53ddbfea7562 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
66c9d8ef-8b5a-50cb-8589-98c04cf352ee | date | DATE:
| checkpoint | 2 - NOTATE INTERNAL DRAWING REGISTER - IN HOUSE
36ac551e-de37-5524-b163-9b19f8851a68 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
34949e7b-8ec2-5c73-b8d1-3989033a4feb | date | DATE:
| checkpoint | 3 - REVIEW TENDER/CONSTRUCTION DRAWINGS - IN HOUSE
7693e38b-788b-5a7b-86c1-3efa973fcef6 | textbox | Drawing Reference Number:
9f26fde9-2076-5fe0-9931-c8b9126c4e2f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e618dccc-2177-57d3-8779-3cc7a18e0810 | date | DATE:
| checkpoint | 4 - REVIEW SPECIFICATION - NCC2019 FIRE SPECIFICATION
00d5633f-16ad-5fb1-a24a-c9d96f348b0a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
77748099-7a47-5a67-9b13-9d615a91f89b | date | DATE:
| checkpoint | 5 - PREPARE SHOP DRAWINGS/ LAYOUTS - IN HOUSE NCC2019 FIRE SPECIFICATION
5a9508ac-cc7b-542a-a155-3fad64cc7ff7 | textbox | Approval by: Please print name and company of all involved parties
fa0dbdbc-d0a3-5a0b-8a68-e757c8982277 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4eadd2a2-2e8a-5aea-a196-ce15c5fca140 | date | DATE:
| checkpoint | 6 - REVIEW SUPPLIERS SHOP DRAWINGS - NCC2019
ed90f828-c390-51eb-a126-fd3f2bf2426d | textbox | Drawing Reference Number:
a51fcbda-3839-599f-9230-1fb70592cadb | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
5aee3a47-a276-5ef8-a96b-a95309ae0cb8 | date | DATE:
| checkpoint | 7 - DESIGNING FIRE ALARM SCHEMATIC - In House Design 1670.1-2018 – Must specify size/type of cable to be installed, transmission paths, type of devices to be installed and End of Line Devices
1b7d91d6-8438-5101-a8a2-ebe6e4cfefce | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f3261dc3-b3df-51d4-9a18-f222ab3013ea | date | DATE:
| checkpoint | 7 - PREPARE SCHEMATIC DRAWINGS - Prepared to as installed drawings.
c19364b6-0404-52af-acab-6790dd41e57b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
36caae91-9557-57e0-b3c7-df1e72102fa8 | date | DATE:
| checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL - In house design Referenced to PC specifications
391ec2d4-eeaa-5485-9eca-df591f01ac80 | textbox | Drawing Reference Number:
7e12f842-2fa0-5275-a0eb-b5e7647d1d41 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
663d4073-caa9-584a-bd60-88db3cd6b5f4 | date | DATE:
| checkpoint | 10 - REVIEW RETURNED SHOP DRAWINGS - In House QA
359501c1-1dc0-5c51-b223-7855b471eec5 | textbox | Drawing Reference Number:
a8b961ce-39af-5ddf-a31f-9ca93a7cee69 | textbox | Witnessed by: Please print name and company of all involved parties
f28ef354-c2cc-5f76-8052-74a335d6ac26 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
93dbe3d3-7615-5334-a053-c10056568963 | date | DATE:
| checkpoint | 11 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS - Referenced to PC specifications. Updated and superseded as needed
5c64924d-ba11-5f3e-bdc0-b42bb6eae1b6 | textbox | Drawing Reference Number:
e5dc3978-ebd6-55f0-b378-309a1e128e20 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
da1366fb-3e26-53c8-a16f-73ac90154af1 | date | DATE:
| checkpoint | Hold Point Details
4a58546a-393e-5121-a38b-36fa356e3229 | button | Hold Point Required: | Yes,No,Other:
0c5437bd-196b-5672-8981-2e6ea3b88d9f | textbox | Other (if applicable):
6ff01513-285c-53b2-b930-18cfe65cc4a6 | textbox | GM Sign Off - Name:
1466eabd-55e9-520d-ac8a-631d944d8425 | textbox | PC Sign Off - Name:
c31c0a8b-4e9e-5fe9-8569-f8e86236e42f | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-002 Purchasing and Procurement | itp | ITPS-002 Purchasing and Procurement |  | 9018ebca-5aa0-4d14-8b21-a34c7e4bffa3
| section | Details
| checkpoint | 1 - EQUIPMENT PURCHASES TO SPECIFICATION - In House QA Samples approved by PC/ CL
8d7ae4b7-35d0-51aa-a2fd-654ba00741b5 | textbox | Drawing Reference Number:
0619487f-d616-5b4e-bdaf-9d1ac9ed28a0 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
085265d2-4adb-5f6d-a9fd-e182fcd9a745 | date | DATE:
| checkpoint | 2 - CHECK SPECIFICATION SAMPLES HAVE BEEN APPROVED. - Approval by PC/ CL
b69d9ff6-4263-5300-b955-f537a0ce6ff1 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b2e39a3a-d003-5489-a2d8-635bb5922051 | date | DATE:
| checkpoint | 3 - MATERIALS APPROVED FOR INSTALLATION - CL Specification
cd6aa7f0-af60-5ed3-9fd1-c6af85ff6ab5 | textbox | Drawing Reference Number:
523e89c1-6f97-5cfd-94e5-d441657322e6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f21bb6e6-63e7-50c5-b1d7-7b44f8d07588 | date | DATE:
| checkpoint | 4 - PURCHASE ORDERS SPECIFIC AND PRICED - Orders from approved suppliers; In House QA – Equipment ordered > Equipment Supplied; POs referenced and invoices approved
477acd74-a82b-5178-9837-1d62940b5cce | textbox | Drawing Reference Number:
d3faebe4-ce52-57f8-a36d-267d050a5b7f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4cc540a8-2d89-5c36-ab18-027eceacbb94 | date | DATE:
| checkpoint | 5 - FIRE PANEL DELIVERED – AS ORDERED - In House QA Reference Design Invoice from Supplier
80b1c661-cf13-5029-8357-a20744774f3a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
3adea04f-9c96-5d4d-a585-b9031da1e6a9 | date | DATE:
| checkpoint | 6 - FIRE PANEL Q.A. CERTIFIED - In House QA To system Design requirements Supplier QA referenced
b4b5f900-70f0-57a9-b718-20958ac7c2ef | textbox | Certificate: Please print name and company of all involved parties
1bb1bc3d-42c1-563c-96aa-91407e59282f | date | DATE:
| checkpoint | 7 - SMOKE DETECTORS DELIVERED AS ORDERED - Samples approved by PC/ CL. Quantities as required. Invoices checked.
855e725a-d1e1-546e-9d55-1910dbb15070 | textbox | Drawing Reference Number:
37c44354-b5ea-5316-af56-80aebcdc2f0c | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f260f837-8e52-5e3f-ab48-5346bc16f2a2 | date | DATE:
| checkpoint | 8 - FABRICATED PIPE & VALVES DELIVERED AS ORDERED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes, valves and fittings shall be supplied new. HYDRANTS: AS2419.2-2005 – Section 8.1.1; Pipe, valve and fittings provided shall be new and comply with fitting specification. In House QA.
41236956-4633-599d-abc2-92a04a99687d | textbox | Drawing Reference Number:
745c2d10-bbbd-5323-a4c7-a10ae5311d15 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
da3225d5-bb82-5cce-bdef-f1fce7978258 | date | DATE:
| checkpoint | 9 - SPRINKLER HEADS DELIVERED AS ORDERED - AS2118.1-2017 – Section 9 & 10; Shall be new and meet the demands of the system they are installed on (Light/Ordinary Hazard) - In House QA
6390ecf3-ffc2-5171-bcdf-60181be23dfd | textbox | Drawing Reference Number:
a4b6ad4b-b695-5f14-a729-e72865c488f9 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
7b72c42d-3bad-5a88-9bf7-9d7124190d41 | date | DATE:
| checkpoint | Hold Point Details
f8649dbb-9ddf-5f8e-a5a6-cb0ca09d5271 | button | Hold Point Required: | Yes,No,Other:
21d06884-a548-58dc-8330-5dd514f30d2d | textbox | Other (if applicable):
174f798e-9536-5851-8f59-e51069db2ba6 | textbox | GM Sign Off - Name:
4c51b95f-6468-5185-a909-d77a5366a20b | textbox | PC Sign Off - Name:
a215ed8f-7daa-5f08-b415-5122eab50685 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-003 Fire Alarm and EWIS Installation | itp | ITPS-003 Fire Alarm and EWIS Installation |  | 240de470-1e53-449f-802a-3a16674f79fd
| section | Details
| checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
d4b4332c-6f0e-571c-9fe1-31055d8a0cee | button | C5.4.0 Wiring | Pass
42d19c37-5762-5c0f-ac35-42965e6d2d50 | textbox | Drawing Reference Number:
7c92011c-d24c-5d68-a321-a023538921c7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b8127666-6248-580a-b95a-b98f692a958b | date | DATE:
| checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
2d798dde-f905-5fca-9501-b4488b2c1ea1 | button | C5.2.5 Control Loops | Pass
8de9f9f4-e686-5972-9525-dc9a28e69a6e | button | C5.4.0 Wiring | Pass
f694ba28-9d02-5c3d-93cd-c0339d6a2315 | textbox | Drawing Reference Number:
d395e679-61ed-5652-a0f4-dc6b26b8ffce | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
3e0e8337-864b-52be-8836-8d3f6fbc936d | date | DATE:
| checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
a2dadb8c-68d5-5dcd-9fe4-7a491faeb967 | button | C5.2.5 Control Loops | Pass
54fcb519-3d0d-5aa7-bccd-2bae4dcb3881 | button | C5.4.0 Wiring | Pass
df2b80ad-27de-5ea1-aa43-fa27b60ae608 | textbox | Drawing Reference Number:
5fbdcfd7-2fda-56cb-871f-51eb9e99b2e9 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
8aada611-b0ef-5e08-bf7b-fdbbcef047e5 | date | DATE:
| checkpoint | 4 - DETECTOR BASES FITTED OFF - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
7ceb6321-a1f4-5377-bc5f-7e9eeb42c93b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
46f68240-f238-5e60-8ade-f4a0bea6279a | date | DATE:
| checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED - Detector type to appropriate location. Installed to Latest RCP
fae2daae-6af1-5dbe-9d92-9aabecbab1c4 | button | C5.6.0 Sensors/Detectors | Pass
b8cc3abf-143d-5cef-b3b5-69662e3ece1b | textbox | Drawing Reference Number:
ed3a5ea9-79f1-5055-a6fd-e02c73fdc8cd | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
bc0ec284-845b-51bd-b0ab-e5791eaeb6f5 | date | DATE:
| checkpoint | 6 - MANUAL CALL POINTS INSTALLED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
13f903ba-5120-54f5-a8fa-04dc0299fce4 | button | C5.10.0 Manual Call Points | Pass
4bf394f6-063f-53cb-9f13-449c88091e42 | textbox | Drawing Reference Number:
bcda8c10-b038-5ad0-8bd5-fa11f5efc563 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
1c902bc3-7c81-518e-840b-19b4537124ef | date | DATE:
| checkpoint | 7 - STROBES FITTED OFF - AS1670.1-2018: Check with Design Drawing and/or RCP
fc83272b-0008-5df2-ba2e-9651ba32c71b | button | C5.2.2 Set Points | Pass
c1aac25b-863f-573f-b143-237b1bf15193 | textbox | Drawing Reference Number:
9cc917d3-f0f7-5262-898c-083f642685a7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
10a116f0-4f81-5789-a759-aff34d2fd9aa | date | DATE:
| checkpoint | 8 - SPEAKERS INSTALLED - AS1670: Check with Design Drawing and/or RCP
463c0674-93bc-5c37-94d2-0c5ea2f3a106 | textbox | Drawing Reference Number:
6b85662a-3ddd-5a21-b45f-18467db78e76 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
707570db-a2c9-5def-90c4-6865bf367df2 | date | DATE:
| checkpoint | 9 - WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
ea915006-c7ae-5c22-8b7a-060a7354cb13 | button | C6.2.8 Warden Intercom Phones | Pass
f40ae91e-c1b2-59b4-9b9f-01caf65a2ac7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
72706a85-c6a4-5109-bcd7-5e28fde29f62 | date | DATE:
| checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
6ac0db7a-3970-5d40-a730-6a9611e7f7a2 | button | C5.2.2 Set Points | Pass
54aae543-3290-566e-ac16-156ec12a4a60 | button | C5.8.0 Modules Input/Output | Pass
6be1ffe6-f62b-5c8d-8205-c745f650e6f8 | textbox | Drawing Reference Number:
fd44afeb-b35b-5a19-81a7-271919b4c41f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
a11d1279-f471-5414-9309-ba836ceb7cbf | date | DATE:
| checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
48eb6881-7716-560e-9690-ee597992ef59 | textbox | Drawing Reference Number:
74f8b7f7-8280-5a31-b506-5e548bce54ae | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b5f74187-9b95-590c-8635-51c7e40542f1 | date | DATE:
| checkpoint | 12 - LABELS AFFIXED - AS4072.1-2018: The label should be positioned close to the service penetration
0e9ccd41-7920-55d5-ab0d-b046ff463637 | textbox | Drawing Reference Number:
69975f77-b866-53ec-931f-dfc891e9bef3 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
9a8723d3-cd73-5c79-9962-a0b23908fedc | date | DATE:
| checkpoint | 13 - ACOUSTIC PENETRATION SEALING - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
52c419cf-45da-5601-a2fb-e94ac97c7a16 | textbox | Drawing Reference Number:
bea98d6b-b823-5809-b4d4-6fd17d444a82 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
5ccff0b7-8bba-5307-b5c0-a151b8380f9d | date | DATE:
| checkpoint | 14 - CABLE TRAY BRACKET SPACING - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
d846db4a-1202-556f-b961-a728eec2c478 | textbox | Drawing Reference Number:
c6280678-ac3e-5a48-977b-df63e839f34f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
72935626-1607-53da-a471-7d2cdcd7198d | date | DATE:
| checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL - In House QA, Up to Date drawing register, Drawings updated with MPX approved references
8b012b47-842e-51d3-8c39-5ec9edbe0f39 | textbox | Drawing Reference Number:
e8155fc3-2034-5a30-9cdb-487801a4636b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
26ff3a14-1f45-56ed-9c1d-62ca3fbe553f | date | DATE:
| checkpoint | Hold Point Details
82d973cb-13c9-5c75-9523-d75114cf5359 | button | Hold Point Required: | Yes,No,Other:
49c59905-a9a7-557d-ae5c-b571349f973a | textbox | Other (if applicable):
1367999a-d71a-5b59-b8c4-81fc451e9c01 | textbox | GM Sign Off - Name:
f940793a-0209-595b-a95c-042a832172e2 | textbox | PC Sign Off - Name:
1f36fef9-c5af-5acc-83e7-39cd92ab4d4c | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-004 Fire Alarm and EWIS Commissioning | itp | ITPS-004 Fire Alarm and EWIS Commissioning |  | a009c352-01ad-434a-aeba-5b6ec7e0ed6c
| section | Details
| checkpoint | 1 - CONDUCT 100% TESTING OF ZONING - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
6d9aac08-0a89-5fbc-9d7b-358bd51d63fc | button | GMF-COMDRY-001 - Fire Detection Zone Commissioning | Pass
c3596fe6-a573-5c62-ad2c-ac3911b0d6e7 | button | C5.2.6 Sequencing | Pass
616a38f8-76bb-5beb-8c17-d94775342937 | button | C5.2.9 Alarm Functions | Pass
901b9857-05e6-5040-bd92-5a2001129c02 | textbox | Drawing Reference Number:
37248ba4-7693-5957-ae38-46aa3fc41c05 | textbox | Test performed by: Please print name and company of all involved parties
99d7d578-7989-51c2-82f5-d138d4d80f1a | date | DATE:
| checkpoint | 2 - CONDUCT 100% TESTING OF SMOKE AND THERMALS - AS1670.1-2018: Aspirating detectors measure and record the transport time (TT) from the most disadvantaged sampling point for each sampling pipe or branch.
76931d4f-8f9d-5928-a1ed-1bcbede78602 | button | GMF-COMDRY-002 - Fire Detection and Alarms (Smokes, Thermals, Duct Probes) | Pass
6b6db891-a1e9-5014-be32-50fc890ee34a | button | C5.6.0 Sensors/Detectors | Pass
9ca5a91d-d205-5369-a765-fbafba6e87a7 | textbox | Drawing Reference Number:
fdc020f3-e943-5bb9-83a4-2e4df567dfbd | textbox | Test performed by: Please print name and company of all involved parties
1c7e86a7-61fd-5913-a111-1c3e37699bae | date | DATE:
| checkpoint | 3 - CONDUCT 100% TESTING OF MCPS - AS1670.1-2018: (i) the correct operation of each manual call point; (ii) that the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and (iii) that manual call points are not subjected to alarm dependency.
d813cc22-f6f8-5b65-8be2-2daabcb8ee3d | button | GMF-COMDRY-003 - Manual Call Points | Pass
3e59dd42-3a92-560d-95a1-f25097d3612e | button | C5.10.0 Manual Call Points | Pass
141ad488-27fe-5c7d-a26e-6c070295409a | textbox | Drawing Reference Number:
883d6285-6f2e-5e1f-aaaa-31af7c056336 | textbox | Test performed by: Please print name and company of all involved parties
1a5c1bd5-4bb4-583f-b53b-d215c43e7486 | date | DATE:
| checkpoint | 4 - CONDUCT 100% TESTING OF DOOR DEVICES - AS1670.1-2018: Check the operation of each device/door release once installed
fdd126ba-8a92-5f53-990b-3dd3c3d0225b | button | GMF-COMDRY-004 - M.D.H / Auto Door Commissioning | Pass
d7e8aa1e-af2b-51d9-ac64-57d9e96c572e | button | C5.8.0 Modules Input/Output | Pass
40ffb3d5-7288-5b7e-97e0-2de078c19742 | textbox | Drawing Reference Number:
caa43783-e594-52d7-9a22-b3edee567c7a | textbox | Test performed by: Please print name and company of all involved parties
72c7d176-fdb6-50fd-aef2-022d047cab4a | date | DATE:
| checkpoint | 5 - CONDUCT 100% TESTING CASCADE AND EWIS ZONING - AS1670.4-2018: Audible signals, visual and tactile signals to be checked – automatic operation.
1a222f69-a717-57ee-b335-761ce4857f28 | button | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
609ec260-e41d-52e3-816d-4ef8f58e0934 | button | C6.2.5 Cascade Sequence | Pass
27e7ff39-193c-58ec-b7e5-131242d88b7d | textbox | Test performed by: Please print name and company of all involved parties
ff085a0a-de2c-5117-9707-df48904a6215 | date | DATE:
| checkpoint | 6 - CONDUCT 100% TESTING SPEAKERS AND ZONES - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
b040b0a0-ad6d-5af4-ba5b-53484506140f | button | C5.6.0 Sensors/Detectors | Pass
9475749c-3a9f-544e-87be-d4f2e07f6b10 | button | GMF-COMDRY-006 - Emergency Warning Commissioning | Pass
5c5e3529-50f7-51c3-a844-e6e9cad39aa0 | textbox | Drawing Reference Number:
07c93774-5c54-51b1-bd96-3584c3574cf5 | textbox | Test performed by: Please print name and company of all involved parties
285c96db-80b9-5f1b-9087-afcb6829811a | date | DATE:
| checkpoint | 7 - CONDUCT 100% TESTING WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP. The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
b857021b-a14c-523b-8d8a-30cbe6b521c6 | button | C6.2.8 Warden Intercom Phones | Pass
7dcf2967-2616-5965-8ece-d1e1bf9c465b | button | GMF-COMDRY-007 - Warden Intercom Point | Pass
e84a98a6-3916-580f-9a70-547161306137 | textbox | Drawing Reference Number:
67543692-3e19-5c3e-a28f-511fa5847e01 | textbox | Test performed by: Please print name and company of all involved parties
533b408c-919e-5456-934c-84097f340ab9 | date | DATE:
| checkpoint | 8 - CONDUCT FIRE MATRIX TESTING - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix
d1bc0c62-206f-59a4-84b0-1cec6e39beca | button | C5.2.2 Set Points | Pass
de63c73b-37aa-503a-967e-f5632f5d613b | button | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
f6b918ac-cc4d-520f-b12c-c12656946b9b | textbox | Drawing Reference Number:
1b53498a-7e59-5836-b651-8bdfa8a00385 | textbox | Test performed by: Please print name and company of all involved parties
2d5eb416-a778-5277-b53a-c6967e716f12 | date | DATE:
| checkpoint | 9 - CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING - AS1670.1-2018: The FFCP shall be incorporated into or located adjacent to the FBP and constructed in accordance with the FDCIE requirements in Clause 2.1
487b0365-a5c9-50a0-97a8-7913dae8fa36 | button | C6.6.0 Brigade Interface – FFCP | Pass
d7213309-0a8a-57f1-ba01-f8c4a4b013f1 | button | GMF-COMDRY-001 Fire Detection Zone Commissioning | Pass
e4ad2ce3-d6ad-54e1-9b36-4f3c3ced8aab | textbox | Drawing Reference Number:
9fdeb4ef-0516-5fbc-80fe-28b8464a4ff1 | textbox | Test performed by: Please print name and company of all involved parties
c528a041-c356-56f7-9b71-4f2893a3c8a9 | date | DATE:
| checkpoint | 11 - CONDUCT FULL FUCNTIONAL FIRE TESTING AND WITNESSING - AS1670.4-2018 – 100% test of installed devices, Interface testing to Trades: Mech Shutdowns, Security trips
00f0b490-ab6d-5c0b-9f71-5080a3e9c2d9 | button | C7.0.0 Full Function Fire Test – Witnessing | Pass
f245b882-beaf-50fd-9abf-0a3851944dc9 | textbox | Drawing Reference Number:
8cb0e9f5-6644-550c-8829-46a396c57482 | textbox | Test performed by: Please print name and company of all involved parties
88306b59-f876-519d-96ed-a55defa7d2b0 | textbox | Witnessed by: Please print name and company of all involved parties
88ff3207-5cb6-555f-940b-4296d3c51e98 | date | DATE:
| checkpoint | 12 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2015: Systems interface testing Prior to any interface testing check that all systems listed in the system interface schedule are complete and operable. This will involve checking that all systems interfaces to the FDAS
79e85036-6528-5b47-b483-40c9644b4977 | button | C5.2.2 Set Points | Pass
dae8a991-24b6-59d9-be9f-0b4397f1cdc4 | button | C5.8.0 Modules Input/Output | Pass
9dc6a2cb-d057-56d6-b810-787c6c6edfa6 | button | GMF-COMWET-001 - Sprinkler Zone Commissioning | Pass
f29f9da3-8a9f-54b4-a9e6-f3e952df24d2 | button | GMF-COMWET-002 - Flow Switch, Valve, Pump and Tank Indication | Pass
52c2280b-0baa-566d-b83a-0f2a62c47a3a | textbox | Drawing Reference Number:
763cbfdb-ebe2-558c-baa5-687c3324d78a | textbox | Test performed by: Please print name and company of all involved parties
c36644b3-2366-5f8f-8062-21b72697e06e | date | DATE:
| checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENTS, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS - In House QA, Correct documentation, Referenced and submitted to PC
1cd15bc7-8fd8-53df-86a8-a3163abf4b4e | textbox | Drawing Reference Number:
d87212f0-9b28-5e9a-bc81-1738fd6b99d4 | textbox | Test performed by: Please print name and company of all involved parties
216295f1-b796-5186-b42b-f05814f71310 | date | DATE:
| checkpoint | Hold Point Details
38066b36-4fe2-5bca-b0bd-1b2495a2def2 | button | Hold Point Required: | Yes,No,Other:
4ebdae1d-a8a9-56c6-8559-c4618a0d6de1 | textbox | Other (if applicable):
52923515-66a0-5e13-9e0c-2d910801dc28 | textbox | GM Sign Off - Name:
ae8c5576-e5cb-5897-8514-f05e36d723bb | textbox | PC Sign Off - Name:
5c84b622-a162-5236-8ebc-bd769a037a79 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-005 Fire Brigade Inspection | itp | ITPS-005 Fire Brigade Inspection |  | e2c7bf9e-b3fd-4b3f-9bce-088efa152317
| section | Details
| checkpoint | 1 - FIRE INDICATOR PANEL LOCATION ACCEPTABLE - AS1670.1-2018 Section 3.9 – FDCIE to be installed with .5m clearance either side of panel and 1.0m clearance in front of Panel.
425f413d-b2a2-5648-ac41-cbffcca5ccef | textbox | Drawing Reference Number:
3d7241e0-ade8-52b2-bf4e-11c725ea3e5e | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
2e48ca8a-5043-559f-a524-68f70ef255b1 | date | DATE:
| checkpoint | 2 - HEAT DETECTORS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
66c40977-2b64-502f-a367-8d54ca870620 | button | GMF-ITP-005 | Pass,Reviewed
da0c1e37-95b6-5a81-b7fa-3ad05fe38617 | textbox | Drawing Reference Number:
01121ae5-de11-58d2-b34c-905cfb8bff98 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f6fae19f-d0f3-5086-883d-454fac2087ec | date | DATE:
| checkpoint | 3 - SMOKE DETECTORS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
c9ccd312-05e8-5c40-8acf-2bf239f57a6c | button | GMF-ITP-005 | Pass,Reviewed
be412fb7-a82d-564d-bdfd-ffbacc6911f7 | textbox | Drawing Reference Number:
8e56dbcc-7622-56cc-807f-374f840ee60c | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
9cedb935-a9d0-57d6-b1ca-8ab4696dfbef | date | DATE:
| checkpoint | 4 - A / C INTERFACE TESTED - GFAs triggered from correct zones/devices. Interface Matrix referenced.
a1bca428-3e9c-58ba-b11d-4188f6968ac7 | button | GMF-ITP-005 | Pass,Reviewed
9aa37dd0-df53-509f-a372-7a3460046362 | textbox | Drawing Reference Number:
88980bf0-c347-5e36-9f41-a5da11255c24 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
df46d8c5-d74f-5b99-9d41-27b849bcac2e | date | DATE:
| checkpoint | 5 - MANUAL CALL POINTS TESTED - 100% Test of installed devices. Correct location and spacings. Correct zoning and description at FDCIE. Correct interfaces triggered.
32cca62c-18a0-50c1-8e63-8afd796316f4 | button | GMF-ITP-005 | Pass,Reviewed
8421ceaa-0c34-5432-8da8-9cdc90201f8a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c5e72f7f-5e7d-5980-8514-afabb7473948 | date | DATE:
| checkpoint | 6 - DOOR INTERFACES. BMS INDICATION - GFAs triggered from correct zones/devices. BMS correct to descriptions provided from trades.
a9b13fd5-31c8-53a6-91eb-e52acc82800d | button | GMF-ITP-005 | Pass,Reviewed
88394a7d-bd13-5954-8c7d-398f6919df8d | textbox | Drawing Reference Number:
19329dd1-2e60-5d7a-a8d7-bab2d0a4cf16 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b3c27d2c-e6a9-530a-b40b-4f296e603f57 | date | DATE:
| checkpoint | 7 - CERTIFICATES PROVIDED - GMF-COMDOC-001, GMF-COMDOC-002, GMF-COMDOC-003, GMF-COMDOC-004
62b6a1dc-a28e-5e9d-afed-5b3ccf35f390 | textbox | Drawing Reference Number:
d461aca1-a9c7-5ee2-8670-20819bc8d3c3 | textbox | Certificate: Please print name and company of all involved parties
5579da96-0f93-5cb9-a59d-dc7f25f7fbc8 | date | DATE:
| checkpoint | Hold Point Details
deaf9a1c-8173-5695-a1d6-70c75c83bd3d | button | Hold Point Required: | Yes,No,Other:
5bc6bc00-2286-54ae-ae7b-340b19028554 | textbox | Other (if applicable):
afb723fb-d55f-5096-a2fc-73699145d1d5 | textbox | GM Sign Off - Name:
8921a4ad-37c2-55a2-9dd7-2a4c91dfd196 | textbox | PC Sign Off - Name:
5424299a-2db6-581d-9959-c074232890e1 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-006 Warranty Period | itp | ITPS-006 Warranty Period |  | ea5c79c2-91c1-49e0-a3fa-4968ca6bd539
| section | Details
| checkpoint | 1 - PROVIDE CLIENT OPERATOR INSTRUCTIONS - As and when required
448099fa-3cc0-5d9e-b53a-e5b26e00d18d | textbox | General: Please print name and company of all involved parties
93e95ec5-9749-53d2-a87a-40efdd0ee540 | textbox | Witnessed by: Please print name and company of all involved parties
e34ff725-756c-5329-b19b-0e9ffe4d8a82 | date | DATE:
| checkpoint | 2 - TRAINING - As and when required
d0af0170-2cfd-5da2-85e0-cf0d97c90bdf | textbox | General: Please print name and company of all involved parties
86928ad5-8e9f-5765-9eae-9f1854cae7e0 | textbox | Witnessed by: Please print name and company of all involved parties
40e9a645-958e-408d-9844-6eee4506d5cb | textbox | Held: : Please print name and company of all involved parties
7e181b80-c746-5381-a6f4-15ff436345cc | date | DATE:
| checkpoint | 3 - MAINTENANCE PLAN - As per spec. and quoted offer.
eecb9723-8ff1-5f1b-96c2-4c7568b6f3ca | textbox | General: Please print name and company of all involved parties
b32d20ab-47b5-5a0d-91bf-c6e2e03de3b7 | date | DATE:
| checkpoint | Hold Point Details
e321ac3f-9cd3-52f0-a2ae-5f40c4c03fe0 | button | Hold Point Required: | Yes,No,Other:
9c44acae-608c-5381-b00e-27003c52e231 | textbox | Other (if applicable):
9bfe2111-c07e-5ff6-85ea-59f69e82b7f9 | textbox | GM Sign Off - Name:
7f730866-7219-55bf-98ba-1af3f128453b | textbox | PC Sign Off - Name:
b8f375f7-dd72-586f-ae17-23655e652cce | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-007 Sprinkler and Hydrant Design | itp | ITPS-007 Sprinkler and Hydrant Design |  | bf0589fc-713f-48fc-97f4-a8e6b036d376
| section | Details
| checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
5435e5ac-041c-5277-b918-9081ba9e3c28 | textbox | Drawing Reference Number:
c612f198-f0a1-5aa8-adeb-95b9cd1fe0ed | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
1e5f7dd3-fc92-5d7d-b62e-578634e0d2fb | date | DATE:
| checkpoint | 2 - REVIEW TENDER/CONSTRUCTION DRAWINGS
9f373b84-d9c7-5244-907a-bb959e146bb5 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
ad0149c5-111d-5728-a4ae-9f9a7d894499 | date | DATE:
| checkpoint | 3 - REVIEW SPECIFICATION
da3cc992-3260-5708-b4e4-06a34a09bdce | textbox | Drawing Reference Number:
e5491d43-8ef1-578e-92b4-8eaf3e60b4d2 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
515c2cc2-ac45-5796-949e-721b791ad967 | date | DATE:
| checkpoint | 4 - PREPARE SHOP DRAWINGS/LAYOUTS TO LATEST ARCHITECTURAL DRAWINGS
1c6407e7-3d26-507a-ad33-08ae7964d1d3 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
d060f218-b814-5cac-875d-d367a105206a | date | DATE:
| checkpoint | 5 - DESIGNING PIPING LAYOUT - SPRINKLERS: AS2118.1-2017 – Section 2; All new sprinkler systems shall be hydraulically designed in accordance with the requirements of Section 14 (hydraulic calculation of Sprinkler Systems). HYDRANTS: AS2419.1-2005 – Section 2; Fire Hydrant systems shall be compatible with the equipment and procedures employed by the attending Fire Brigade
a870b07f-bbb1-5359-9934-ec9c2afcb5de | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
14fe8e1d-fe41-5310-ba3a-bca94d2ebb22 | date | DATE:
| checkpoint | 6 - PREPARE SPRINKLER VALVE DRAWINGS - AS2118.1-2017 – Section 8.2.3(b); All sprinkler stop valves shall be clearly labelled on this Sprinkler Block Plan
d8528eeb-581a-5a98-8c18-dd820cf270d7 | textbox | Drawing Reference Number:
aac8df5d-76e1-5b71-ad4f-f90b14358921 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
61ac235e-9c78-5703-809c-e6a41c71560d | date | DATE:
| checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL - Clients Specifications In House QA
66229b8b-3679-5f0b-a3a1-926793b34c0f | textbox | Drawing Reference Number:
b33f01c7-343b-5078-bbb1-2165bd57a3eb | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
8ae43f2f-0dfb-5b23-bdec-415518512949 | date | DATE:
| checkpoint | 8 - REVIEW RETURNED SHOP DRAWINGS - In House QA
3702eca1-97a4-5077-9a76-94c9f9e10830 | textbox | Drawing Reference Number:
26ac68d6-788d-5648-9643-da59331b4fc6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4621bd8f-3e05-5a3c-8ee2-22a28c9e6cae | date | DATE:
| checkpoint | 9 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS - Per clients Specification
23aecc4d-e9a7-5206-9818-aef2b4055c10 | textbox | General: Please print name and company of all involved parties
317d56c8-82a5-5614-ae14-626e843dc08c | date | DATE:
| checkpoint | Hold Point Details
85af548c-38b3-5a56-824e-49dc1001455c | button | Hold Point Required: | Yes,No,Other:
e8488e25-9f10-5b76-84bc-93dec28ffe5c | textbox | Other (if applicable):
6b4af6b1-a531-5869-8855-c00e9b7977c2 | textbox | GM Sign Off - Name:
d4847cb3-ecbd-57be-a5df-6eba86449af2 | textbox | PC Sign Off - Name:
2f5dcaff-7a0a-5789-8537-98c7f96abf76 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-008 Sprinkler Installation | itp | ITPS-008 Sprinkler Installation |  | b8965e64-4bc2-4a17-a206-75a9f7f319ab
| section | Details
| checkpoint | 1 - PIPING, DRAWING & CUTTING SHEETS CROSS CHECKED - IN HOUSE
a7f8ba8e-97d6-5e01-ab72-4311823961bd | textbox | Drawing Reference Number:
8b729f7a-d83d-5849-91db-997c03d50ac6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
cf8c7c59-8733-50b9-86e5-51b6372334db | date | DATE:
| checkpoint | 2 - UNDERGROUND PIPING TO PUMP HOUSE FROM BOOSTER TO APPROVED LAYOUT & DETAIL - IN HOUSE QA
f2a4300d-d6f3-5028-9446-824471928f8b | textbox | Drawing Reference Number:
04057f80-05c0-5c6b-948a-028ba1f5bb51 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f88cce42-3aae-58af-9582-fd7a2abd7594 | date | DATE:
| checkpoint | 3 - PIPING & SIZE TO DESIGN CRITERIA - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes shall be supplied new and conform to the standards and relevant requirements. Latest Design Drawings
024bb0c3-e88b-5446-a8f9-ee82647aa8d2 | button | W5.5 Pre – Commissioning | Pass
630fe848-d76f-5a46-a12a-952c13509ec5 | textbox | Drawing Reference Number:
07b8bddc-5133-521d-a095-b4904746ebea | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e3bb2836-2103-507b-a9ee-7b041be1fc9c | date | DATE:
| checkpoint | 4 - MANUFACTURED FITTINGS TO DESIGN DETAILS - AS2118-2017 – Section 7.1; All fittings shall be supplied new and conform to the standards and relevant requirements.
7bbd934a-122a-5a9d-a221-cf08c17e5e2a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e69eb898-9d05-5979-afc2-f03d9d15be89 | date | DATE:
| checkpoint | 5 - PIPEWORK SUPPORTED BY SEISMIC BRACING - AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
39c64afe-8f62-59a7-b60f-e225aa9aa0b9 | textbox | Drawing Reference Number:
49f2f49d-66f5-560e-9a64-c539370f6527 | note | ○ Construction Issued Drawings Number:
c83b5de2-8ad0-5ae8-a045-bd0332a014c9 | textbox | Approval by: Please print name and company of all involved parties
ef8a65ed-9fd7-5105-9db2-a21571e6a253 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b81b8158-7371-5d18-8666-bfd061258ece | date | DATE:
| checkpoint | 6 - PIPING FIXED TO SPECIFIED REQUIREMENTS - AS2118.1-2017 - Section 7.8; Sprinkler supports shall be of the correct type installed in the correct locations and meet required load ratings for the pipe they are supporting.
1c98cd36-1c3b-5b5a-84da-d89f8ad58f2b | button | W5.5 Pre – Commissioning | Pass
c3e2dd59-938b-541b-8802-81c7bea0312a | button | W5.6 System Checks | Pass
916bf14b-205c-56e0-b7e3-efdcf809f21d | textbox | Drawing Reference Number:
802a935f-05e9-54b1-b41c-3f67d4f0e5e2 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
942cc24c-f8fc-5011-a694-93cc026a77b6 | date | DATE:
| checkpoint | 7 - VALVES TO DESIGN DETAILS - AS2118.1-2017 – Section 8.2 – each installation shall have a main stop valve fitted, have clear identification and be shown on the Block plan.
440a8da0-85a6-5329-8c81-12d83b1f1f4d | button | W5.5 Pre – Commissioning | Pass
5ec7e58e-4619-51b0-94e0-3e50b985e2b5 | button | W5.6 System Checks | Pass
dccf2598-5d18-55e6-b2d0-973409af96a8 | textbox | Drawing Reference Number:
edb26e39-d030-5d2e-8366-d184245ae7f2 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
8e09596b-828e-548e-aa63-1f96a3b87c20 | date | DATE:
| checkpoint | 8 - SPRINKLER INTERFACES FITTED OFF - AS2118.1-2017 – Appendix H – check to ensure alarm interfaces are fit off and tested prior to sign off
0c315dc4-bff4-5c3b-87f8-5b4d932ef763 | button | W5.5 Pre – Commissioning | Pass
d29e6e3d-6302-5702-8f89-aa5a2aa7bf3a | button | W5.6 System Checks | Pass
56f870ec-f896-5c69-b85c-5facb9a2aabd | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
69ec0a44-d43b-5fcb-b5a0-a20f4eb1f01d | date | DATE:
| checkpoint | 9 - WITNESS DRY FIRE TESTING OF VALVE SETS AND MONITORING EQUIPMENT - AS1670.1-2018, AS2118.1-2017 – Appendix H6 – system tested in accordance to the standard prior to witness testing with client or QFES.
d014c727-9d75-56b3-88ad-a199c2a1413f | button | W8.2.2 Witness Requirements | Pass
80936da8-6f84-5534-9323-b38adab52aa0 | textbox | Witnessed by: Please print name and company of all involved parties
14f6f499-569d-4a93-979a-3d64ef53366d | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b8507125-651c-5cc7-9c4f-b4d93da373ff | date | DATE:
| checkpoint | 10 - SPRINKLER HEADS FITTED OFF - AS2118.1-2017 – Section 5 Approved and up to date Reflected Ceiling Plan (RCP)
e3ec8212-29d5-5147-ba5d-8021c2c63db1 | button | W5.6 System Checks | Pass
c595c89d-f834-5b85-9954-827176fdc0cb | textbox | Drawing Reference Number:
71d6c1cc-d465-5a78-ac41-9218ec89c0e3 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
8a7ba3b0-9f3c-557f-a29a-7bafbac0e028 | date | DATE:
| checkpoint | 11 - OMISSION OF SPRINKLERS - Fire Engineers Report (FER)
b2ea29cd-a02e-5297-bfa5-ef142a94cfe1 | button | W5.6 System Checks | Pass
9e1c5466-6413-5d54-8086-24960a35109d | textbox | Drawing Reference Number:
e1671474-6b3a-5782-8743-8b4f6080aa35 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
a5adb717-b03c-5d87-a112-b4198f6a33cb | date | DATE:
| checkpoint | 12 - SPARE SPRINKLERS & KEY INSTALLED & TYPE CHECKED - AS2118.1-2017 – Section 6.7 – spare sprinklers of each type used in the installation shall be provided and located in a spares box.
f97bd35f-141b-5ab4-9e78-756f7162488e | button | W5.6 System Checks | Pass
dc7cd86c-e789-51a2-a9ed-e68096489ead | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c8d07ac2-3f48-55e1-8a51-dcf9051d2969 | date | DATE:
| checkpoint | 13a - LABELS & BLOCK PLAN INSTALLED - AS2118.1-2017 – Section 8.3 – Block plans shall be provided, be of permanent design, water and fade resistant
4c260486-6aa7-58f6-a9c7-5c753618686b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
063121a5-05bc-5e40-afc2-739cdaaca44d | date | DATE:
| checkpoint | 13a - CONTROL ASSEMBLIES - AS2118.1-2017 - Section 8.1 – shall be located in a secure location and readily accessible to the fire brigade.
09553069-d1dc-5f59-b99d-6a9346fcf2b9 | button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
b90f5619-01cf-5035-a908-fbf92c9bee98 | textbox | Performed and witnessed by: Please print name and company of all involved parties
faa9f391-65b2-5b33-a1b9-5b37423312b5 | date | DATE:
| checkpoint | 13b - LABELING OF CONTROL EQUIPMENT - AS2118.1-2017 - Section 3 (3.3.4) – shall be permanently affixed fade- resistant and water resistant
c52dc809-01d7-5dd4-afe1-4124d04b6261 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
d1ac72e7-5810-5855-bc5d-74b0e9e5fdb8 | date | DATE:
| checkpoint | 14 - FIRE RATING TO PENETRATIONS CORRECT AND LABELS AFFIXED - BCA
3e6e42d7-7167-56d0-bbaa-974ec251c266 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f8246cf7-57c5-54fc-aa0d-0b3a29de7491 | date | DATE:
| checkpoint | 15 - ACOUSTIC PENETRATION SEALED - AS4072
8a569626-5af1-5f4e-896d-74d139932348 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
bd25b1dd-f7cc-5304-8799-00fb1fd383c3 | date | DATE:
| checkpoint | Hold Point Details
bbcbb141-908b-52b5-a465-71ef63bc6c4a | button | Hold Point Required: | Yes,No,Other:
a06b36b1-009e-5f7e-8bf2-092de7546592 | textbox | Other (if applicable):
5f92a269-706a-5215-a61e-9674e53093e3 | textbox | GM Sign Off - Name:
90f602e7-7176-5940-b7f7-0203ff6eeba6 | textbox | PC Sign Off - Name:
a8122c50-ba6c-56be-9324-1509d45c876d | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-009 Sprinkler System Commissioning | itp | ITPS-009 Sprinkler System Commissioning |  | 87d22ebe-ea73-4d08-b0d0-9fcc84eff4c2
| section | Details
| checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
191419f5-283c-5888-a7ce-0a0e935b0189 | button | W5.2 State of the System | Pass
91dede89-a3ec-5775-ba8d-89b7f8098db9 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b276a28b-31cb-54f3-8953-3e849135be0d | date | DATE:
| checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
c32092f8-0723-5d6b-b7e6-952a9353b130 | button | W5.2 State of the System | Pass
ff8eef12-2bc6-5fa5-a733-22b43cebe3ca | textbox | Test performed by: Please print name and company of all involved parties
c01973b6-4cd7-51bb-8c08-ae996ea92fe3 | date | DATE:
| checkpoint | 3 - AIR TEST INSTALLATION BEFORE WATER FILL - AS2118.1-2017 – Section 7.9.4 – hold 300 kPa for 30 minutes without a 10% loss.
cd742355-5c43-5b04-84d6-62bc221585d8 | button | Hold Point Required: | Yes
28a04ff0-1a4a-51d7-bcb7-0c06e922dc7b | button | W5.4 System Filling and Venting | Pass
410be762-8414-57f0-a613-d025ff0e2c79 | textbox | Test performed by: Please print name and company of all involved parties
e895f7c2-c81b-59c2-9ca6-add6ad3f0648 | date | DATE:
| signoff | HOLD POINT
| checkpoint | 4 - STATIC TEST INSTALLATION WITH WATER TO 1600KPA - AS2118.1-2017 – Section 7 (7.9.3) – system tested to 1.6MPa and holds pressure for 2 hours
049b9bcc-6983-5978-a622-29054852e3b0 | button | Hold Point Required: | Yes
71107acd-ef7b-5ed3-aa20-56efcf4cf7f3 | button | W5.4 System Filling and Venting | Pass
d701db62-cbae-5b8e-bfde-932e9674498d | button | W5.4.1 Pressure Testing | Pass
a66fcb0b-3e0a-5c3d-b190-bb040555f0e9 | button | W5.5.2 Flushing Procedure | Pass
d1d6a48d-233a-529e-b6a1-853a7880161b | button | W5.7 Static Completion Records | Pass
47ba1fee-398d-5eda-a72a-a23889a90ed2 | textbox | Test performed by: Please print name and company of all involved parties
f10c8b69-1298-59f5-b656-5263ca999409 | date | DATE:
| checkpoint | 5 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
a5416993-59ad-5ffa-a0ea-7040620095b1 | button | W7.2 Flow Rate Measurement Tolerances | Pass
c94240d1-ae77-591e-acfd-1c22d23c6818 | button | W7.5 Preliminary Flow Rate Check | Pass
3b5391a3-6871-5cfe-9d76-ca5898cc9624 | textbox | Test performed by: Please print name and company of all involved parties
2b973774-7318-5fbc-a2a0-97132be5bd98 | date | DATE:
| checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
0cd149ee-fdf2-56f6-b568-6e909ccbdbdd | button | W5.6 System Checks | Pass
375383a4-9404-56b3-936e-fadb9c9d370c | button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
7852e6a5-862d-5ef5-87e8-d360d0afbbea | textbox | Test performed by: Please print name and company of all involved parties
9127040c-45ac-52e1-a65a-adddc758652c | date | DATE:
| checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
c6a7534e-e4b9-5a01-8d76-40a269665798 | button | W5.6 System Checks | Pass
bb82baf2-8718-5312-862e-6cc3e37d43b2 | button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
12733177-6996-5ac5-80a4-32fc5aba4f22 | textbox | Test performed by: Please print name and company of all involved parties
71193325-c816-52cd-b483-d41b91d225ef | date | DATE:
| checkpoint | 7 - CONDUCT 100% TESTING OF PRESSURE SWITCH, FLOW SWITCH & VALVE MONITOR - AS2118.1-2017 Appendix H6 – equipment to be tested to procedure set out in standard and in conjunction with Fire alarm workers.
05f8ff2c-adc0-537e-a912-11c42fdd1328 | button | W5.6 System Checks | Pass
fa28d8c5-c08a-5624-99cf-448d60bebf42 | button | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
c8a5676b-2670-568a-b167-5f936e4ca5b9 | textbox | Test performed by: Please print name and company of all involved parties
c5fac5b4-d4e0-53b8-87f3-cc95679f8a96 | date | DATE:
| checkpoint | 8 - CHECK PUMP PRESSURE AND FLOW REQUIREMENTS - AS2118.1-2017 - Section 14.9 – shall be capable of satisfying the flow and pressure requirements of the design +50kPa.
6d993509-e030-55d0-9266-9cbd66bd80aa | button | W7.2 Flow Rate Measurement Tolerances | Pass
c295a8b0-020e-59cd-842c-8c293ea0ecdf | button | W7.5 Preliminary Flow Rate Check | Pass
45f5b53f-686c-5e2c-9d2c-c2acff080769 | textbox | Test performed by: Please print name and company of all involved parties
9b03aee2-cbe2-5af5-aaed-7447ad25f7fb | date | DATE:
| checkpoint | 9 - WITNESS TEST HOLD POINTS - PIPE TESTING PROCEDURE
f279de52-ee0f-57b2-a456-e1791adc10b5 | button | Hold Point Required: | Yes
58d75261-bee2-5178-a4b1-31b2caaccc28 | button | W5.7 Static Completion Records | Pass
42288b33-9af7-5672-9f01-2ee72d0032d4 | textbox | Test performed by: Please print name and company of all involved parties
1e76972d-5d7b-4ae5-bb9f-86e36e401658 | textbox | Witnessed by: Please print name and company of all involved parties
cb8c22ac-244a-582c-862e-624e5f00d258 | date | DATE:
| signoff | HOLD POINT
| checkpoint | 10 - HYDROSTATIC SPRINKLER PIPE TEST - AS2118.1-2017 Appendix H & Section 7.9.3; All new installations, trunk mains and water supply connections shall be capable of withstanding for a period of 2 h, without loss of pressure, a hydrostatic test pressure of 1600 kPa.
f3325c52-c7f6-5f1e-9756-1ea24abaee11 | button | Hold Point Required: | Yes
fff7b0f5-7052-5da0-a6eb-607fc94eed32 | button | W5.7 Static Completion Records | Pass
0c5dfc69-a0ff-5a81-b8fa-b39e9974d870 | note | ○ As per GM Fire ITPS-013 Sprinkler Pipe Testing.
97271bdb-f70c-512c-8c70-20e8d003952f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
919747f7-b536-4985-88c0-9b71824046e6 | textbox | Test performed by: Please print name and company of all involved parties
28a45c1f-c743-5fdb-b595-4886933595d8 | date | DATE:
| signoff | HOLD POINT
| checkpoint | 11 - COMPLETE FORM 71 SPRINKLERS - NCC 2019, AS2118
a3a42ab2-ab28-55a8-a10a-17f135f2e47c | button | W7.10 Commissioning Certification | Pass
529db5fe-e667-57c7-b809-5a0fb2629432 | textbox | Certificate: Please print name and company of all involved parties
7361a3dc-9af6-5611-9ef4-a33daffc081a | date | DATE:
| checkpoint | 12 - COMPLETE FORM 71 HYDRANTS - NCC 2019, AS2419
cf940cc5-9f4b-558c-a0af-bf336e047388 | button | W7.10 Commissioning Certification | Pass
6085eca7-97d2-5e1a-9a6e-9ab787c2be4a | textbox | Certificate: Please print name and company of all involved parties
6b008284-fa83-5254-ad2e-564a406d2608 | date | DATE:
| checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENT, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS - In House QA
0073a765-a102-54ae-ab8e-30128cdc5210 | textbox | Certificate: Please print name and company of all involved parties
02abb706-2294-5dba-b5f5-61bf3f20191c | date | DATE:
| checkpoint | Hold Point Details
2e6654d9-30f5-5332-a522-2ddc2f3119f7 | button | Hold Point Required: | Yes,No,Other:
34197039-a980-5728-9388-dad859c95cc7 | textbox | Other (if applicable):
3a63e46b-2e4b-5dab-ac21-ee839909a6a5 | textbox | GM Sign Off - Name:
58d38a38-fd4f-5608-bf3f-fd14e851570b | textbox | PC Sign Off - Name:
b2d719f5-1acc-56af-8781-46fc19d7bdd4 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-010 Brigade Inspection Sprinklers and Hydrants | itp | ITPS-010 Brigade Inspection Sprinklers and Hydrants |  | d9cef835-6d8b-4c53-8038-d799bf7a1132
| section | Details
| checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
a969ff56-5663-5391-b0b7-a5f77bec8833 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
2356c08e-7faa-5b72-98a9-cb459ed5f91b | date | DATE:
| checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
af67527d-5250-5a8f-ac10-67a270346b5b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
1aaf4b76-64d3-5594-9725-6f681006c217 | date | DATE:
| checkpoint | 3 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
ddc2b9a6-ef2b-5442-a870-5cfde0dc82d9 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e1975c8a-6d32-5c85-a392-d62f56b28ebc | date | DATE:
| checkpoint | 4 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
0362f8ed-af00-520e-9dc6-3a8f134bbe3d | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6bd22fa7-3cfe-527c-a87a-770cdbb1cc00 | date | DATE:
| checkpoint | 5 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
55ae55ce-44c1-5c77-bd2d-edd2363b1f6e | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
f41431e7-0c36-5a53-add6-d271200e529a | date | DATE:
| checkpoint | Hold Point Details
e1f67be9-e3bc-5c6a-8053-c640a06cd2ca | button | Hold Point Required: | Yes,No,Other:
0653fdf2-50b0-5c1c-a840-ab58dd8cf7cb | textbox | Other (if applicable):
5e0ef3ed-2931-5bfa-9df2-7431afd8d7bb | textbox | GM Sign Off - Name:
70f51f8b-6d87-5c24-a877-331f9981195e | textbox | PC Sign Off - Name:
d38b432e-8f72-5a74-afb4-338c69e3ceb0 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-011 Pipework Pressure Testing |  | ITPS-011 Pipework Pressure Testing |  | e0303800-66ff-4e5d-a795-0d5656e545e2
| section | Details
| checkpoint | Test Information
d71ba73f-3ef4-5490-8f80-0e1c2940cc5a | textbox | Maximum System design pressure:
3edc4f22-2542-5073-81fc-bca83f90c947 | textbox | Required test pressure:
aee9b2ae-f030-54f8-925c-28902f8b9c0a | note | STOP TEST IMMEDIATELY IF PRESSURE GAUGE REACHES 1650 kPa
a848a8c0-db2f-51f7-8985-d4e207c5ca14 | button | Hold Point Required: | Yes
a69494c2-c869-5635-8479-4e0511afdc91 | textbox | Holding time:
30891645-af68-55ba-aa50-1cf9d93ad7a7 | textbox | Description of test configuration (attach sketch or piping and instrument diagram):
10d849e9-532e-5f8b-9710-9966c441151c | textbox | Test fluid:
064206d7-c128-503c-8a93-3fdff618c33d | textbox | Test Fluid Volume:
| checkpoint | Test Equipment
fc7bedbe-7cd0-5857-bc00-6014f24a82bb | textbox | Pressure Gauge:
0c9b2a52-2a47-52ef-b5f1-512d7e9792c0 | textbox | Pressure Relief Valve:
1feaec21-e745-5767-9633-71db56bb09f2 | textbox | Bleed valve:
| checkpoint | Safety/Environmental Controls
e6967557-0e79-5b07-a656-9e19aeb2cf9e | textbox | SWMS Name:
3036397a-547e-5ad2-a7ce-4cd47ff19ec5 | button | Have all workers reviewed and signed off on SWMS prior to commencing work? | Yes,No (do not commence works)
c91f4c63-7d5f-5646-9786-26e60c9ce96e | textbox | Safe disposal of test fluid:
292f874a-b16a-5747-b390-4b499094872c | textbox | Test area controls (barricades, signage, etc.):
4b3043b0-f72b-5c05-8c59-f47bbe3d61cb | textbox | Inspection requirements (before, during, and after the test):
933bf8f2-70f4-50a5-aca1-e0f0fb5d638c | button | Is test equipment rated for test pressure: | Yes,No (do not commence works)
b9003231-56ea-575e-a6b5-ab3bf53545fa | button | Are end caps sufficiently tightened: | Yes,No (do not commence works)
fa50cb29-514c-5df5-8f73-08f66566e6df | textbox | Pressure Gauge reading at completion of test:
ecbe351f-b857-5fbc-8dfb-49a02905dcb0 | textbox | Any visible water leaks?:
697f50c7-9292-59cd-886e-a2e9b4bc464e | textbox | Test Date and Time Commenced:
27f27fb1-78f7-5755-8227-04adfeb45758 | textbox | Test Date and Time Completed:
| checkpoint | Approvals
0d7b1e49-d1ca-5e35-af0c-9bbc254cdc90 | textbox | Supervisor in charge of test:
6c2a2921-b001-5575-bec1-ec603a4c98ad | textbox | Person conducting test:
a641222e-81ba-5b9a-ba11-e4616f40c8e1 | date | Date:
| checkpoint | Hold Point Details
db9d36a3-2fec-50bc-8538-d8b7f281c812 | button | Hold Point Required: | Yes,No,Other:
7e2ad56c-35ae-55fc-822d-3b4c4091a16f | textbox | Other (if applicable):
8fb0ea7c-2b4f-5705-ae0f-fa1f69ed15e9 | textbox | GM Sign Off - Name:
3930912f-465f-537b-8f9b-1369b82e235e | textbox | PC Sign Off - Name:
cef567d7-33b1-54f1-8bdd-06cecc6e53e3 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-012 In Slab Conduit Installation | itp | ITPS-012 In Slab Conduit Installation |  | 3f734621-7d45-403b-bf9b-98985fdd1ecc
| section | Details
| checkpoint | 1 - CHECK CONDUITS ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA - In-house QA
1d4d54b6-61c5-55a5-bc17-fcafd822cc07 | textbox | Drawing Reference Number:
3f00b1a5-c401-5cc9-96f6-b3d6fc3103d3 | date | DATE:
| checkpoint | 2 - CHECK CONDUIT ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA - Shop drawings (certified by an RPEQ engineer) are to be provided for each and every item required within 1170.4 Structural design actions – Earthquake actions in Australia.
4d767396-ad74-5214-a089-f107d1687b04 | textbox | Drawing Reference Number:
63662228-becf-5361-b037-9af77fea6063 | date | DATE:
| checkpoint | 3 - INSTALLATION, CONDUIT IS JOINED CORRECTLY - Installation is in compliance with AS 1170.4 Structural design actions – Earthquake actions in Australia.
324ca920-7767-5f4e-8739-aa28e114ce76 | textbox | Drawing Reference Number:
6415e655-f646-5319-85c1-0396ac43487c | date | DATE:
| checkpoint | 4 - CONDUIT IS TIED IN
87fc4d82-0207-51a4-83a4-70b4fc735966 | date | DATE:
| checkpoint | 5 - CONCRETE COVER IS IN PLACE - General Technical Requirements – Services Ripley Sub-Acute Facility (RSAF) 2.2.3 - 9. All Fire services penetrations post concrete pours are to be immediately sealed with sheet metal cover plates (mastic or similar) to prevent water ingress. Plates to be fixed by use of nylon anchors or similar. Plates to remain in place and maintained until directed by Hutchinson Builders to remove.
f8e1478e-8dea-5143-ad8b-73e40c6aa03c | textbox | Drawing Reference Number:
e782a2e2-c839-54c5-a510-dc5daac59887 | textbox | Construction Issued Drawings Number:
f345e4fd-195b-56e0-ba35-8f341112d09a | date | DATE:
| checkpoint | Hold Point Details
e933d674-6e4f-5ac0-8454-114932b6d60f | button | Hold Point Required: | Yes,No,Other:
7b6245f8-135c-55bc-81d9-e85647ae9cc7 | textbox | Other (if applicable):
44e88cf3-cf50-5199-a59a-6ff2df77334b | textbox | GM Sign Off - Name:
c310eec6-1061-5275-885f-06e3bf9bf329 | textbox | PC Sign Off - Name:
5bb0d0c1-fcd4-5df4-839d-9c9472e4a927 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-013 Electric Fire Pumpset Installation and Commissioning | itp | ITPS-013 Electric Fire Pumpset Installation and Commissioning |  | 8220df1b-848c-469b-93f9-5d076c02e993
| section | Details
| checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage - AS2941.1-2013 – Section 11 Installation
0976af5c-28cf-5a02-93c4-6ab15300aebd | button | W5.2 State of the System | Pass
55342869-d099-55bc-b011-d32f83e08ae6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e7be2c99-0d3c-51ee-ab7f-93d90d3b19cc | date | DATE:
| checkpoint | 2 - Check clearence of pumpset - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly; - AS2941.1-2013 – Section 11 Installation
deb2f47c-1698-5023-88f9-120c80e998fa | button | W5.2 State of the System | Pass
91a3485d-4cea-5567-9610-0ae903960510 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
180fdf19-473a-54b9-81f1-81c4121004b9 | date | DATE:
| checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided - AS2941.1-2013 – Section 11 Installation
a947156b-cd43-52b6-a62c-1942a5634c86 | button | W5.2 State of the System | Pass
09db26e6-65e7-5c13-8110-3e62380ea915 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c4727975-f1ca-5abf-adb6-6ba943e040dc | date | DATE:
| checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels - AS2941.1-2013 – Section 11 Installation
37eb9087-2de6-5e82-89d3-e99c3acf204e | button | W5.2 State of the System | Pass
0af66815-07ab-5e1c-82cd-70dce93568d6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c7c2e49b-136f-5eb3-85f3-28dcf2f8bf3d | date | DATE:
| checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides. - AS2941.1-2013 – Section 11 Installation
2c511dae-7029-5f23-ae6e-930740ac2f37 | button | W5.2 State of the System | Pass
923d08bb-daa6-5ef5-9ee7-9c688efa6844 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6dc181c6-b823-5991-bbb6-fb8df070c785 | date | DATE:
| section | Electric Pumpsets
| checkpoint | 6a - Check the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance. - AS2941.1-2013 – Section 11 and 12
37417757-46e0-5b2d-9c62-7c726a20c750 | button | W5.2 State of the System | Pass
b5ee7325-7975-537e-b0a7-b695fe644ec2 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
9624ed7c-f781-5f07-a59f-68969fe304c2 | date | DATE:
| checkpoint | 6b - Check the direction of rotation - AS2941.1-2013 – Section 11 and 12
b086f292-c971-5292-ac3a-e775e5f5be54 | button | W5.2 State of the System | Pass
013f2eb8-4274-532e-af99-3fbdf683c92f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
ca1a1ce4-3010-5c16-8ba6-7c3cd3bf3e7a | date | DATE:
| checkpoint | 6c - Ensure that the delivery from the pump under test is the only supply to the measuring device and that all flow from the pump passes through the device. - AS2941.1-2013 – Section 11 and 12
3f68f85d-dc17-5eb6-9c53-03b38dd41109 | button | W5.2 State of the System | Pass
c78f7794-e4df-56ea-aaa1-b4c4a30519b7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
139304b6-e666-5ace-8e2c-dd7e75998e9e | date | DATE:
| checkpoint | 6d - Ensure that the pump is primed and that lines are clear, valves correctly set (open, closed or adjusted to required pressure), and that water is available. - AS2941.1-2013 – Section 11 and 12
3b7a9925-56c1-5b1b-aec5-e8527ca02645 | button | Hold Point Required: | Yes
425cd1c0-a554-5782-bdeb-02ae52a3aa09 | button | W5.4 System Filling and Venting | Pass
759c33ac-c3be-5845-a9d4-6223f56392f5 | button | W5.4.1 Pressure Testing | Pass
a66d10bf-08ad-5b31-afc7-d134edae7a59 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e63f10f9-6a9c-5b5e-96be-890be1c976fa | date | DATE:
| signoff | HOLD POINT
| checkpoint | 6e - Isolate all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and compression-ignition engine driven pumps - AS2941.1-2013 – Section 11 Installation
a7015eba-3f5c-56b7-a0e3-43b09f68be6c | button | W5.2 State of the System | Pass
08f92f51-5127-549e-a9f4-4f4f49563e92 | button | W5.4 System Filling and Venting | Pass
c0bae3dd-09fd-58bc-b65b-fbcb3496c2d6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c0d502c8-e77b-5d0c-94c5-4c946f677acd | date | DATE:
| checkpoint | 7a - The following shall be reported – Pump plate details / photo - AS2941.1-2013 – Section 12
96825fd9-6e2d-5198-aaa0-1e80af9dc3bd | button | W5.2 State of the System | Pass
ecf67ab0-a296-5e77-b322-63aa7bfca071 | textbox | Test performed by: Please print name and company of all involved parties
b80f76fa-bd30-544d-ab9e-5ac24be7d95c | date | DATE:
| checkpoint | 7b - Record - the pressure in the system at which the pump starts automatically. - AS2941.1-2013 – Section 12
aa1bc76b-8ae4-565f-84c2-e9ffd7de8edd | button | W5.2 State of the System | Pass
b6a15d23-b152-5e75-a266-989561b40dfc | textbox | Test performed by: Please print name and company of all involved parties
6aeb2099-0dcc-5665-9e76-7bcb46ddba09 | date | DATE:
| checkpoint | 7c - Record - Pump shut-off pressure on delivery gauge - AS2941.1-2013 – Section 12
4d155a5b-4f97-5f6d-8247-48377e34a77f | button | W5.2 State of the System | Pass
e12f9787-d062-5b79-8ef6-7abeaa67f30e | textbox | Test performed by: Please print name and company of all involved parties
bafc7cd6-f651-5ff2-b258-818fec0e4b40 | date | DATE:
| checkpoint | 7d - Record - Motor current at shut-off pressure. - AS2941.1-2013 – Section 12
9dbe7db4-6d50-5d00-a080-165e16ae2d69 | button | W5.2 State of the System | Pass
5c2a271a-a8f1-5771-a867-a94dcebc65ea | textbox | Test performed by: Please print name and company of all involved parties
c1819dd2-17ce-5f57-8825-565464089131 | date | DATE:
| checkpoint | 7e - Record - Delivery pressure at maximum flow - AS2941.1-2013 – Section 12
a8b3e185-b073-5eca-8217-055b76f696e0 | button | W5.2 State of the System | Pass
55aea28a-707f-551e-93bb-ec2c21dde638 | textbox | Test performed by: Please print name and company of all involved parties
9b79b733-d6a0-5e6d-87c1-1a839e4b4de9 | date | DATE:
| checkpoint | 7f - Record - Pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate - AS2941.1-2013 – Section 12
181e0889-bbd4-5a12-9973-b86b435b7b1b | button | W5.2 State of the System | Pass
5c2e3d9b-5505-56de-aa44-9e92dd90d692 | textbox | Test performed by: Please print name and company of all involved parties
f1a3595e-13bc-5cf5-8158-f8a1ce659ac3 | date | DATE:
| checkpoint | 7g - Check – (i) periodically check the temperature of the bearings and stuffing box leakage and note any abnormality; (ii) check that all alarms and indicators, both visual and aural, have been activated; and (iii) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped. - AS2941.1-2013 – Section 12
8ca01de5-7ad1-55e0-af4b-cabf37a6843e | button | W5.2 State of the System | Pass
ad8f9f2f-6388-5e87-8f04-2973e215baca | textbox | Test performed by: Please print name and company of all involved parties
25826734-12aa-5ff5-b3c6-401c5a955be7 | date | DATE:
| checkpoint | 8 - Whether the electric pumpset, together with its associated control gear and ancillary equipment, functioned correctly. - AS2941.1-2013 – Section 12
ad5f4f69-79d7-54e4-b2ae-e6d133ac9896 | button | W5.2 State of the System | Pass
6736e5ad-e493-5261-9492-fe00b985b8f9 | textbox | Test performed by: Please print name and company of all involved parties
9aae4c5e-5bfd-5949-9299-78400b13561e | date | DATE:
| checkpoint | 9 - Whether the pumpset satisfies the intended performance conditions (e.g. flow rate and head). - AS2941.1-2013 – Section 12
1fe15a7c-be44-55eb-be5f-975384806a75 | button | W5.2 State of the System | Pass
ab87b309-e6e9-5afa-8938-a7a405aaf492 | textbox | Test performed by: Please print name and company of all involved parties
90466251-2233-509d-a5b5-f72d8de4ac94 | date | DATE:
| checkpoint | 10 - Whether there is operational abnormality. - AS2941.1-2013 – Section 12
c9c31afd-e1d6-5311-a2a4-8ff983a4d3e1 | button | W5.2 State of the System | Pass
ae5d1682-806e-567e-aacc-183ebe37789f | textbox | Test performed by: Please print name and company of all involved parties
5af19f5c-7fbc-5399-be4e-ecd2d5fda6f9 | date | DATE:
| checkpoint | Hold Point Details
08eb478f-c40a-5ced-878e-55b3b0e5ec89 | button | Hold Point Required: | Yes,No,Other:
3df0aaf4-0cd9-5a39-b079-0a934069684c | textbox | Other (if applicable):
5dfbf4dc-f160-5dd3-8778-b6e758d7f127 | textbox | GM Sign Off - Name:
c9db8385-a821-5f7e-a58b-839d386cb491 | textbox | PC Sign Off - Name:
04e23378-fda3-5868-b15d-c8178c0a27a3 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-014 Diesel Fire Pumpset Installation and Commissioning | itp | ITPS-014 Diesel Fire Pumpset Installation and Commissioning |  | 2db1fdec-d190-48db-acb5-2787c6a78b45
| section | Details
| checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage - AS2941.1-2013 – Section 11 Installation
6fcf86a2-64c2-52dd-8b44-955ea5ad4900 | button | W5.2 State of the System | Pass
db8b0fec-b0e2-5b06-b6c9-fa83a9305063 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
b725de3b-2e89-5a61-9367-5272af168c6a | date | DATE:
| checkpoint | 2 - Check clearance of pumpsets - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly; - AS2941.1-2013 – Section 11 Installation
89428cdf-22dc-5eea-80f2-6ec0ebeba9d8 | button | W5.2 State of the System | Pass
56f7a393-9195-5a73-ab98-20da70f52b25 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
dfb4103e-2131-5cf4-84f2-b009fe23f256 | date | DATE:
| checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided - AS2941.1-2013 – Section 11 Installation
a18fb477-103c-509d-87e9-a0812bebfeb4 | button | W5.2 State of the System | Pass
26fdecf1-726c-529d-8929-37f538affd83 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6f943801-28cb-5819-a83d-ec2e6ae5d54f | date | DATE:
| checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels - AS2941.1-2013 – Section 11 Installation
689c947b-e410-57f8-80b6-ac73fa7980de | button | W5.2 State of the System | Pass
3c5e21b5-090b-5bfe-8be8-ff7d0faa6b24 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
1b418f4b-0f98-5c93-ab75-0b9ca2dcf44e | date | DATE:
| checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides. - AS2941.1-2013 – Section 11 Installation
3e301fcd-441f-57ff-8ff4-9d480738d5e6 | button | W5.2 State of the System | Pass
2f0d234d-cfc0-527c-80a0-b9aca4d3fcbc | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
00d36e2c-245c-5a0d-841b-c56972600f9c | date | DATE:
| section | PRE COMMISSIONING CHECK LIST
| checkpoint | 6a - Check the cooling supply system - AS2941.1-2013 – Section 12
5e44ea88-55b0-5fc2-9783-056c3d7b82ee | button | W5.2 State of the System | Pass
3b53d315-4973-5b43-bae4-3bcda37e2da6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
cea4a506-a5d1-5f5c-be78-c2947cd5b821 | date | DATE:
| checkpoint | 6b - Check engine fuel supply - AS2941.1-2013 – Section 12
78ee04be-adad-55e0-85cd-efb4a415554a | button | W5.2 State of the System | Pass
e852b99c-3110-54af-a28d-e359ff726114 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6ef88d6a-b6cd-5071-96ad-e7abfe7622ae | date | DATE:
| checkpoint | 6c - Check the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance - AS2941.1-2013 – Section 12
b0fdfeb0-3ce0-5e1d-aff4-d8a8a0980b39 | button | W5.2 State of the System | Pass
26d367c9-6c3b-54f1-bb9a-254ba6bef4fe | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
41c531bb-eb24-53cc-8c0f-339a14a2676c | date | DATE:
| checkpoint | 6d - Check the direction of rotation. - AS2941.1-2013 – Section 12
62a1e4c4-18d3-5d47-8ee8-d87d0a336e55 | button | W5.2 State of the System | Pass
a600202e-8431-57e4-899d-d9ba29635ac6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
72ab4b0a-faa3-5312-8d8c-b74b77068244 | date | DATE:
| checkpoint | 6e - Check – Engine lubricating oil is at the correct level. Check – the battery electrolyte level and the battery leads and connections. Check – exhaust system is intact - AS2941.1-2013 – Section 12
7f40a7ee-ee2d-54d7-8df7-d8006db3b0ea | button | W5.2 State of the System | Pass
70d6d389-8b13-5c67-a12a-3bf648c86132 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
222d6bcf-e6f5-5c11-b966-056c6e627269 | date | DATE:
| checkpoint | 6f - Ensure – pump is primed and that lines are clear, valves correctly set (open, closed, or adjusted to required pressure), and that water is available. - AS2941.1-2013 – Section 12
e0f2a091-a589-5cc3-9224-a3937a8698fe | button | W5.2 State of the System | Pass
2d57bfbc-384b-58a8-89ce-b139fdc85ae7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e47e79e8-a0f8-5d5c-bdd1-2630e8dac460 | date | DATE:
| checkpoint | 6g - Isolate – all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system. - AS2941.1-2013 – Section 12
6bbe4766-edb7-53fe-be6a-e6c994b9fe98 | button | W5.2 State of the System | Pass
c6d1ebe7-b004-5feb-8c8d-e594cbc7f833 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
ad5a1523-aa9b-5d4a-b216-ee72cdce0c22 | date | DATE:
| section | PUMP COMMISSIONING CHECKLIST
| checkpoint | 7a - Record – For automatic starting pumpsets, record the pressure in the system at which the pump starts automatically. - AS2941.1-2013 – Section 12
772e327e-2210-5511-a034-1d099b10cb4e | button | W5.2 State of the System | Pass
a60ed43c-c410-53b0-8f1d-1bd132c1617b | textbox | Test performed by: Please print name and company of all involved parties
cd69e63c-4aa8-51d1-a3db-f25bf7b6a27b | date | DATE:
| checkpoint | 7b - Record – Engine Oil Pressure - AS2941.1-2013 – Section 12
c6d03f30-297c-5453-ac79-91d153ef480e | button | W5.2 State of the System | Pass
6cb92a20-c203-5c67-8084-8e1272f53201 | textbox | Test performed by: Please print name and company of all involved parties
8683a9c0-df5e-576f-9356-04e99f648f9f | date | DATE:
| checkpoint | 7c - Check – Coolant Flow is correct - AS2941.1-2013 – Section 12
d1985b2a-6094-53ce-a216-d60bcaf3db2b | button | W5.2 State of the System | Pass
fef9a6dc-d43f-57ef-a817-f98d5dfd9d8f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
2726ede0-54f3-5e2d-ba5a-7a54b7f02826 | date | DATE:
| checkpoint | 7d - Check – That the fan is rotating and all fan belts are intact - AS2941.1-2013 – Section 12
7c52f8a4-dadb-5a7b-83cc-ae4a13fe55da | button | W5.2 State of the System | Pass
2d5184cc-2962-5027-be27-c634ac8a59f7 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
5d8e7b29-fa57-5789-bab8-8c6857ca4892 | date | DATE:
| checkpoint | 7e - Record – pump shut-off pressure. - AS2941.1-2013 – Section 12
5ada0706-b4b7-5b22-b157-b680c7aac474 | button | W5.2 State of the System | Pass
dcfeca9a-c12e-59f0-b4ef-193ab637acd3 | textbox | Test performed by: Please print name and company of all involved parties
a99ababc-9c61-543a-8a96-8bd8ea78ea2b | date | DATE:
| checkpoint | 7f - Isolate – the flow meter, partially open the test valve, and flush to remove any debris or foreign matter; open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter. - AS2941.1-2013 – Section 12
a0996b86-9925-5472-b5ac-eb6091530a95 | button | W5.2 State of the System | Pass
a0c3ed31-65d7-58f0-8dc0-87a72f7b030d | textbox | Test performed by: Please print name and company of all involved parties
a0af9640-e828-5336-ab31-d8421fa6fa66 | date | DATE:
| checkpoint | 8 - Run the pump for 30 min at maximum flow and record the following: (i) Suction and delivery pressures. (ii) Engine running temperature, which shall be within the engine manufacturer’s recommended limits. (iii) Engine oil pressure, which shall be within the engine manufacturer’s limits. (iv) Air temperature at pumpset. (v) Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate. (vi) Check that the requirements of Clause 9.3.6.2 are complied with by holding the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles. On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position and check if the engine starts immediately. - AS2941.1-2013 – Section 12
adddc62f-379c-5306-b48f-241b23a03938 | button | W5.2 State of the System | Pass
9f6f8ee5-3913-525a-a7b2-47cdf44ae6a0 | textbox | Test performed by: Please print name and company of all involved parties
fe9f92c9-4b10-50cf-bf69-3e7c76baf1d9 | date | DATE:
| checkpoint | 8a - During the operations in Item (h)— (A) periodically check temperature of the bearings and stuffing box leakage and note any abnormality; (B) check that all alarms and indicators, both visual and aural, have been activated; and (C) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped. If the pump failed to start alarms that are fitted on the pump fire pump controller and at the remote station, check that these alarms operate both aurally and visually. (j) Shut down and restore starting mechanism to stand-by status. (k) Restore power supply to the electric pumps and check correct status of indicators. - AS2941.1-2013 – Section 12
1cee6654-497d-5469-9187-6f2b51a7394c | button | W5.2 State of the System | Pass
6b91119f-ce0e-54c5-9b19-b1171756ecf5 | textbox | Test performed by: Please print name and company of all involved parties
64c7031d-2fd3-5033-af85-6c59ea51f6fb | date | DATE:
| checkpoint | Hold Point Details
f8fc6e62-a8e8-5aa7-b01e-01564dd24bf7 | button | Hold Point Required: | Yes,No,Other:
4f78fc85-4873-5430-8e55-cf839ae5c8c4 | textbox | Other (if applicable):
9b14f46d-3295-531f-b843-fbd36fb080e6 | textbox | GM Sign Off - Name:
7e2be269-f735-519b-b997-e4055cf44dda | textbox | PC Sign Off - Name:
e9bfbd1e-6feb-5580-b371-d72b3cf7b2aa | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-015 GM Tank Installation | itp | ITPS-015 GM Tank Installation |  | 6ad8da21-a67f-4e75-9ba6-5d397a52175e
| section | Details
| checkpoint | 1 - Confirm – Structural Elements as per AS2304 – Section 3 - AS2304 – Water storage tanks
62061959-1364-587a-bc5d-08e6458cae47 | button | W5.2 State of the System | Pass
ad7db643-b48d-5cef-bd03-8facf380c4a6 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
9aa32dc8-18d5-5270-ad41-dcd88eddcf80 | date | DATE:
| checkpoint | 2 - Confirm - Correct Installation drawing, onsite. - AS2304 – Water storage tanks
87442255-d15b-5b53-91bc-c987a894a614 | button | W5.2 State of the System | Pass
cb60f210-d15e-5312-b782-4d1e29dcce45 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4852a5ad-751d-5065-925a-7052628020c5 | date | DATE:
| checkpoint | 3 - Confirm – Ladder selection and orientation to submitted design drawings, Confirm – Nozzle selection as per submitted design drawings - AS2304 – Water storage tanks
d943a335-00b5-5df5-b42f-a5cf5843dfc4 | button | W5.2 State of the System | Pass
532c8234-093d-57b6-a72b-1c484d65cd1a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
27019d60-538d-523f-ace6-847bb7541351 | date | DATE:
| checkpoint | 4 - Confirm – Position of tanks with principle contractor onsite - AS2304 – Water storage tanks
deb7d906-7aa2-5dec-aa89-6ee26962f6ef | button | W5.2 State of the System | Pass
49a2928c-069b-5dc6-b056-cc9b40c9b97d | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
fe535ea0-46ae-5434-bdb4-3f7177d53005 | date | DATE:
| checkpoint | 5 - Confirm – Competencies and Authority to work of subcontractor - AS2304 – Water storage tanks
5465ce76-f593-549d-9875-5a6ee7b32267 | button | W5.2 State of the System | Pass
7b0d6c9f-e4b7-5924-a2c6-2b64e456a05b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4c330b7a-8624-5fe0-82d4-4049c7464d63 | date | DATE:
| checkpoint | 6a - Commissioning – Structural inspection prior to filling - AS2304 – Water storage tanks
ed4313b2-3177-5b88-9add-f114c01e2a7f | button | W5.2 State of the System | Pass
cc218157-d716-5392-97eb-caa4e041ec28 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
5ce4bffe-e7e2-5ab8-b994-856d78caead2 | date | DATE:
| checkpoint | 6b - Commissioning – Inspect all ladders for conformance and clearances and position of tank accessories - AS2304 – Water storage tanks
08d882bb-b2e9-5464-83da-b060823b4d92 | button | W5.2 State of the System | Pass
e4c3bd07-dbc3-5062-8338-1a553f0f6369 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
e0dd3b59-a79a-5b76-bc73-24b0dc3a6e19 | date | DATE:
| checkpoint | 6c - Commissioning – Hydrostatic inspection after tank is filled to maximum capacity - AS2304 – Water storage tanks
ed31b7e3-5907-567f-93ef-f8ae9a51abbc | button | W5.2 State of the System | Pass
f1ea8f9e-f8c4-5059-8b74-04b65b83a6b0 | textbox | Test performed by: Please print name and company of all involved parties
459c40dc-6b14-5bd2-a7d5-20093227855f | date | DATE:
| checkpoint | 6d - Commissioning – Record any defects - AS2304 – Water storage tanks
6d5be43f-1cf2-5a44-be3a-6c59c7fff989 | button | W5.2 State of the System | Pass
87aa5cd6-143e-5481-b58b-816e03300268 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
162db7eb-a9ec-533a-9a55-1fb4501b47ec | date | DATE:
| checkpoint | 6e - Commissioning – Submit certificates and warranty periods - AS2304 – Water storage tanks
e5029ec5-f97c-59ba-8159-ea08992c513c | button | W5.2 State of the System | Pass
b9018c72-d7a1-5aa7-a3d5-4265e0d4a16f | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
2b2e2adc-e956-5555-a9c4-ad3e639d5077 | date | DATE:
| checkpoint | Hold Point Details
c63ec206-1a1a-5ff4-a7f8-2083e409a426 | button | Hold Point Required: | Yes,No,Other:
8cebb88f-d94b-516d-9d29-79a1e4516561 | textbox | Other (if applicable):
9a02705a-51da-548c-8eec-28850a26f806 | textbox | GM Sign Off - Name:
14357a76-87ca-5016-be44-36264c2fff49 | textbox | PC Sign Off - Name:
80f2fda8-10b2-528e-80f0-a01e1d41dd4f | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-016 Fire and EWIS Panel Installation | itp | ITPS-016 Fire and EWIS Panel Installation |  | d70ff261-48dd-47ca-bb78-d1ccc56e0b74
| section | FIRE INDICATOR PANEL
| checkpoint | Check – Location - (i) Installed in a location protected by the FDAS (expect where external to building) (ii) Operation of FIP shall not affect evacuation of building (iii) Located in an area which presents low risk of damage to equipment and persons (iv) Not mounted in any rooms containing sprinkler, pumps or motors
a6eeae12-fa39-51c6-9787-8b33d2e43530 | textbox | Performed and witnessed by: Please print name and company of all involved parties
5e20b5d1-7d96-53fe-b74b-23b53278622a | date | DATE:
| checkpoint | Check – Particulars (i) Have controls and indicators not less than 750mm and not more than 1850mm above floor level. (ii) Have unobstructed access to controls and indicators (iii) Be mounted above ground level to protect batteries/on a plinth
935ebe70-967b-5a9f-a89f-0df4795cabd6 | textbox | Performed and witnessed by: Please print name and company of all involved parties
896aa500-1593-5882-aa49-1a90064ba27b | date | DATE:
| checkpoint | Check – Where the FIP is obscured by a door ensure the words “FIRE PANEL” in letters not less than 50mm high. There SHALL be no other lettering on the door.
e17cd00e-43b8-5ff9-9826-153c6ed2e9f0 | textbox | Performed and witnessed by: Please print name and company of all involved parties
06353fb9-ef90-52f2-8ad2-b6e078eb4db8 | date | DATE:
| checkpoint | Check – Clearance. 1000mm in front of FIP and 500mm to each side shall be maintained.
513fe16d-7cf1-52d2-9bf3-f79c59efb5e4 | textbox | Performed and witnessed by: Please print name and company of all involved parties
05e29cb0-64ec-5911-ae7a-be829e9099ef | date | DATE:
| checkpoint | Zone Block Plan – Installation shall be securely mounted and easily accessible.
5b40d9cd-eac4-5da9-a393-3c440ecfcaca | textbox | Performed and witnessed by: Please print name and company of all involved parties
2c116653-2d3b-50d4-b583-93f1c415c452 | date | DATE:
| checkpoint | Manual Call point – Manual call point must be installed at the entry point to site if the FIP is not located close to that point.
88c0b431-ea8f-59ba-af79-197e861fc0b0 | textbox | Performed and witnessed by: Please print name and company of all involved parties
f15e4372-e027-549f-b329-e8a9599a05fe | date | DATE:
| checkpoint | Check – Power cabling is installed at FIP location
98506e26-53ea-576e-926c-2a6656d89cfc | textbox | Performed and witnessed by: Please print name and company of all involved parties
92bfbaeb-38eb-5fb2-9157-0c5039eaa57b | date | DATE:
| checkpoint | Check – Location strobe on front of building is installed and operational.
5fc10584-afcb-52a3-ab32-d8587ceb3243 | textbox | Performed and witnessed by: Please print name and company of all involved parties
b16b587e-a7e2-5960-bd44-9fd3bb38332f | date | DATE:
| section | EWIS PANEL
| checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
63ac244c-9b84-58e8-9e03-4d8eda2e5681 | button | C5.4.0 Wiring | Pass
c45ec71a-5ef5-506e-8e5e-ccf64d15a4f9 | textbox | Drawing Reference Number:
fcf7f629-0929-5086-a2e7-945f2d4baea8 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
dd8ffcfd-6d69-5859-aca7-64418a139e5c | date | DATE:
| checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
5adac045-75d3-5573-b583-e79349118b01 | button | C5.2.5 Control Loops | Pass
f9454dbc-b469-5eba-bcc6-f07008214c10 | button | C5.4.0 Wiring | Pass
b83207ce-a0c5-5831-a138-eb924e2d4930 | textbox | Drawing Reference Number:
20029ec1-1d5c-5d55-a337-de1ceb425712 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
88f1340d-48fd-5317-bad9-3d4b2cbb3496 | date | DATE:
| checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
c4f3bd05-cefd-54ad-a37f-c8fd81720636 | button | C5.2.5 Control Loops | Pass
0178d34f-c14b-52fc-82a9-c520e90b784c | button | C5.4.0 Wiring | Pass
6713ac0f-7048-5246-aa47-ef42b8454a06 | textbox | Drawing Reference Number:
d8a91574-4852-5b72-8587-5c7c0b0eeeff | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6dbc0e52-f24e-55f7-9c66-ea7bb5e6f1bc | date | DATE:
| checkpoint | 4 - DETECTOR BASES FITTED OFF - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
127a5f6f-6b4d-5205-84e7-c622a3591b6a | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
174a463f-da0c-5194-9a2f-33b19ddb6698 | date | DATE:
| checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED - Detector type to appropriate location. Installed to Latest RCP
9ed3cc82-a0dd-5fc3-a957-87875b3e106b | button | C5.6.0 Sensors/Detectors | Pass
74236c09-5ffe-5f41-8aed-5b6d463f6c42 | textbox | Drawing Reference Number:
5a9673a6-6f25-5c03-aa2d-9ac833ed2c6c | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4bd3f712-fd45-5095-a143-ff434cd89152 | date | DATE:
| checkpoint | 6 - MANUAL CALL POINTS INSTALLED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
745f3032-2d3d-536e-83db-1e254d098bdb | button | C5.10.0 Manual Call Points | Pass
5bfd54fa-2132-54fd-a323-c063d50bed8c | textbox | Drawing Reference Number:
7c2ff6f7-aef4-52c0-b870-e7a90df491a8 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
3cff8ca2-6772-56bd-95bc-f3bb1f00e6e9 | date | DATE:
| checkpoint | 7 - STROBES FITTED OFF - AS1670.1-2018: Check with Design Drawing and/or RCP
e9de5fb5-d1f3-539b-9558-3601ba6bb59e | button | C5.2.2 Set Points | Pass
85058926-f68a-5455-a54a-a9cc8f9fab15 | textbox | Drawing Reference Number:
1a5c0d2c-7008-5e95-994b-843d535c5da4 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
59d17b6f-f466-5b44-a856-dbc637ca6bc9 | date | DATE:
| checkpoint | 8 - SPEAKERS INSTALLED - AS1670: Check with Design Drawing and/or RCP
8009a2a0-db4b-5c0f-b9f7-4762744d0bcd | textbox | Drawing Reference Number:
7745894c-4f18-5026-b509-f033b97b01ad | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
da58c8bc-c191-5b61-a7a7-14ce9edcf59b | date | DATE:
| checkpoint | 9 - WARDEN INTERCOM PHONES - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
a854c181-fa1b-5431-86c1-db84de61946e | button | C6.2.8 Warden Intercom Phones | Pass
847cf5c0-f805-5871-92e1-f952cd3fefc0 | textbox | Drawing Reference Number:
de219c64-65d7-58ec-860f-4a2c64484c2b | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
12a8b9fe-c0ed-59e8-b003-7350738efdcb | date | DATE:
| checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
06915f0f-08bd-5ada-9e08-c873acfb1627 | button | C5.2.2 Set Points | Pass
bda85d77-6d22-5ee7-b576-ae3ce7fe6edf | button | C5.8.0 Modules Input/Output | Pass
fcc5729e-1e22-5ded-b67c-72a3a94084f7 | textbox | Drawing Reference Number:
f5af4fcd-31df-5301-af49-a25088a5cf00 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
70a8005b-bdec-507a-8b47-e29dc4362f5c | date | DATE:
| checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
0b976d4c-fe03-5cc0-a34d-78b0b3f6404f | textbox | Drawing Reference Number:
92f924c0-f49f-5f6f-aefb-057178b458ce | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
0760a252-6747-5779-92d0-e6a7f298308d | date | DATE:
| checkpoint | 12 - LABELS AFFIXED - AS4072.1-2018: The label should be positioned close to the service penetration
4497778e-d457-5aee-bf43-93eead8a55ee | textbox | Drawing Reference Number:
8052de2d-76da-5067-bf53-38ccfef14b74 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
bd087965-e456-52fc-97d4-28c9cddf238b | date | DATE:
| checkpoint | 13 - ACOUSTIC PENETRATION SEALING - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
0e8cc4f3-04d8-5fb4-a222-87e448366268 | textbox | Drawing Reference Number:
9e33f671-cef2-5865-974f-136c8d764221 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
6ef432df-9136-5229-b403-4af9abe70906 | date | DATE:
| checkpoint | 14 - CABLE TRAY BRACKET SPACING - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
caa5c5bf-066a-5d70-9050-f6c23b80a529 | textbox | Drawing Reference Number:
96f36020-a662-5fe4-a99f-b92363ddf3c8 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
4b8dba09-0c24-5044-8feb-78ee73853bc1 | date | DATE:
| checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL - In House QA. Up to Date drawing register. Drawings updated with MPX approved references.
7f12997e-a7e2-5e43-b1da-95ba8e04f5fa | textbox | Drawing Reference Number:
c02c598c-6f46-55f8-9757-6d7adb673649 | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
c79cf8bc-eb56-5beb-9b38-27ed28937455 | date | DATE:
| checkpoint | Hold Point Details
22a0ad41-7aca-55f1-a539-5b4831627f4b | button | Hold Point Required: | Yes,No,Other:
80908cb6-f41f-5c10-b34b-d89d92306708 | textbox | Other (if applicable):
6d277abb-edfb-5678-a72a-72577724d5ae | textbox | GM Sign Off - Name:
d224bd8a-ba9f-59c9-84f2-6fcd388304e2 | textbox | PC Sign Off - Name:
4ef62066-c7ac-54e7-9fd4-57379e2dfbbb | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-017 In Slab Sprinkler Sleeves | itp | ITPS-017 In Slab Sprinkler Sleeves |  | 576acc7f-9671-496c-a59d-fc8810a162dc
| section | Details
| checkpoint | 1 - CHECK SLEEVES ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA
d9fd6ac1-901b-5e3a-9461-b48ab32239db | date | DATE:
| checkpoint | 2 - CHECK SLEEVES T ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA
c394bf9d-c0e4-503a-966f-afd722973f25 | date | DATE:
| checkpoint | 3 - INSTALLATION, SLEEVES ARE JOINED CORRECTLY & TIED IN TO DECK (NOT RESTING ON FORM WORK).
f67cc1bd-d765-5eaf-a396-e86d05973e6f | date | DATE:
| checkpoint | Hold Point Details
603e02f9-4af2-52e7-86ef-11776e40a8a7 | button | Hold Point Required: | Yes,No,Other:
8b681646-425a-5b4e-a43f-930e505c91d6 | textbox | Other (if applicable):
9677084e-cba6-5c39-b970-d53416b567e9 | textbox | GM Sign Off - Name:
95053d1f-483c-5b31-8197-c3393162293a | textbox | PC Sign Off - Name:
b04c229b-aa21-5aa8-a3c7-30a4c9be800a | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-017 In Slab Sprinkler Sleeves |  | ITPS-017 In Slab Sprinkler Sleeves |  | 969e9d48-64ab-407b-8ea9-537850f7eb86
| section | Details
| checkpoint | 1 - CHECK SLEEVES ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA
e29c1117-e59c-5e85-8b82-c198d45fe90e | date | DATE:
| checkpoint | 2 - CHECK SLEEVES T ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA
a77e0b06-a534-59f9-96a1-d525499dbac3 | date | DATE:
| checkpoint | 3 - INSTALLATION, SLEEVES ARE JOINED CORRECTLY & TIED IN TO DECK (NOT RESTING ON FORM WORK).
43bb8a12-2055-57c6-aac2-1cc13f33ff46 | date | DATE:
| checkpoint | Hold Point Details
edd09c4c-bd77-578d-bf58-f7bb9ba482b8 | button | Hold Point Required: | Yes,No,Other:
6fbd4704-3d33-51df-a323-603a651a62a1 | textbox | Other (if applicable):
461be7d7-8c82-5e7a-b1d0-641e9f2b3bc8 | textbox | GM Sign Off - Name:
e22fa881-6497-5c25-a632-29c6e3e68764 | textbox | PC Sign Off - Name:
3dcfdb60-17a5-5034-8ac7-6bb1ab2f9062 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-018 Temporary Fire Strategy | itp | ITPS-018 Temporary Fire Strategy |  | 193644fb-15ea-4116-912e-f59627c83916
| section | Details
| checkpoint | 1 - INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
81bfcbda-6267-54d2-b49d-704e56fc801f | date | DATE:
| checkpoint | 2 - INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
9d2d857a-cae2-59d4-a24e-cbcbda07ebeb | date | DATE:
| checkpoint | 3 - CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
1143ec01-0ef7-5058-88dc-a9486b47669f | date | DATE:
| checkpoint | 4 - INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
23dd76d4-75d6-57e1-931e-85215da62f3b | date | DATE:
| checkpoint | 5 - INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
6dfb085c-b58e-5ca4-9887-afb04340bcb5 | date | DATE:
| checkpoint | 5 - CONDUCT WATER PRESSURE TEST OF HYDRANTS
c3431637-9ea6-5c0b-a3b2-95a4c695b4a3 | date | DATE:
| checkpoint | Hold Point Details
91ef6cfa-42a8-5244-94fc-10f32b25ee5f | button | Hold Point Required: | Yes,No,Other:
29bd253d-02e0-50bd-b135-16bb9d86d6eb | textbox | Other (if applicable):
142a1229-a1a2-5c0f-8a77-1c70b3ce7910 | textbox | GM Sign Off - Name:
2ba833ae-7fce-5c39-9e35-4b94a7238c99 | textbox | PC Sign Off - Name:
0a0e97a5-d3c8-5b88-b80c-0f5f5a707f28 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-018 Temporary Fire Strategy |  | ITPS-018 Temporary Fire Strategy |  | a37854fa-5d41-453b-9262-10f0b87c031b
| section | Details
| checkpoint | 1 - INSTALL AND CHECK PORTABLE FIRE EXTINGUISHERS INSTALLED AT FIRE EXITS
f3a2f893-8fab-5278-b4fe-3d9c7bc1f253 | date | DATE:
| checkpoint | 2 - INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
4202cd89-8ed7-5745-9d97-abf7c89fa3dc | date | DATE:
| checkpoint | 3 - CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
c8d23f6d-59f7-5b92-bbf0-6a40f6b6b313 | date | DATE:
| checkpoint | 4 - INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
1f8a8926-0d82-5cb6-9552-d9c2f6a3234c | date | DATE:
| checkpoint | 5 - INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
ee7d90d0-8260-515e-95d9-1e749ede1b81 | date | DATE:
| checkpoint | 5 - CONDUCT WATER PRESSURE TEST OF HYDRANTS
f2f81676-8064-5b05-8835-62547a347783 | date | DATE:
| checkpoint | Hold Point Details
d0255c1d-e955-58bf-b601-ef097d6ed665 | button | Hold Point Required: | Yes,No,Other:
adfacd7b-7963-5902-b67c-37ccd3606846 | textbox | Other (if applicable):
32a4eb17-6dc2-5af3-a828-120f9544ea81 | textbox | GM Sign Off - Name:
46b229f3-3934-5940-a50c-2fb10f2f33ee | textbox | PC Sign Off - Name:
5fba35f6-63cd-5fdd-a552-131f6b0d0e59 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | ITPS-019 Site Temp Asset Lists Extinguishers | itp | ITPS-019 Site Temp Asset Lists Extinguishers |  | 82f858aa-5531-4eb0-bffa-770746f3a5c5
| section | Details
| checkpoint | 1 - ASSETS 1 TO 10 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
25d92acf-212f-5c6f-a13a-c329962e1cd6 | date | DATE:
| checkpoint | 2 - ASSETS 11 TO 20 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
8b788147-3215-5c0f-ad9f-ba7f37cd3114 | date | DATE:
| checkpoint | 3 - ASSETS 21 TO 30 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
5a6f7887-412b-5fec-94df-7b41749d8195 | date | DATE:
| checkpoint | 4 - ASSETS 31 TO 40 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
affa1b79-3ad8-5b19-a210-fcd9b8cf3421 | date | DATE:
| checkpoint | 5 - ASSETS 41 TO 50 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
21fd1ffb-5322-5c12-9ba2-c2d65fb1c472 | date | DATE:
| checkpoint | 6 - ASSETS 51 TO 60 - TAKE PHOTOS AND NUMBER IN COMMENT BOX
e4d2eec0-4fce-5ec3-a3d9-a6a0db936bf4 | date | DATE:
f23a756b-6b84-559e-aa82-3561d3ad3eb9 | textbox | GM Sign Off - Name:
daeb5533-5d94-5dd2-bbdc-73a4d2bf5136 | textbox | PC Sign Off - Name:
eebcf352-97ad-50b7-ab9a-3eb411610a16 | textbox | CS Sign Off - Name:
| signoff | Signatures
| checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist |  | eccb5f1a-42f7-439b-b784-23328f04a690
| section | Incident Reporting
| checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
| section | Workers compensation first, progress and final medical certificates and Return to Work Plans
| checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
| section | Reporting
| checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
| checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
| checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
| checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
| checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
| checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
| checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
| checkpoint | I have submitted copies of daily pre-start inspection records for the month
| checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
| checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
| checkpoint | I have attached a copy of the Fall Prevention Register
| checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
| checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
| checkpoint | A copy of the Ladder register has been submitted this month
| checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
| checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
| signoff | Signatures
| checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure |  | f852ef4c-fb7f-4d6c-97cd-5be73b183eb2
| checkpoint | Task Details
35e1d1ba-0df8-5940-a259-bccb2e916c8f | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
fb9e0a76-393d-592a-91df-e815f04daa63 | textbox | Work Area:
88a56175-6e66-5759-acca-aff345430919 | textbox | Task:
da1bc784-0a9f-5d8c-920c-1ef0c5a72b5d | textbox | Safety Risk: e.g. electricity, moving parts, noise
| checkpoint | Personal Protective Equipment (PPE)
6455ae14-9591-5d78-a126-6b32f61c8232 | note | The following PPE must be worn, and precautions taken, when doing this task:
9f713af5-73c1-59dc-b084-7a3c2cf3b600 | tickbox | Work Gloves
6ec63488-d4c6-5096-8d62-8158b75870b4 | tickbox | Safety Glasses
64c63526-5a83-5c7d-a3fa-bbb76c5b5c62 | tickbox | Steel Cap Boots
83f78842-c3cd-59b1-9ff7-a8a0017d78dc | tickbox | Ear Protection
72bcb4cb-bf42-5039-b494-9375956a3b79 | tickbox | High Visibility Vest
30b3c185-f375-5785-99bd-75f1c6181665 | tickbox | Head Protection
943a7197-78bf-5b79-99b5-476d057fb450 | tickbox | Respiratory Mask
dee2c30b-edc0-5cd4-aaeb-4bf5a219de4e | tickbox | Face Mask
16c50b5b-5bd7-5e8b-bdcd-08c57fc113d6 | tickbox | Protective Clothing
7a9b8916-016c-5db4-a6f5-12378ee517c0 | tickbox | Wash your Hands
| checkpoint | Supervisor Signoff
| signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
| checklist | REPORT-002 Hazard |  | REPORT-002 Hazard |  | b211097e-9139-4776-a1fb-2d7c9033d66f
| section | Details
| checkpoint | Hazard Report
43f0228c-2fe3-5c6e-85e3-84048cef3fea | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
82bf4eeb-5f0e-5f93-8ead-f55641b15686 | note | The principal contractor will be informed immediately and provided with a copy of this report.
| checkpoint | Hazard
c157c7de-d92d-505c-adbd-f9a7620ee7c6 | textbox | What is the hazard?
| checkpoint | Contributing factor
9664582b-bef9-5594-8875-1f56cd1aab82 | note | What are the contributing factors?
655bdfbb-ee2b-5728-aae5-5d3b6624ae50 | tickbox | Environment such as noise, slip or trip
9eb4f112-dc84-55ca-95ee-606b2ae625f4 | tickbox | Equipment/ materials i.e. wrong or inadequate
bdecd7f1-1e7e-59b7-8cff-fa37b4488ea3 | tickbox | Work Systems i.e. inadequate training
f9ec5884-395b-5fc3-8193-6f73553c064e | tickbox | People i.e. production pressures, lack of communication, lack of procedures
90dff80b-44cc-5e29-b4ee-fe7e1df7551e | tickbox | Other
d7af76c9-77a3-5b3d-85f2-229e182aed20 | textbox | If 'Other' please specify:
| checkpoint | Corrective Action
43a01400-3788-576b-a07c-ee5c2b0958e7 | textbox | What are we going to do to fix the problem?
dc1a0db9-5b08-56a1-8f09-eb0c829dcf7b | textbox | Who
7cb0663d-55b6-50d9-816f-cf668d5aa4df | textbox | When
| checkpoint | Completed By
| signoff | Signature
| checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review |  | 605340ad-68f9-47c1-a04a-692ba31e9ef4
| section | Details
| checkpoint | Details
fcbbdfbf-a580-58e2-aca3-6db3938b62ef | date | Date:
3d0346a2-15c4-5dd1-83d7-39fc0feb5a90 | textbox | Time:
| checkpoint | Existing Register
96c307f7-229a-58ec-8971-6703204bb9aa | date | Last Revised on (date):
e98ad3cc-027f-5273-ad68-b11ab5b72cea | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
| checkpoint | Chemicals on Site
c1791c45-bbc2-5226-98ec-daa09d584a45 | textbox | Location where Chemicals are being stored:
64ef467f-1d6e-5a89-a833-62bedc96024f | note | Upload a photo of each Chemical on site
| checkpoint | SDS
0dbf4695-dd94-54f8-b2bb-e4da68cc1f63 | button | Have any of the SDS sheets expired? | Yes, No
edcab06a-642e-5627-89fb-26a64e7739af | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
c1c991c6-f8b7-58b3-bc66-63d765265e0f | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
| checkpoint | Declaration
c387a439-caf3-57d6-9d2f-ee67f6d50db0 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
4f739c58-52c1-51f6-b261-1f8b7f974967 | button | All Chemicals are stored securely | Yes, No
6d438445-ff59-5c63-922f-bb4443e6bf75 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
| signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
| checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation |  | 14f03151-c05b-400d-9088-2325403cfe50
| section | Details
| checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
| checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
| checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
| checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
| section | What factors contributed to the incident?
| checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
| checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
| checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
| checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
| section | Corrective actions:
| checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
| checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
| signoff | Signature
| checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action |  | 053b8733-f121-4f43-8fb1-b584f52484f5
| checkpoint | Details
297d7da6-d94b-5611-bd0c-702c41cc33b1 | date | Date:
eedfd367-e843-5c3e-9193-ab41c84ef7aa | textbox | Time:
7a3ad93f-82ff-58bd-8541-95c08d4b5a25 | textbox | Location:
1207ac55-2622-5c8f-951b-2639b0dc564e | textbox | Supervisor Name:
| checkpoint | Corrective Action Report
8935e3f9-ddeb-55d4-a028-6925bb83b863 | textbox | Principal Investigator
d0e213ca-26d1-5132-b6f3-d05c03ab33d5 | note | Non-Conformance is:
1ae631a5-072b-53cf-91df-6dd2aea39da5 | tickbox | Minor
de4f5de6-b1c9-550b-8bd5-3a7b53fda615 | tickbox | Major
bd4c3acf-a07e-5421-93fa-20e23a4a5b31 | tickbox | Critical
ddfa40b8-8d09-56f1-a1da-f91e07948d85 | textbox | Details of Non-Conformity Identified
db9b8c8d-7035-5210-8db8-53f6d5fc9674 | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
8687753c-2eb2-584f-b974-2298103b5684 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a0ddfdb1-ac2a-55ba-805f-904b06bf787a | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
5ab5854b-b2a6-57e3-bf06-6738c14f36b6 | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a1447274-b77a-579d-813e-8403ec194660 | note | Add photo evidence if applicable.
| checkpoint | Corrective Action Plan
a567af7e-c8e7-580f-a2d1-bb2fbe30ed4a | textbox | Describe corrective action
b7d89de9-a208-53f8-875e-fef30341ce39 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
167dc1ac-6bf6-5cec-95fb-38014a1058a3 | date | What is the proposed completion date?
| checkpoint | Signoff
| signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE