## Checklist Templates
Id | Type | Name | Values | Prompting Name
ae26eec3-abdf-4f27-a973-9f3a58f4d88a | checklist | Documents |  | Documents
fbdfba17-fa2e-4037-a5dc-f3ef076d92c6 | checkpoint-no-value | Documents
c60454a2-cc3c-5870-bc6b-5a4754e84d42 | note | Drawing Rev No.
73e098f7-717e-4513-b9f7-1b6959a5a1a7 | checklist | ITP No. 08 STRUCTURED CABLING FIT OFF |  | ITP No. 08 STRUCTURED CABLING FIT OFF
8050135c-2af2-46e4-add7-b64b31020b20 | checkpoint-no-value | Documents
334b2dca-9f49-57c4-a859-c3ca7101e5a0 | note | Drawing Rev No.
076ace86-0d0a-4b2c-b7de-fb92e2dc0c02 | checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
b516bfc4-82ac-4519-82a0-cc4dab9b295c | checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
0acd29e8-c45d-4f69-856f-6f205ae422b3 | checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
f927cb48-5b41-48d3-9d5c-3716cbf68f8e | checkpoint | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
e830f5bf-4648-4b73-8f78-b1cd9d834ee7 | checkpoint | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING
3cb96a2c-d23f-4044-8673-eedeb8ec64a0 | checkpoint | INSTALL JACK INTO WORKSTATION OR WALL OUTLET.
67d299db-e4d3-4c6a-b11b-6098980b3396 | checkpoint | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL. TIE INTO POSITION USING VELCRO STRIP AND/OR CABLE TIES SUPPLIED.
a776c17b-dd80-46c0-b858-991b524062a1 | checkpoint | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE AND CHECK FOR CORRECT OPERATION.
ebee7dc0-4950-433b-b687-535ce8aee61d | checkpoint | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
7d834bcd-71fa-469a-bf7e-a1da650ebfd3 | checkpoint | COMPLETE CERTIFICATION AS REQUIRED
1a6f0b2a-43fa-4e90-8e57-f3913efc12a9 | checklist | ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM |  | ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
776505d5-2d82-4036-8ebf-6243fe570423 | checkpoint-no-value | Documents
5a114758-fc05-5a4e-a83f-8fce1d0156af | note | Drawing Rev No.
66617bbc-4367-4adb-bf9c-e4977c5b9ba6 | checkpoint | REFER TO INSTALLED DRAWINGS
5453885b-45fd-4943-ba52-01090b074459 | checkpoint | test terminations using COPPER STRUCTURED CABLING tester AND LOG RESULTS
c2a94f04-6cd4-4fd0-87bf-5b4f3ccc0ca7 | checkpoint | RECTIFY ANY FAILED RESULTS, RE-TEST AND LOG
2875780a-dfee-48b9-9576-7fe2962dfce6 | checkpoint | LABEL FRAMES AND PATCH PANELS
597aeb43-fb05-4435-a5f6-bbb0e329650d | checkpoint | COMPLETE PATCH PANEL SCHEDULE
0b109235-368f-4880-b69d-f198aa7799d4 | checkpoint | DOWNLOAD RESULTS FROM TESTER TO PROJECT FOLDER
8606439b-3f4d-41fa-8510-c1546687bf9a | checklist | ITP No. 13 SUB-CIRCUIT CABLING FIT OFF |  | ITP No. 13 SUB-CIRCUIT CABLING FIT OFF
82d7daf7-78bb-436b-bc77-00c6b11984fd | checkpoint-no-value | Documents
c71f0fa2-ee87-546d-946a-4fb8b61a05ea | note | Drawing Rev No.
64a94420-5a9e-49ac-8c05-e9d3a9c63743 | checkpoint | COMPLETE WALL OR CEILING CUT OUT WHERE REQUIRED
00195ae8-43ad-4f17-99c1-5056397491f5 | checkpoint | TEST & ENSURE SUB CIRCUIT CABLING IS NOT LIVE PRIOR TO FIT OFF
dd364acf-8453-4c8c-b3d0-4e193a0f3624 | checkpoint | TERMINATE CABLE TO OUTLET OR PLUG BASE, CHECK CORRECT CONNECTIONS AND FIX TO SURFACE, IF CIRCUIT CAN NOT BE FULLY TERMINATED A JUNCTION BOX MUST BE INSTALLED WHERE REQUIRED
24e41d1a-1891-4950-9090-e5c2df2338ab | checkpoint | CLEAN AREA AS REQUIRED
f268a731-d7e5-412e-b3de-d8be29c947e9 | checkpoint | RECORD ANY RELEVANT INFORMATION ON DRAWINGS.
fc256288-e22f-4a0a-82da-d9625e5b7b8d | checklist | ITP No. 14 Construction Wiring, Installation, Test and Tag & Removal |  | ITP No. 14 Construction Wiring, Installation, Test and Tag & Removal
d88c0f12-1f05-4ff8-8357-98d895d02862 | checkpoint-no-value | Documents
edbf5e8d-61fd-5648-b7de-3cb1e795c922 | note | Drawing Rev No.
870b11e0-a06b-46bd-882e-17d040f91423 | checkpoint | Area accessible & ready
ca0a9d7c-7fff-4297-8925-c92e72550713 | checkpoint | Refer to temporary wiring setout plan
f8d86cd4-b904-5a8c-a96e-91fad8bf210e | note | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
2920289e-55ef-4cb1-acef-8d19e41eac2b | checkpoint | Fit off plug base and or powerpoint/isolator
c2529e2d-8d1f-4817-acd6-b8b44261f3ee | checkpoint | Install light fitting, exit/emg, power
e570b52b-ce25-4698-b516-2c6bddc762ce | checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
8bda44f0-83d2-4630-b2d0-2375b8ed5a3f | checkpoint | Test & commission
eca9d699-4f41-529b-a7b9-da8da803ea5b | note | Lodge non prescribed certificate of electrical safety
108afaa0-5303-4df7-9bcf-cd9b4ef245e1 | checklist | ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING |  | ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING
7498b545-df18-45b4-956c-e51f386e9720 | checkpoint-no-value | Documents
6bb4bf31-5c2d-5c3f-8adc-e77a1d1a9e25 | note | Drawing Rev No.
cbd1aed8-2ca7-477a-b33e-f9ed5ecf3f3f | checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
f56403cf-baef-4df4-951a-762f78aac1d4 | checkpoint | COORDINATE LOCATIONS WITH OTHER SERVICES
e4c43433-06d3-4f1d-b752-0b543ce14373 | checkpoint | MARKING OUT (IF REQUIRED) REFER TO DRAWINGS FOR LOCATIONS
909cbb1e-b11b-4af1-abdc-90797f2f3ad8 | checkpoint | PLUG IN OR FIT OFF LIGHT, FIT OFF DATA CABLE IF REQUIRED
0aa37569-2175-4573-8d6b-1069911ff382 | checkpoint | INSTALL LAMP & DIFFUSER AND CLEAN FITTING
18d4bce1-6664-4c3f-acf3-4b25152c4b57 | checkpoint | INSTALL EMERGENCY BARCODE TO FITTING AND TO DRAWINGS (IF REQUIRED) OR,
a6c4f7a1-bf05-4378-8e42-f79c17531db1 | checkpoint | NUMBER FITTINGS AS PER VAST SHOP DRAWINGS.
50a802d9-c47c-414e-9a04-035dc4a9653b | checkpoint | UPDATE ANY CHANGES FOR AS BUILTS
5c808c6a-1863-4cf1-9afb-4f92c49c60bb | checkpoint | COMPLETE LOG BOOK
41f4f21b-14cd-469c-8ff5-495a023a7f69 | checkpoint | COMPLETE INITIAL 2 HOUR TEST
b7318805-4199-4e3d-a20f-72f8648d0baa | checkpoint | RECORD RESULTS
a6834514-7191-4514-8630-c36864053dbd | checklist | ITP No. 19 Installation of Temporary Power Board |  | ITP No. 19 Installation of Temporary Power Board
c967f64e-e545-47c0-a1d8-2f93d8310df4 | checkpoint-no-value | Documents
4231143b-10ec-5d07-9d31-b51ea77dbabf | note | Drawing Rev No.
f66de0f4-be6e-4bec-b1b2-447957045b7a | checkpoint | Area accessible & ready
80ed5acc-9deb-4534-b363-c2764ece1324 | checkpoint | Locate & fix into position, bolt temporary board down with at least 2 fixings
d60a772d-1691-4449-b4ac-8e1edd2d5ce9 | checkpoint | Install submains cabling as appropriate eg: glands/tray/duct
f38eb3f4-e741-461e-8227-c0b66d5bc4f6 | checkpoint | Install lugs and terminate
d495421c-7a65-4960-9a0b-af0d895b8862 | checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
ad8f36b8-b2ad-4332-9b85-97ac8bef62e5 | checkpoint | Clearly identify services
32d54545-9dce-4db9-b1e6-8766c1d003f5 | checkpoint | When ready to energise proceed in accordance with energisation procedure
73cbfa70-933d-40ad-aa5e-db2804ca850a | checkpoint | Energise & record results on Vast RCD test sheet
6091ae2c-6f4c-4ee0-8858-7e81170d7de9 | checkpoint | Install A3 laminated sign on face of temp board with floor plan and where the board is fed from
4eb5bc03-4533-4a87-96af-fa43fdcac83c | checkpoint | Update Temporary Power Board register & save to project folder/design control/temp const.
911700b2-5a57-5942-91a6-34faeb51daf0 | note | Lodge non prescribed certificate of electrical safety
26ead13d-587e-58a1-ad72-de4d3b8c47b0 | note | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
633692c3-4d19-4a49-b3ac-a2526a6ff6bc | checklist | ITP No. 20 Decommission Temporary Power Board |  | ITP No. 20 Decommission Temporary Power Board
fc10fd8f-94b6-402c-9f33-2f9aa39eac9f | checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
f101ab87-b5d9-546c-bef4-caca3ee227cb | note | De-commission form issued to builder, 48 hours notice to be given
3a5b69b9-333e-4e25-b576-1780c02d8d8c | checkpoint | Sign off builders checklist
666e4c35-c52e-4fcc-9fb2-a3ad428cf712 | checkpoint | Safety Committee Inspection
3375ddd9-7082-4460-b349-9ac432c2aac2 | checkpoint | Final approval to be given by builder
e65fd2ee-c9b3-407c-8868-5335f1f34d9b | checkpoint | Perform voltage test to ensure power supply has been isolated
98b873f4-685f-4a67-a121-a65545e65d5d | checkpoint | Disconnect supply cables
46d47802-80df-475d-b957-96b09e2a9de1 | checkpoint | Fire sealing of penetrations
b0e747e0-3d93-42e7-9853-2b39eb517a85 | checkpoint | Remove temporary board
8287e871-aa9b-4cc7-981a-d02f1dbac065 | checkpoint | Update temporary power board register
80393826-f258-4243-bfba-a642e382c514 | checklist | ITP No. 29 Installion of Electrical & Communication Pits |  | ITP No. 29 Installion of Electrical & Communication Pits
4ebdbf0d-bf14-472f-b8b8-b5bdf38d528d | checkpoint | Inspect pits for any damage on arrival to site
76cb708f-60f3-4c65-aa0e-82f5f965e6a0 | checkpoint | Mark out pit locations and alignment/arrangement
0c22b260-e95b-432a-bd11-56a42f02eeab | checkpoint | Check finished heights of pits against civil drawings/finished floor height
1bd18972-dc66-4ffe-afb8-7b7067278a2c | checkpoint | Erect pedestrian barricading
f0e7e83d-1a95-432a-a520-88b7b676b2fa | checkpoint | Excavate ground around pits as required
49f24189-44e1-4e94-bace-8edd7abf5f11 | checkpoint | Place bedding material as per pit installation requirements
15a48d9f-d1fd-4bc9-87ba-edd6c8d1a1b5 | checkpoint | Cut out pit entry as required
c89bf200-a7c9-4f0a-a352-a849cbe04c42 | checkpoint | Install pits in ground (using correct lifting equipment)
08a34e57-d300-49a5-b2f1-94ca62e6e33c | checkpoint | Check finished heights of pits against civil drawings
45d81b80-46d4-4e31-9490-1bfbd7207b7a | checkpoint | Install relevant conduits
2707e357-5ab1-4bc1-ac0c-44d17f357b9c | checkpoint | Backfill and reinstatement of ground
8755477f-45d2-4302-94ca-116f68e88127 | checkpoint | Check stabilised FCR backfill 200mm below proposed road level, compacted FCR above that
20405550-f8e4-4b51-9d08-b944d6254ccc | checklist | ITP No. 43 Lighting Control Rough In |  | ITP No. 43 Lighting Control Rough In
04f7feb2-7f40-4659-b4ab-450f08ac2f4d | checkpoint-no-value | Document
a9f2f839-0ffe-52de-80fc-c84b62db3f61 | note | Drawing Rev No.
a8a04379-0f54-440d-8c06-ae5b1a316e77 | checkpoint | Area clear, tidy and accessible
eb5d89d3-d3cb-46f7-802b-c4ee151d5315 | checkpoint | Plan lighting control route in conjunction with supervisor.
5d2961f8-2de0-44e5-a23d-a1b77b503519 | checkpoint | Rough in lighting control cable to all sensors and switches.
17294971-c3c0-4ab3-8dc3-9c9111c37a85 | checkpoint | All lighting control must be roughed in point to point, daisy chain style (no star points, two cables at each point only).
f8e37107-a1ef-4ee7-80db-74d9294d2812 | checkpoint | Lighting control route must be drawn clearly and precisely on dedicated plan, if there is a change or revision, a new plan must be created and superseded written on old plan.
ab209d21-662b-46d1-9e5d-09e42b04afbe | checkpoint | Upload lighting control plan to Conqa, use this spot as a place to upload any and all plan/revision of this drawing.
b9d28028-adfa-4728-adad-9cb0c2f30c33 | checkpoint | Rough in of all booster cables applicable to the lighting control system (1.5mm2 twin active)
d23c99a1-c912-4875-b493-7544626a3351 | checkpoint | Ensure all cables are clearly labled and are to the appropriate length.
1c036563-0175-432d-93f1-a5cedb99ad64 | checkpoint | Ensure area is left clean
11293f6a-e62e-4eae-bb6a-a8c4dc7d7df6 | checklist | ITP No.07 Structured Cabling Rough In |  | ITP No.07 Structured Cabling Rough In
fcba2ccf-6b31-41b3-8932-fea4b5e0dbe6 | checkpoint-no-value | Documents
5593f9bc-b03d-5d7f-bd5c-5e6ce25abeae | note | Drawing Rev No.
91d09f15-6eee-5309-bb14-d8e4ea2418bf | note | REFER APPROVED DRAWINGS AND SPECIFICATION.
60ec7658-5398-464f-8b2f-f8982eed68ed | checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
8cea6c54-4655-402e-8de6-6b096b284004 | checkpoint | VERIFY CORRECT CABLE TYPE.
9aa4bbe6-ca88-4e97-8f25-f289bbde595f | checkpoint | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD
672f2b31-c8e3-42b8-80e2-71fe300372e0 | checkpoint | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS, ENSURE VELCRO CABLE TIES ARE USED AS PER SPECIFICATION
4b507adb-d326-4fbd-be2a-c11960c7b75f | checkpoint | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
50c8696e-6257-42aa-aff6-614fd62b7a0e | checklist | ITR 33. Installing Underground Services (Electrical) |  | ITR 33. Installing Underground Services (Electrical)
5846bf6b-5783-4494-ac65-6f1e2f1a3a3f | checkpoint | Inspect conduit material to check that it meets material specifications
829ceadf-1756-4d69-84f6-f4c5b36ab034 | checkpoint | Check conduit alignment as per plans
7b37bc34-7605-4f6f-99b8-7bfcb2c9d969 | checkpoint | Set out marked, and all services located
73b0cfb0-3d44-4a09-b924-cde9cf0530e0 | checkpoint | Erect pedetrian barricading as per plan
6ee88055-ce69-4c20-a034-8c282003ee58 | checkpoint | Check excavation depth against proposed road level
e82b710c-04f7-4947-8300-95f92a28deca | checkpoint | Excavate to the trench as per plan
6222d60e-246d-436f-afb4-7506b64c42c9 | checkpoint | Place specified bedding material in trench
8134abf1-0f9e-431d-93c1-bc7d2c2c00cb | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
f3539665-cb57-4187-b33b-2c357c0059dd | checkpoint | Backfill over conduit to 500mm
89261778-fdb4-43e4-9adc-91d3a1b2d7db | checkpoint | Install cover slabs over conduit
20bfa4a9-95ff-4597-96a4-f8cf2096ddad | checklist | ITR 33C. Installing Underground Services (Comms) |  | ITR 33C. Installing Underground Services (Comms)
33dba755-817a-4a9d-a4d3-c3b793f4b6cf | checkpoint | Inspect conduit material to check that it meets material specifications
5acc3b20-4e81-4e38-81a3-617ffd001354 | checkpoint | Check conduit alignment as per plans
7b41b4ac-ef36-4fae-8bd4-acb92c9e156d | checkpoint | Set out marked, and all services located
1380eadf-c1bf-4a77-8f8b-b7a936119a32 | checkpoint | Erect pedetrian barricading as per plan
989f7bec-1fda-4573-9cdf-f90246e2bb0a | checkpoint | Check excavation depth against proposed road level
28967b46-b9e3-41bd-8d5d-8b5d9d647ad5 | checkpoint | Excavate to the trench as per plan
596d8f7b-8f16-4c25-9f8c-79cb0529d692 | checkpoint | Place specified bedding material in trench
23dfc98b-986b-4476-a875-e5b71cb0d57c | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
0b8afabf-ed56-4fef-856c-3e2b4a9561cd | checkpoint | Backfill over conduit to 300mm
a4947f0c-0cca-49a4-9ae2-926a44fa5bf5 | checkpoint | Install cover slabs over conduit
6f6d0221-3e9b-4daf-aa14-0ade35e01a11 | checklist | ITR No. 10 Cable Tray Installation |  | ITR No. 10 Cable Tray Installation
772d035c-1e8a-48a4-bf15-af698ce6039c | checkpoint-no-value | Documents
5cb4aaee-6a77-5ed6-a8e7-bf4e09b83769 | note | Drawing Rev No.
ae994407-ef5a-4898-84ad-57a24e17fed2 | checkpoint | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES)
24fff756-7bbe-4b3c-91dc-25ac2a8699b5 | checkpoint | CONFIRM SIZE OF CABLE TRAY
cea9ca56-a699-454d-930f-a82602ca8eaa | checkpoint | INSTALL FIXINGS AND SUPPORTS AS NEEDED
57bdcad0-46eb-4fa2-a157-ac9263a3a411 | checkpoint | INSTALL CABLE TRAY
2f60e7dd-d27e-4423-83ef-21953e595624 | checkpoint | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS
756ac2d6-1ca4-4152-bec9-3bddfe5df5f6 | checklist | ITR No. 16 Switchboard Installation and Terminate Submains |  | ITR No. 16 Switchboard Installation and Terminate Submains
4e915949-e0c9-43cb-9065-2c5ffb023d84 | checkpoint | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS AND DOORS AGAINST APPROVED SHOP DRAWING
ff9c9d5b-a62f-43f3-ae5b-eae56d90ac74 | checkpoint | LOCATE & FIX INTO POSITION
ea238173-7f8f-4710-b2e7-126cc49f3d52 | checkpoint | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
764211c2-97ad-412e-b7c1-9688f0dad8ba | checkpoint | INSTALL LUGS AND TERMINATE
7fd11e3b-b907-4707-bcd2-5e8886e771a3 | checkpoint | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
293c68a6-2156-4438-b96f-bbc1f79bc91d | checkpoint | CLEAN & VACUUM
524c5b94-d514-4c73-b67f-8c19cb56e500 | checkpoint | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED).
264ce516-96ea-471c-8538-52d0cf93580b | checkpoint | CLEARLY IDENTIFY SERVICES
970d8a71-6b12-4789-9d6c-961a4adcfdf5 | checkpoint | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
771229cd-e3e2-47b3-bd01-e4e6442d7c53 | checkpoint | ENERGIZE & RECORD RESULTS
dc07df99-bd0c-453b-92ae-3dedad5aaefb | checkpoint | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE
e88829af-4fd1-4cc6-9693-99bd799118d5 | checkpoint | CLEAN SWITCHBOARD CUPBOARD
589901b2-8494-4430-a40f-2c1963439af1 | checkpoint | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE AND TERMINATE. if circuit not complete at the other end, it must not be terminated BUT PLACED IN A JUNCTION BOX AT FIELD END AND IN CONNECTORS AT dISTRIBUTION BOARD END.
708bc3df-bd34-4498-8e79-948a5b87c963 | checkpoint | CLEAN & VACUUM
5a080556-c3d1-43ce-9ede-0416e3a9d646 | checkpoint | RECORD RELEVANT INFORMATION AND ANY CHANGES ON DB SCHEDULE. AND RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM
d0745596-6fb1-4fe8-a4fb-e0f2ee5a1a8e | checklist | ITR No. 18 Light and Power Fit Off |  | ITR No. 18 Light and Power Fit Off
4998d51c-cfee-4067-8cdc-bcf96e3fff66 | checkpoint-no-value | Documents
a1cdd8fb-2b9f-5416-ad3a-830fc7acfdf9 | note | Bakelite & Power
a2923781-e8af-5de4-b7e0-b42fc715e39d | note | Drawing Rev No.
9ed1c812-1979-4573-8283-703ccc60ce90 | checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
63a84566-a37a-4c34-8a0a-8565384451ad | checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
7b0933e5-abc4-4e50-8094-cdc1bfe2c18c | checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
f6158fe0-a537-4727-b089-0b9accdaa68c | checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
117caea5-668c-40c4-887b-c87666b9a79a | checkpoint | FIT OFF FINAL APPLIANCES
0d7c172e-02c2-418c-8fd3-63acb6acba37 | checkpoint | COVER PLATES (IF REQUIRED)
f3fd305e-2b1b-53f0-9e2f-b1c3e07601cb | note | Light Fittings
c0d46821-9b0b-5f26-a3c0-c1b4b6e3e803 | note | Drawing Rev No.
8d57c7e1-8450-40dc-8e2b-e8ce801bc961 | checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
d007f1f8-81cd-48b3-a6f2-ea1ae2a9f7fc | checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
49f4dd1a-4444-40f8-9f16-e9304e73015d | checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
798b4033-2e9c-457c-8e71-ce3a77cb1d2d | checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
bca51ba9-b7e1-42c0-943c-1762cda42cc3 | checkpoint | INSTALL LIGHT FITTING
d63cdc28-af09-48dc-881c-6a9cf26a37cd | checkpoint | INSTALL LAMPS AND DIFFUSER
4f746570-8565-4230-94e7-768f81933f0d | checkpoint | CLEAN FITTING, LAMP DIFFUSER
9d27f1f7-7750-4b7b-945d-554394527e99 | checklist | ITR No. 34 Installing Light Pole Cages |  | ITR No. 34 Installing Light Pole Cages
97c20218-3d02-40b2-93e6-89235c92d111 | checkpoint | INSPECT CAGES FOR ANY DAMAGE PROIR TO INSTALLATION
b6f79d75-e8b4-4245-a2c8-5f6e410a00c7 | checkpoint | SET OUT LIGHT POLE LOCATION, ALIGNMENT AND HEIGHT AS SPECIFIED
27ae80ce-360c-43fd-bbad-991558a557b5 | checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
5cc7e6a2-dd15-454e-a95a-1b07b39ca60a | checkpoint | EXCAVATE AS PER PLAN
53c5584b-2ed4-4c1b-b6c0-8b34de5d7677 | checkpoint | PLACE SPECIFIED BEDDING MATERIAL AS PER REQUIREMENT
49410f80-9e6e-44ea-ba81-11dd3e76ce13 | checkpoint | INSTALL LIGHT POLE CAGES AND CONDUITS AS REQUIRED
1e50d0f2-41cf-4954-a142-71135f42d9e7 | checkpoint | RE-CHECK FINSHED HEIGHT AS PER CIVIL DRAWINGS
d5baba1e-f1c5-4486-91d8-f593992623e8 | checkpoint | POUR CONCRETE FOOTING WITH SPECIFIED MPA
49b98603-98aa-4d6f-9c01-58d6de8fde91 | checkpoint | CLEAN UP AND BARRICADE WORK AREA
8bfe423d-ddeb-4f2a-9266-012f7cd4efee | checklist | ITR No. 44 Lighting Control Fit off |  | ITR No. 44 Lighting Control Fit off
611153fb-aec2-4e62-9403-62311d297055 | checkpoint-no-value | Document
ecca0b8e-de44-5d9f-b355-be402ed020de | note | Drawing Rev No.
f7dc6804-67fe-4134-a656-7d2af3317071 | checkpoint | Area clear, tidy and accessible
cd49001f-1cb1-46e3-89b3-3068014483e9 | checkpoint | Dediacte one person to be in charge of lighting control fitoff.
63e42429-a9fb-4f2a-9414-a5aab9ea75af | checkpoint | Always use the correct tools to fitoff the lighting control equiptment
819d4de1-8ed6-49e3-80ce-531f86d6d2fc | checkpoint | Fitoff all sensors
d6ba9148-6c4b-4338-b3e1-1f628e46bf10 | checkpoint | Fit off all untumbra switches
8f71f0a1-35cd-4069-8302-69098b4f4c7d | checkpoint | Stick barcode of sensor/switch onto the designated plan in the location of the sensor/switch
17842911-9bc4-45fa-b7fd-040225910ec6 | checkpoint | Make sure all installed items are clean and undamaged.
94c4111f-4505-4570-b860-e3944e54141a | checklist | ITR No. 45 Lighting Control Commissioning |  | ITR No. 45 Lighting Control Commissioning
ec32559c-5d4c-48a7-bdbd-e96fcdf2d3a4 | checkpoint-no-value | Document
d1925349-cebe-5e7d-ae29-78893342a177 | note | Drawing Rev No.
f5da86b7-4aae-52f4-8d01-a3e0e7230a67 | note | Before lighting control programmer
3d36428f-08b1-483e-be02-c201c47621f3 | checkpoint | Area clear, tidy and accessible
e6f64108-8a94-4476-8773-03acc75241e2 | checkpoint | Complete testing and commissioning of general light and power.
1c0f98cc-37eb-4d74-8387-36506baaadea | checkpoint | Once lighting commissioning is complete, assess all sensors light up red upon registering movement.
b2c9945d-aba8-4cbf-8796-dc71a0f55ecf | checkpoint | Ensure all switches are illuminated.
4b098b5a-0a2e-4fc7-9518-4afc41792eb8 | checkpoint | Put Dali universe in flash mode, all lights on that universe should be flashing.
24ab7766-eb72-423a-8863-e85598896391 | checkpoint | Address any issues
9511d483-078c-56c2-9e28-bbb559adb8b5 | note | With lighting control programmer
083c4fa0-eb4b-42f1-b62e-fecff5b51a07 | checkpoint | Explain which fittings are to be programmed and what they should be programmed to do
bd706386-3f98-47ce-9d75-02b9fc796fc3 | checkpoint | Walk around with programmer, show him the DB feeding the lighting and control modules.
cad31ee1-e19f-4533-a885-1cedfcd6868a | checkpoint | Be on standby for any rectification works needed brought up by the programmer.
b5483c89-730f-4b70-b0c1-8f355ad6af2e | checkpoint | Visually see all working as intended before he leaves site.
466cd674-ab3e-4552-b89e-c6b6fbb764f9 | checklist | ITR No.0 5 Rough in |  | ITR No.0 5 Rough in
ca0913fb-3a10-4822-a7f4-60138b336676 | checkpoint-no-value | Documents
052c1403-ebbf-5bcf-b9c3-ba33dae0e583 | note | Drawing Rev No.
551e55aa-cb4a-44c2-96cd-5d03bf7a52c8 | checkpoint | Area clear, tidy and accessible
c4ac9695-ebb5-40d7-9c31-7763a572947a | checkpoint | Rough in of all lighting circuits- inc Emg/Exits and sensors
a5aede36-b687-4315-9cf3-b9d4c76900ab | checkpoint | Rough in of all external lights
9466d284-4f1a-4ddd-9c49-84bbc896b8bc | checkpoint | Rough in of all power circuits
1dfc8e65-f435-4f29-b8ec-b16fa566cc10 | checkpoint | Rough in all lighting feeds and label on plan
e26c93f7-5b16-435a-ada7-20deeeb24e41 | checkpoint | Rough in all power feeds and label on plan
d558870b-5415-4e10-8586-867219876e20 | checkpoint | Check for clashes with other services
a04a1c54-7b84-4f10-b7fa-42090e787d18 | checkpoint | Assess all relevent drawings to ensure cables are in appropriate location.
d33b5a3d-4e35-461b-bfdc-14a2569ac7ea | checkpoint | Ensure area is left clean
5982629d-9108-402a-9662-ab712757fcf4 | checkpoint | Make sure any junctions are left in an accessible area and clearly marked on relevent plans/uploaded to conqa
23b07780-92e3-4d1e-95da-fa0556dc9d82 | checkpoint | Lighting control to be roughed in by one person and path must be clearly marked on its own plan and uploaded to conqa. Any changes will require a new plan.
682a7a78-849d-4b67-b54b-76703efad3eb | checklist | ITR No.02 Cutout of Ceilings & Walls |  | ITR No.02 Cutout of Ceilings & Walls
89079483-4fe4-4661-82f2-06817f9d0af2 | checkpoint-no-value | Documents
fa9e6ed6-02a7-5f7a-ba44-bba84bd8db5c | note | Drawing Rev No.
82b58b20-347e-4b02-9d9d-05d5d929ac65 | checkpoint | Confirm sizes off all fittings prior to cut out
ee175da3-c2e8-41ba-892e-b9413d460bbf | checkpoint | Cut out for all sensors, EX/EMG and light fittings
82b4741d-dd83-46e3-946f-5aeaa416ccbd | checkpoint | Consult supervisor before cutting a patch of is a mistake is made
c4582cda-1a1a-4f17-b7e6-8db8d36ea994 | checkpoint | Cut out items on joinery to the joinery plans
930e0cf9-7491-4dd2-92e2-0a7142a5fc9a | checkpoint | Cut out GPO's
4c2d8139-0756-43d3-a21e-2b6ae8156475 | checkpoint | Cut out bathrooms and other wet areas to relevent wet area plans
ba8d77a0-2786-4c5d-ac75-f1e61761e70c | checkpoint | Ensure kitchen outlets are in correct position (where applicable)
1ddf8962-780a-4e66-a53d-ed6127e445ce | checkpoint | Locate all cables
b82ffd89-7e19-4910-8951-63ad38e7f475 | checkpoint | Install Fire Boxes and hit all 4 tabs in
a77b7292-b3ff-4a41-82c1-9ecfa4b13db7 | checkpoint | Fire caulk ( if applicable )
04b55e07-1ca0-41c1-81be-7747b71a092b | checkpoint | For AV power and data, consult relevent AV plans and coordinate with AV contractor
a7357c87-e45f-4c94-8766-14eb18e3b472 | checkpoint | FIT OFF ALL 413'S + QC'S + CEILING ROSES TO LIGHT FITTINGS THAT REQUIRE THEM
3a0176fa-a290-4839-a9d6-e7cea54642bd | checklist | ITR No.7 - Fit Off |  | ITR No.7 - Fit Off
a05a929a-4bbc-4b27-8bc0-719a90c895cd | checkpoint-no-value | Documents
10e55fa5-c408-54af-a53c-aa2f813ab098 | note | Drawing Rev No.
89df899e-11db-41a9-98f1-79471ca934cb | checkpoint | Area clear, tidy and accessible
245e01bd-3ec6-42d2-aa6e-c4ee29f6141e | checkpoint | Ensure danger tags have up to date contact & isolation details
271324a1-513e-4dd9-9eef-0a413ce35bfe | checkpoint | LOCK OFF & TAG circuits that require isolation (Ensure key is with supervisor)
b29535ba-4c43-4512-b34c-a433b6803a47 | checkpoint | Test circuits to ensure they are isolated
4119119c-8202-43b7-839a-c14b8b066344 | checkpoint | Area clear, tidy and accessible
898718cd-6aa4-4388-80fa-15658afdb055 | checkpoint | Fit off all Lights
cb102ddb-620c-4f46-9527-565dbc4d1863 | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
85c0d136-05d7-4637-8ec5-4dbca64b1391 | checkpoint | Fit off all EX/EMG’s
c765015b-3364-4b5e-bff6-bf32f6cccdde | checkpoint | Label all EX/EMG’s as per plan number
ecb96fd9-b8fd-4e9c-a814-1c4b4478098a | checkpoint | Fit off all GPOs
720b17fd-8873-4137-88ff-511c383f6a46 | checkpoint | Fit off of all isolators (signs, hand dryers, hws)
3df79fde-d2e0-467f-8e0c-08856f8f839a | checkpoint | Ensure all fit off has been ticked off on plans once completed
6c82ff12-f0ee-479e-a5dc-0356a93c4f13 | checkpoint | Ensure area is left clean
104666c0-5c06-4eef-8a6c-60e09acec05f | checklist | ITR No.09 In Slab Conduits |  | ITR No.09 In Slab Conduits
f8c1951b-d82d-4fb7-a385-1a48f012fe6b | checkpoint-no-value | Documents
277d9ec1-fd7f-5cc5-97c5-c2717f251997 | note | Drawing Rev No.
d62e2d93-f8ed-4eff-9c2d-09d532b9719b | checkpoint | Determine origin and destination
06fd26d8-2208-45fa-89ab-4ded78a97905 | checkpoint | Look at both power/lighting for above level slab and lighting/rcp for below level ceiling to determine where conduits are required.
52a98bec-a65f-40d5-abf5-afeaeeddd8b5 | checkpoint | Check clear of other services, penetrations etc
185b9baa-1199-49bd-9e8c-9dac61475970 | checkpoint | Check cable size to verify conduit size
dd5e844e-e2ba-403b-a165-865a2a7d805d | checkpoint | Check if expansion joints are required
039b477c-cfca-4316-891a-f30b5346a843 | checkpoint | Mark out positions of junction boxes and penerations whee necessary
073810d5-bbba-4074-b264-28e14d69c4c5 | checkpoint | Install bar chairs where necessary
7687c177-ceaf-4eb1-b812-64cdc3491ccc | checkpoint | Install junction boxes and penetrations where necessary
c550350d-a440-4ef4-a37b-41869627e369 | checkpoint | Install junction boxes and glue conduits
238c3d1e-9871-4705-94a6-8e34ef40df84 | checkpoint | Tie conduits securely at all joints and midpoints
f453a086-e244-4aca-b510-7b066ceefa16 | checkpoint | Ensure all conduits are 50mm above deck
aa5b11ca-5835-4208-a733-58f74e922627 | checkpoint | Mark up drawing of conduit runs (if required)
cd1156cc-c6a2-42f0-8531-dd0aa459de2b | checkpoint | Observe conduits when concrete is being poured
34a19e9a-1b91-4e39-a008-99b74d537200 | checklist | ITR No.14 Mains and Sub Mains |  | ITR No.14 Mains and Sub Mains
364e3d07-42e6-4a8e-86ff-5aec610f9bea | checkpoint-no-value | Documents
4afcd2b7-57a6-5128-971e-8bb0074946db | note | Drawing Rev No.
79472a0a-6438-4491-bbd3-706176de79b8 | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
1e86998d-8761-4c0a-b909-1636219798f4 | checkpoint | Confirm length of cable
afcebd23-d2ba-4cdb-826a-7ceb181d7d8d | checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
f0b6f51a-1d3d-5fad-8868-d7e4ef41dd45 | note | Any cable not terminated immediately must have the end taped covering the bare copper
d4be765d-a47d-4a9e-a777-5ff16357d5b5 | checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
81d0aacc-0533-4230-8674-cfde68b81b01 | checkpoint | Check cable requirements for cable identification and install
7969e409-a2aa-43ca-b04d-efed6e55bc3f | checklist | ITR No.35 Installing Underground Pits |  | ITR No.35 Installing Underground Pits
0e4948d7-24a0-4717-a51d-93c25f110e04 | checkpoint | INSPECT PITS FOR ANY DAMAGE PROIR TO INSTALLATION
fd0dc69d-f052-4789-9631-931779fead83 | checkpoint | SET OUT PIT LOCATION, ALIGNMENT AND HEIGHT AS SPECIFIED
dc62e6b5-d49d-40e0-ad55-4cff646f537f | checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
265fccf5-877e-4b35-9491-f9109a998d4d | checkpoint | EXCAVATE AS PER PLAN
af6944a8-a8e1-4eaf-b1c1-9fd02d7253af | checkpoint | PLACE SPECIFIED BEDDING MATERIAL AS PER REQUIREMENT
318b6088-54d9-4daa-a978-6d37d0bafb64 | checkpoint | INSTALL PIT AND CONDUITS AS REQUIRED
58546cd4-dbc2-4f20-9d23-fdd6f8052253 | checkpoint | RE-CHECK FINSHED HEIGHT AS PER CIVIL DRAWINGS
8bffbd94-0ad6-4138-9afa-4112d968ac29 | checkpoint | BACKFILL AND REINSTATE GROUND AS REQUIRED
b059b77a-5b4e-45fb-a988-edec9eff02c1 | checklist | ITR No.41 Field Commissioning |  | ITR No.41 Field Commissioning
bf482fb2-c94f-4fe0-8450-dac0eff56324 | checkpoint | Energisation permit completed prior to energisation
2974a6e7-3dac-470c-971b-239f058fe12e | checkpoint | Address site at prestart and inform of no access to area under commissioning.
de23844f-5f8b-46cd-badb-fb1a389daaba | checkpoint | Place all relevent signage and barricading and have LV rescue kit on standby.
a53e6fbd-45ba-4abc-94a0-ebd90507fc68 | checkpoint | Visual check of DB serviced areas
90e3a26a-111c-4e1d-a0bf-87426aa01fb4 | checkpoint | Dead Testing
f36f0c97-84d3-44ed-9598-71787c65ac5a | checkpoint | Live Testing
e1979ad7-78fe-49d1-9a2e-e90f48ea6e00 | checkpoint | Report any issues to supervisor and generate plan to rectify (if any)
93c325fa-8e0a-49ee-90de-873f367f3e1e | checkpoint | Perform a 2 hour test on all exit and emergency lighting (allow time for initial charging of batteries)
20e045c6-5ace-4ce8-8c2c-0550ed56296e | checklist | ITR. 12 Switchboard Commissioning |  | ITR. 12 Switchboard Commissioning
d560eed6-86b3-47cb-ae86-add670671c2b | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensure compliance With This Procedure
1d0738f1-2588-466b-8ddf-491729269442 | checkpoint | Place all required signage and barricading and have LV rescue kit on standby.
87ee4931-712c-418e-b50d-92902aeaa7eb | checkpoint | Refer To As Installed Drawings
6a99f65d-360e-4aef-a9b2-00f96a4d9994 | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
afb7b62e-7211-4551-a209-d1588505ac7b | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
32662d3d-200d-4c38-a2ff-e3cc41d3f71d | checkpoint | Complete Visual Checks
2edb843c-34b9-4cd2-afeb-61fd30cc37bc | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
b83e66db-7bfe-47be-8e30-54058a22e811 | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
58ffc0c8-837e-4bbf-8ac5-4d2a1ad13451 | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
cb7beb2f-0a10-4bb3-873f-f15b8f9d06de | checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
d2122a33-9063-4d1a-9f60-76d0c864f4e0 | checkpoint | Ensure Vast Witness Test Has Been Completed
094a74e4-52c9-4834-a9dd-384a8743a6d8 | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
807389a5-17b0-40b9-8d50-8d849f76ec00 | checkpoint | Ensure No Access To Live Parts
b612fb2a-f0db-41c5-addd-653e75e27259 | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
3d335ee6-8781-4484-94f0-fa728167ac09 | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
9252438e-7202-47b8-b3d3-ad04e4d3636a | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
41410b09-6ee0-4d52-894b-59ab2f631c8f | checkpoint | Take photo's of all Switchboard internals without escutcheon
240a937d-1286-49f5-9c03-0b3b0fca0170 | checklist | Preventative Maintenance Checklist |  | Preventative Maintenance Checklist
ec4087df-28ee-4d57-b793-b1ba4c5b77cf | section | Details
647d19d2-9505-4d2b-b17f-226617a896dc | checkpoint | Visual Inspection of Electrical Installation
3c164a23-c8a3-5a4a-a77a-baa3040c9112 | note | Lights are operational
d340f00a-de3a-5a73-b706-c7d1fc708ac7 | note | Light fittings correctly installled and not hanging down
5d124210-912a-51ab-a640-eca33688a437 | note | Switches and Power outlets securely fixed and cover plates not missing
059a030f-a04b-5200-b2cc-825e325574d2 | note | Switchboards not missing pole fillers
bdb3f546-c686-5176-90c8-fab37217778a | note | Any surface conduit or tray work is securely fixed
383f0ebd-af69-5ef2-bae8-40065df964d3 | note | Difusers, fitings, switchboard cupboards free from obvious debris
8f0bd831-d7b1-4634-9d44-3d6284c4b270 | checkpoint | Exit & Emergency Lighting Testing Carried Out & Logbook Completed
fb860070-e8e8-457e-9407-4cea1b23c237 | checkpoint | Operation of Switchboards Checked
38a11cd3-5fa0-52a6-a034-120add871558 | note | Performed at 12 months only unless otherwise advised by Builder
28e76edc-846e-4662-aafa-c445e3599e9e | checkpoint | Operation of Lighting Control checked
dfc6259c-ec36-4297-b852-74f87c50b9e2 | checkpoint | Check and replace fault lamps
17d24cf0-830e-4e0e-8e87-8e6caf7f045b | checkpoint | Fire Detection System Test carried Out
d2424c5b-0c1c-45b7-a134-5dc73fb34030 | checkpoint | Fire Detection System Test Results Issued
a3887c43-ae5e-4795-ad3f-a87a8de60655 | checkpoint | Switchboard Thermal Imaging Test Carried Out & Report Completed
57269f3d-2c21-564e-bd5f-467ad00485c6 | note | Performed at 12 months
deddd98f-d052-4a27-aea5-e0070fbd0ca5 | checkpoint | 40kVA UPS system check and filter clean
0bac54fb-d721-5c9c-860e-8d4c19730074 | note | Performed at 12months
de01d8a5-3510-477c-a09d-4306ebcd9be9 | checkpoint | 120kVA UPS system check and filter clean
770ae781-7d36-5434-a198-45187ac6b5f6 | note | Performed at 12months
0f62d89e-57a0-4260-831a-65fe04aeeb47 | checklist | Toolbox Meeting |  | Toolbox Meeting
decd8a96-685e-4f28-8e50-47e2bd93d09d | checkpoint | Details
acd446e9-425e-519b-992d-37c653e93b3a | textbox | Location
584c8b07-1952-52fb-96b1-d33f22ebebe2 | textbox | Supervisor
f2df7993-08bd-55a7-b963-f6a24029d7ac | textbox | Date
86bf3f4c-4b87-5460-95df-79f833b3d475 | textbox | Time
aada1ba2-e42e-522a-ae83-93188c9d606e | textbox | Persons present
2edb7a82-9792-5c51-b090-590b130131a1 | note | Topics discussed
8620ec71-f1d1-5bde-a218-01579e56052b | tickbox | - Injuries, near misses and incidents
dcd8d09c-2b0c-5491-af13-836000890d20 | tickbox | - Management of major hazards
eb62f661-8372-533c-a886-19ced59e43bd | tickbox | - Compliance with our Vast SWMS
109aba20-cfdb-59df-8651-ead89987567b | tickbox | - Safety - E.g., Apply LOTO processes when applicable. When Megger testing ensure that no person is working at the other end of cable being tested.
f3c0de5c-d953-5538-b42c-851b5412762b | tickbox | - Housekeeping
a8f4766f-f8aa-5b17-80ae-f20aa19b7cdc | textbox | Comments from the floor
afc579b0-8161-444b-9a54-76d0ef67c71d | checklist | zSYS - ITR. 12 Switchboard Commissioning (old version) |  | ITR. 12 Switchboard Commissioning
b53b9e1c-0fca-4c85-be8e-06dfdf6065fe | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensurecompliance With This Procedure
235dc450-f22d-4400-9a77-a57d62ca263d | checkpoint | Place all required signage and barricading and have LV rescue kit on standby.
b2ed405a-43d8-4c06-9d3d-e5b3587ecc78 | checkpoint | Refer To As Installed Drawings
76b8ceeb-1c23-4185-9642-75e66f128b3e | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
a927deaf-997b-4685-b638-7b153e9cbdae | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
37fef88f-4aaa-41cb-af05-9150d2eeb707 | checkpoint | Complete Visual Checks
402abdd3-f1b0-4e88-8bd1-f5fa09ca7ab3 | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
3d153722-f6f6-4889-91c1-b3a06ee8410f | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
530cb924-1ac9-4f17-b1d8-09eadaad1504 | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
02661de5-f221-4e42-910a-5e8c7bfdca74 | checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
045d773d-23c6-454f-b4f4-a76b6b38a8f7 | checkpoint | Ensure Vast Witness Test Has Been Completed
bec4d721-da3e-4bf4-8e3a-a7d08b2e7e60 | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
13df6274-4c80-4bbf-8ef6-aaa8d53cc374 | checkpoint | Ensure No Access To Live Parts
ce5f0504-4588-43fe-8fd2-c0191dce3d6b | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
c3de86ce-8878-4470-b781-b7760a23f8cf | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
50006968-da71-43d3-baac-8c59890e4376 | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder