## General
SECTION 1 – GENERAL DETAILS
Project Name: | Ōtaki to Levin Saftey Improvements | [5 empty] | Inspection Key |  | Responsibilities
Project Number: | 558010 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | 345084-NZ Transport Agency | [5 empty] | B | Report by Breach | CM | Construction Manager | Chris Colman | CC
Contract Number: | NZTA 6581 | [5 empty] | C | Check | ER | Engineers Representative | Luke Cameron | LC
Area/ Sub-System: | Ōtaki to Levin State Highway 1 |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | O2L ITP 5 |  |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager | Glen Flint | GF
ITP Description: | Covers all inspection points pre, during and post construction of the street light installation. | [5 empty] | I | Inspection | PM | Project Manager | Sam Christensen | SC
Discipline: | Lighting | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor | Richard Wild | RW
Specification: | Consultants Standard Technical Specifications TS1 NZTA M26 NZTA M30 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | For construction drawings : | [5 empty] | S | Subcontractor | SP | Supervisor | Richard Wild | RW
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: | Sam Christensen |  |  | Date: | 2023-05-10 |  | W | Witness Point | SV | Surveyor | Andre Wilkes | AW
Quality Specified: | Project Technical Specifications cross referencing relevant to Transit New Zealand (TNZ) & NZTA Z8:2022 | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Tipping |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:

## Item
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency |  | Inspection Type | Inspection
[8 empty] | Key | By | Checked (PM Initial) | Date
5.0 | Lighting | Final Sign Off | All below requirements are met and approved by CR | Referenced Item numbers as below | Once post construction |  | Hold Point | H | ER
5.1 | Technical Requirements
5.1.1 | Electrical Installation undertaken by qualified & "approved" technician | To be confirmed with Subcontractor prior | Relevant qualification documentation provided by sub-contractor. | Qualifying Documents | Once Per Source/Supplier |  | Review | R | PM
5.1.2 | Earthing | Inspection Post Install | Each pole to be separate installation, earthed using driven earth rod & M.E.N link - NZS3000 | Site Inspection Form | Once per pole installation |  | Witness Point | W | ER
5.1.3 | Testing and Commissioning | Completed Post Install | To be carried out in accordance with NZS3000 & NZTA M30 - Electrical test certificates for each lighting pole - Electrical Certificate of Compliance for the complete installation - As Built information - Completion Certificate (refer Appendix VI I of NZTA M30) - Any particular maintenance requirements (e.g., shear base poles) - Contractor to enter Ramm data for all installations | Relevant Documentation | Once per pole installation |  | Review | R | ER
5.1.4 | Poles and Luminaries | Documentation provided Pre-Construction | All lighting poles and luminaries to compley with NZTA M30, M26 & project technical specifications. | Manufacturers Certificates | Once Per Source/Supplier |  | Review | R | ER
5.2 | Construction
5.2.1 | Ducting & Cable Installation | Trench Inspection | Ducting to be installed as below where open trenching is possible - Required minimum thickness of separation 150mm - Minimum cover depth from crown of ducting 700mm - Type of ducting required - Orange PVC 100mm duct - Warning tape required over ducting minimum 300mm above duct | Site Inspection Form | Once per tench installation |  | Witness Point | W | ER
5.2.2 | Asbuilt of ducts | Survey Asbuilt | As-built location of ducting prior to backfilling as per design. | Suvey Records | Once per tench installation |  | Review | R | ER
5.2.3 | Trench Backfill | Density | Material is visually compact and tightly bound, and passes proof roll during subgrade inspection under ITP 2 Item 2.2.3 | Site Inspection Form | Once prior to subase placement |  | Witness Point | W | ER
5.2.4 | Pole & Luminaire Positioning | Check setout prior to installation | Poles to be located a minimum of 1m behind kerb/edge of seal & at right angles (90°) to kerb lines and lane markings. When poles are set in place they shall be vertical to within 1°. When each luminaire is installed it shall have the required tilt to within 2° The axis of the luminaire beam shall be in a vertical plane to within 2°. | Site Inspection Form | Once per pole installation |  | Inspection | I | PM/PS/ER
5.2.5 | Concrete | Compressive Strength | As per NZS 3112 - Concrete surrounding base to be minimum 20MPa at 28 days | Compressive Strength Report | Once per days production |  | Review | R | ER
COMMENTS
[6 empty] | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: