## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | F2LSIP - ITP 5 - Lighting | itp |  |  |  |  | F2LSIP - ITP 5 - Lighting
section | 5.0 - Lighting
checkpoint | Lighting
label | Inspection Point: Quality Control Activity - Final Sign Off
label | Acceptance Criteria - All below requirements are met and approved by CR
label | Verifying Document - Referenced Item numbers as below
label | Frequency - Once post construction
label | Inspection Type - Hold Point
label | Inspection: Key - H
label | Inspection: By - ER
holdpoint | AUTHORITY HOLDPOINT
section | 5.1 - Technical Requirements
checkpoint | 5.1.1 - Electrical Installation undertaken by qualified & "approved" technician
label | Inspection Point: Quality Control Activity - To be confirmed with Subcontractor prior
label | Acceptance Criteria - Relevant qualification documentation provided by sub-contractor.
label | Verifying Document - Qualifying Documents
label | Frequency - Once Per Source/Supplier
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - PM
checkpoint | 5.1.2 - Earthing
label | Inspection Point: Quality Control Activity - Inspection Post Install
label | Acceptance Criteria - Each pole to be separate installation, earthed using driven earth rod & M.E.N link - NZS3000
label | Verifying Document - Site Inspection Form
label | Frequency - Once per pole installation
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.1.3 - Testing and Commissioning
label | Inspection Point: Quality Control Activity - Completed Post Install
label | Acceptance Criteria - To be carried out in accordance with NZS3000 & NZTA M30
label | ○ Electrical test certificates for each lighting pole
label | ○ Electrical Certificate of Compliance for the complete installation
label | ○ As Built information
label | ○ Completion Certificate (refer Appendix VI I of NZTA M30)
label | ○ Any particular maintenance requirements (e.g., shear base poles)
label | ○ Contractor to enter Ramm data for all installations
label | Verifying Document - Relevant Documentation
label | Frequency - Once per pole installation
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
checkpoint | 5.1.4 - Poles and Luminaries
label | Inspection Point: Quality Control Activity - Documentation provided Pre-Construction
label | Acceptance Criteria - All lighting poles and luminaries to compley with NZTA M30, M26 & project technical specifications.
label | Verifying Document - Manufacturers Certificates
label | Frequency - Once Per Source/Supplier
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
section | 5.2 - Construction
checkpoint | 5.2.1 - Ducting & Cable Installation
label | Inspection Point: Quality Control Activity - Trench Inspection
label | Acceptance Criteria - Ducting to be installed as below where open trenching is possible
label | ○ Required minimum thickness of separation 150mm
label | ○ Minimum cover depth from crown of ducting 700mm
label | ○ Type of ducting required - Orange PVC 100mm duct
label | ○ Warning tape required over ducting minimum 300mm above duct
label | Verifying Document - Site Inspection Form
label | Frequency - Once per tench installation
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.2.2 - Asbuilt of ducts
label | Inspection Point: Quality Control Activity - Survey Asbuilt
label | Acceptance Criteria - As-built location of ducting prior to backfilling as per design.
label | Verifying Document - Suvey Records
label | Frequency - Once per tench installation
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
checkpoint | 5.2.3 - Trench Backfill
label | Inspection Point: Quality Control Activity - Density
label | Acceptance Criteria - Material is visually compact and tightly bound, and passes proof roll during subgrade inspection under ITP 2 Item 2.2.3
label | Verifying Document - Site Inspection Form
label | Frequency - Once prior to subase placement
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.2.4 - Pole & Luminaire Positioning
label | Inspection Point: Quality Control Activity - Check setout prior to installation
label | Acceptance Criteria - Poles to be located a minimum of 1m behind kerb/edge of seal & at right angles (90°) to kerb lines and lane markings.
label | ○ When poles are set in place they shall be vertical to within 1°.
label | ○ When each luminaire is installed it shall have the required tilt to within 2°
label | ○ The axis of the luminaire beam shall be in a vertical plane to within 2°.
label | Verifying Document - Site Inspection Form
label | Frequency - Once per pole installation
label | Inspection Type - Inspection
label | Inspection: Key - I
label | Inspection: By - PM/PS/ER
checkpoint | 5.2.5 - Concrete
label | Inspection Point: Quality Control Activity - Compressive Strength
label | Acceptance Criteria - As per NZS 3112 - Concrete surrounding base to be minimum 20MPa at 28 days
label | Verifying Document - Compressive Strength Report
label | Frequency - Once per days production
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER