## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | DEFECT LIST |  | DEFECT LIST |  | 5cf0eb00-c5ce-4de1-924a-81141a211a08
| section | Details
| checkpoint | Details
a48d6cc4-18a8-5f57-b74a-1f4e7685bd40 | number | Defect Number from Register
643df9e2-11db-5633-a448-c34b7f7a37cf | textbox | Location
d9185b86-bb21-566e-8153-2528c7ae9a7c | textbox | Description of Defect
7f524f64-0ad8-5082-be43-4d2c6fcfae89 | textbox | Assign to Engineer
| checkpoint | Walkdown
b565ed96-8e63-5bbb-be49-6f9117f5e3e4 | date | DATE
b9e5a6b7-2d2b-58a2-805f-c343284f8101 | dropdown | Category | A,B,C
| checkpoint | Attach Phtotos
| checkpoint | Close-Out
5dec0ddd-197e-5554-ba06-b1fab461e50b | date | DATE
8c75c134-1fab-544b-b4c7-07d2d8867739 | dropdown | Category | A,B,C,Closed
| checkpoint | Close-Out, Attach Photos
| checkpoint | PE Sign-Off
| signoff | Signoff
| checkpoint | QA Sign-Off
| signoff | Signoff
| checklist | File Upload |  |  |  | 2eda2ef7-996a-4391-bd44-7de1e51aeb7b
| checkpoint | Optional Document Upload Below
| checklist | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2 | itp | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2 |  | 1c6dc460-8091-476b-a2ce-699177311463
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
c60c84df-1b49-58cf-b11b-a418b623f5f5 | note | Ref docs - Issued drawings / Site copy drawings
27b52c1a-f966-5003-a5ee-d541c8c0c9c5 | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
c757d7ae-6f26-5a2a-b27a-b5bd5f4d1d37 | button | Acceptance | Yes,No,N/A
af9030db-2a2a-54ed-af9c-867c84bcf9c9 | note | HPP CON Key - S
106f7316-8d0d-5d74-9265-63467605ee7b | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
293b4f1f-30e7-5be1-b927-5144c449312c | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
7a1a3754-e0f2-5e4c-8de1-93612a8956a4 | note | Acceptance criteria - Prepare a lot map for traceability of the work area.
23661ccc-69d5-5485-834d-ed82e53f416c | button | Acceptance | Yes,No,N/A
66eca277-178d-5a8d-a085-59e626240b3b | note | HPP CON Key - S
faab98b1-75a4-5e18-a9a9-836a0f920e4f | note | HPP QA Key - S
| checkpoint | 1.3 - Set out
a39907b4-c760-5ce3-9fb3-bb5647fd20be | note | Ref docs - Drawings
19e04819-6d01-5023-ae3b-0f73c38fcffd | note | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
69934601-e4f5-594e-a07b-dfb805c8b05f | button | Acceptance | Yes,No,N/A
637640fd-6e6b-5f5f-a206-e30f9565b2df | note | HPP CON Key - S
6c0e1d82-c98b-5674-88a7-cbcfa08a3dc8 | note | HPP QA Key - S
| checkpoint | 1.4 - Underlying Lot Conformance
a4049f0f-e0f0-5826-bafd-d8a2c3345b6e | note | Ref docs - Underlying Lot ITP
b8236a7c-c6d9-55f3-b01b-68aa4e6603b3 | note | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
0ac16a93-bc94-5e4c-9337-ebbf4b018b64 | note | ○ Refer underlying lot ITP(s)
f09bcdbd-3336-5288-ac44-cbfbb8d176ac | button | Acceptance | Yes,No,N/A
00ace88b-6f05-57df-a43b-99283da2a24e | note | HPP CON Key - S
bfa433fb-2b5b-5d9b-9e7b-72a56c65d3ab | note | HPP QA Key - S
| checkpoint | 1.5 - Site Checklist(s)
32bc56b0-8cb2-5d3c-90e5-ab7c2a25873f | note | Acceptance criteria - Have Site checklist(s) been signed and uploaded?
d9b7a3d3-3883-5c95-a1b3-6eb9ed6dabf8 | button | Acceptance | Yes,No,N/A
4e146152-5e77-551b-abd2-0221f0f0eab6 | note | HPP CON Key - S
1756e808-b4ff-5143-9f9a-39a90a90d446 | note | HPP QA Key - S
15d89f3d-c29d-538a-ad81-8d542818de25 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
090e428b-da7c-5cf6-9141-217383e53ec3 | tickbox | Site Checklist(S)
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
3b8b2767-6792-530e-88b1-77b8e8069680 | note | Acceptance criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
85229522-06ac-5b5e-8723-22be12663ae2 | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
0f5dbbe2-3f30-5114-a650-6eb95db57fc5 | button | Acceptance | Yes,No,N/A
f2b0d068-4e87-5114-8178-60fb3de8b363 | note | HPP CON Key - S
9c84627f-73c1-544c-8930-fe34efe0952c | note | HPP QA Key - S
3c97fbcf-5a42-588e-9c82-3f1af4d039cc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
| checkpoint | 2.2 - Unsuitable Material
5426b24d-2901-51c9-ace8-7a872f38d00f | note | Ref docs - Spec. 1112 Earthwork s [Cl 4.6]
8ef2a836-5a4a-593f-b4df-78253403674b | note | Acceptance criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
a8d36eb4-a4a8-5875-8973-037801ad8285 | note | ○ HOLD POINT
7e365618-a204-507b-b90e-06699581e4f7 | button | Acceptance | Yes,No,N/A
f729a7fe-f743-52fe-8ebf-9645d513d5fc | note | HPP CON Key - H
bf494884-aca1-5043-8010-d2a02ef0ce6f | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction - Foundation
69db9fd3-d99a-5260-a7f3-8498b1760824 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.7, 4.13], Spec 0161 [CL 7.2]
ab05bf26-ae78-5a3e-ae6b-d85f92e7c13d | note | Acceptance criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 97% modified to a depth of 200mm below foundation level
d3c4e944-e310-5db9-a286-ed7197b7db32 | note | ○ Test Frequency = 1 per 500m2
4f2d7ee8-65ff-57c2-841d-6757de46941e | button | Acceptance | Yes,No,N/A
2b34550b-0bf9-5016-a1c2-3728e039a13b | note | HPP CON Key - S
77e38b80-4cdc-594a-b44d-39da84e7b0cc | note | HPP QA Key - S
6cb42743-474b-5fbd-86f7-a515260f4ff6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6f32605f-8c52-53cb-b118-e49920920531 | tickbox | Test reports
| checkpoint | 2.4 - Foundation Inspection
95ad6f1a-a51f-5fb1-83ee-24f551c37215 | note | Ref docs - Spec. 1112 Earthwork s [4.7]
f12fa3f1-d446-50ce-9595-7173058ac9fd | note | Acceptance criteria - Foundation to be inspected by the Superintendent prior to placing blinding
c004eb4b-dbb0-5568-bdf6-2e5434bf56e6 | note | ○ HOLD POINT
15f654bc-7f62-5b41-9423-cdaf5e2a8ef1 | button | Acceptance | Yes,No,N/A
cd5f360d-b988-5503-bab1-373eeaef6938 | note | HPP CON Key - H
fa9f8289-a7fa-5f69-80e9-50a399eb41c2 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Blinding
63edb35d-4763-597f-b887-45bb30fff3a0 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
2894bab0-030e-52e9-9bbe-1eb3d6015d31 | note | Acceptance criteria - Blinding (N15) for Reinforced Concrete Bases to be a 100mm thick mass concrete layer or as otherwise shown on the drawings.
d2d300f1-f7a2-5159-ba6e-f6691208fbbf | note | ○ Unreinforced bases can be poured directly on the earth
2870a525-a839-5f23-9cca-63ffaaa05d50 | button | Acceptance | Yes,No,N/A
8e4af1ad-574b-5e81-9974-e6b3dee5d43a | note | HPP CON Key - S
208f0f0d-9f31-5a1a-acc2-3504fb55e05d | note | HPP QA Key - S
| checkpoint | 2.6 - Mating Concrete Surface Preparation
ba9be1c7-c353-5e97-bb57-9953af79b95d | note | Ref docs - Spec. 0002 [CL 3.9]
1bae79c4-c065-57c7-afbd-a8dd9c39f3bb | note | Acceptance criteria - Construction joints prepared and free of loose material
f31cdbcd-6915-53f6-90e2-d5876191a727 | note | ○ Dowelled joints prepared and bond breaker applied for expansion joints if applicable
4a57aab1-bc4f-544f-8893-6620f4d2f63c | button | Acceptance | Yes,No,N/A
cf524272-f047-5fab-8ce6-af1a8e18c176 | note | HPP CON Key - S
93d33769-7a96-5487-ab3d-eede1cce7204 | note | HPP QA Key - S
| section | 3.0 Installation of Cast In-situ Structures
| checkpoint | 3.1 - Formwork
3cc9ba6d-efaa-506f-b3ad-4f5ecd323e06 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.0] Drawings
2df1831c-3ac1-50ea-8955-cbe03abf27b6 | note | Acceptance criteria - Formwork installed as per drawings and adequately supported.
4928edac-8e32-5eaf-93f9-5ec6e4f490cf | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
8803f5f3-fca3-5bdb-a6c8-4c1b5e98d1f0 | note | ○ Formwork engineers inspection certificate complete and received Survey report to be received prior to ordering concrete.
1f6d7ae4-fb05-5332-98be-c192fd495e7d | note | ○ HOLD POINT
9d30863e-b837-5a69-89e4-8713c272cabe | note | ○ Before Placing Concrete
ed72ee01-bed2-5b3c-8432-ea2d7482a209 | button | Acceptance | Yes,No,N/A
231d7d5b-4d3f-51f0-8102-72b691c30712 | note | HPP CON Key - H
f5a1ef13-b621-5a68-bee7-b7476de6f500 | note | HPP QA Key - H
4843d47a-c944-5a0c-a6b4-9d6e785e0a0d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a15889a8-fbd3-531d-b838-784bf08e0e7c | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Steel reinforcement
ac9f018e-a3bb-5926-9205-975c1cb10540 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.0] Drawings
0e6e0cca-f6c5-56a4-86b7-37fddee9cb65 | note | Acceptance criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars. Inspection per layer installed.
019bb8f0-b18c-55ec-bc14-632f412cfb3a | note | ○ Concrete pre-pour inspection complete.
f2a968ed-9bc5-5436-a3c2-f049400816ba | note | ○ HOLD POINT
ae514156-ffc0-54d5-a6aa-21288d906438 | note | ○ Before Placing Concrete
b282c6f8-e3b7-5398-9546-0dbcbdcf92c7 | button | Acceptance | Yes,No,N/A
09b98ce8-13b0-5230-9b0f-62421f6684e9 | note | HPP CON Key - H
5fffa92e-dff3-52c7-a543-a06d9a7e8c55 | note | HPP QA Key - H
6b1dd62b-6552-5a76-84a6-1774ac924842 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd7d16b4-80b8-5790-b038-672fe6f76c59 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Reinforcement Splice Lengths
60eba216-d399-51ca-acae-04291c2d06b8 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.7]
c0129881-53cb-5c56-8b2d-35c0ed86b139 | note | Acceptance criteria - Where splicing of reinforcement is not shown on drawings min. lap lengths shown below shall be adopted. (SPT-0002 Table 6)
41e5e9ab-be38-5e8a-a2b5-22dd34854ddf | button | Acceptance | Yes,No,N/A
2b10f850-c0ef-50e5-8519-ecc72ac271d9 | note | HPP CON Key - S
5cb118a2-2b4e-5eb6-9cd7-15840242f988 | note | HPP QA Key - S
| checkpoint | 3.4 - Pit & Pipe Connections
57fb4b92-3185-5ac0-a425-d0ad549be4a5 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3], Spec. 0002 Concrete supply, construction, and grouting [Cl 2.6] Drawings
cc27d066-f4e7-53de-9b1e-77e5227b7483 | note | Acceptance criteria - Inlet and outlet pipes to be integrally cast into foundation/pit walls and the joint waterproofed as per design requirements.
18329f62-221c-5baf-abdc-96643f16fae6 | note | ○ Embedded pipes to be adequately restrained against flotation
bd6d1fc2-60a5-526c-9bbb-e461a4eead02 | note | ○ HOLD POINT
dc92fa36-cafc-5090-955a-5162616e48d7 | button | Acceptance | Yes,No,N/A
126b4ce9-68a4-5898-8521-fa2e0226e258 | note | HPP CON Key - H
5762e6cb-16fb-587c-b2ef-8f71c6857229 | note | HPP QA Key - W
9a7fc328-f94e-5737-99e2-b517edb03d27 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - ITP for associated pit/pipe reviewed for conformance
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Installation of Core Holes, Voids, HD Bolts and Embedments
337fc49d-9a2b-5196-9304-516a4f949f83 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
d07b2da7-103a-5819-a15d-9b984ead675f | note | Acceptance criteria - Firmly Fixed in position in all directions
ebcca41d-a7e0-565f-8750-abeb64a223c1 | note | ○ Reinforcement displaced where necessary, bars requiring cutting approved by superintendent
9f97cb56-64c9-5fbb-a317-675be1c88349 | note | ○ Integrity of surface treatments maintained (galvanising, painting etc) Threads covered
ee74b250-085c-5148-a717-346c9336be99 | button | Acceptance | Yes,No,N/A
69f81e9e-e633-5f7a-84ac-ab7b8c1ebe5d | note | HPP CON Key - S
41ec78ca-c645-5971-b2a8-cd32b78bf95a | note | HPP QA Key - S
| checkpoint | 3.6 - Tolerances of Core Holes, HD Bolts and Embedments
07971b7b-4f67-533f-81a4-ba622283a52f | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
cedcac6d-5497-57c1-8fbd-fe001ab678af | note | Acceptance criteria - HD bolts positioned using a template. Tolerance for HD bolts as per CL 7.2 (see below table)
05e5488d-d141-5680-97ff-cdc75d983dea | note | – – – – – – – – – – – – – – – –
9384639f-ea1e-5d83-9c84-02412f27a83a | note | Condition ¦¦ Tolerance
d0b60f01-14fa-53fe-8788-5ad04322cf84 | note | – – – – – – – – – – – – – – – –
149654ca-d8f6-5452-8233-ae473813a991 | note | Any 2 bolts within a group ¦¦ ± 3mm Centre to Centre
503f2756-f6a8-50af-bb4d-19cc4f7d80af | note | Adjacent HD bolt groups ¦¦ ± 6mm Centre to Centre
d0301179-9829-51b9-9c08-119fb064df7c | note | Bolt Projections – From concrete level ¦¦ + 5mm, -0mm
42c6b0f5-3dba-564e-98ef-004a18ba3a7d | note | Embedded steel finishing flush with surface ¦¦ ± 3mm from surface
499c2e64-738e-5439-9b76-1a801fd124e5 | note | Bolt reduced level ¦¦ + 5mm, -0mm
4e4aca4e-56d3-581e-a14e-6d7efc0a0405 | note | Verticality of any bolt ¦¦ 1:300
37bfcef0-a7f1-5bdf-86a8-b41398e3a572 | note | – – – – – – – – – – – – – – – –
9635091f-0fe6-5b29-a400-3d90ca9ce57b | note | Maximum accumulation of 6 mm per 30,000mm along an established column line of multiple HD bolt groups, but not to exceed a total of 25 mm.
45109b99-aced-580f-b389-baa113829e6e | note | 6 mm from the centre of any HD bolt group to the established column line through that group.
7c7ca62f-81d5-530b-9bbd-2c5ea5552285 | note | – – – – – – – – – – – – – – – –
7bc10d94-7f84-5b6b-9737-4a27236651cd | note | * Before pouring concrete of the GT & GEN foundation, MPW TA will check the setting condition of GT & GEN anchor bolt. Witness Point as per MHI ITP.
ffc4ec84-8b44-55b2-b649-088e88da1e33 | note | ○ Tolerances for other embedded fabricated items in line with AS 3990 or AS4100 as applicable.
7b2840c5-f60a-5855-af09-f0fbfc6df691 | note | ○ Pre-pour survey performed and recorded to verify location
4ae78dd6-5d98-5753-bc15-9442fb7e6ca3 | note | ○ HOLD POINT
4bac51fc-e0f1-5f35-b588-35dd08bd0a7e | button | Acceptance | Yes,No,N/A
a4871036-f8a3-5542-ae37-957eb8ea5582 | note | HPP CON Key - H
2ec3b2a1-eb03-5e96-907e-ff70e370bd8a | note | HPP QA Key - W
6cd1443e-fb30-57b4-bd3a-35cb69617cc9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
85808471-4318-5ba8-a295-cc022dd7fde7 | tickbox | Pre-pour inspection and Survey Records Inc MHI Check Sheet for GT & GTG Anchor Bolt Setting CG-64294
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.7 - Earthing for Concrete Structures
fe3dcd26-f1c8-5c1d-a3e9-48f669582bc5 | note | Ref docs - Drawings Spec. 0002 Concrete supply, construction, and grouting [CL 2.6]
cde7527b-421b-5fb9-aad1-567c4625caf9 | note | Acceptance criteria - Earthing installed for concrete structures as per provided Drawings
cfd470dd-d375-5775-b083-998dcf03573c | note | ○ HOLD POINT
7fa907db-2a74-5b85-b51d-23b266ec7115 | button | Acceptance | Yes,No,N/A
404c8417-6796-5f05-92f4-1f2a3179c811 | note | HPP CON Key - H
e3b0a604-902e-5bb2-ae11-c147271d5fc7 | note | HPP QA Key - W
c81b894a-b9ff-5bd1-8ab1-f0c52f56d4b9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a5af57e4-d3f2-575a-818a-a9f952cd87c0 | tickbox | UGL Earthing FIC
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.8 - Concrete Mix and properties
88d8c435-87de-5761-b33d-4e43800de7c0 | note | Acceptance criteria -
9d02740d-6f7d-52b1-88f8-09b143b64a50 | textbox | Concrete compressive strength required (28 days) |  |  | MPA
1625ffeb-3852-52d9-b8b8-88e449b6c0e2 | textbox | Approved Concrete mix ID
4b8ef3b3-6ba5-577a-a1ba-5e65d868c696 | textbox | Slump |  |  | mm
4448dc0d-0f9a-50c1-8fc1-7295f84dda01 | button | Acceptance | Yes,No,N/A
959955a4-0db7-5ab3-b9fe-88ae3af0d9c4 | note | HPP CON Key - S
a6d477ab-833f-5a85-97e0-cd2a7b1df453 | note | HPP QA Key - S
b07f0337-09c2-5e9b-955a-15ae0455a298 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e021cc4a-296c-5d7f-850b-7f5ceabaf273 | tickbox | Material dockets
d0592693-43c4-5d96-88c7-5677d8dc1f84 | tickbox | Concrete pour records
| checkpoint | 3.9a - Concrete Supply Temperature - GT Foundation Only
35f7d8c3-bf2c-5ff9-8e9b-f4897935b04f | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2] Thermal Analysis Report
ebd4f1bc-bdb0-50fd-b372-c1784cac609b | note | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 25°C.
2c22cdac-e3b6-50bf-81f3-7fb7d6b4a79c | note | ○ Ambient air temperature at the time of placement must be between 5oC and 30oC.
98cfe851-1a78-5949-a584-8dfbb897441f | note | HPP CON Key - S
1183f600-cbfd-52fe-b248-9b48de445901 | note | HPP QA Key - S
559d0214-42dc-55b3-b6fb-ff5b606397ab | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3ec71db2-af72-5797-a8fd-5f6c951a5472 | tickbox | Material dockets
087a61dd-b65a-531c-bccb-0617c9deaaea | tickbox | Concrete pour records
| checkpoint | 3.9b - Concrete Supply Temperature - Other foundations
c35afc66-2df0-51ee-ae45-e70da0e665af | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
0940340c-05b8-5e07-a093-5bde3ca7b19a | note | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
76d97212-9e71-5ebc-9259-f84a141212a4 | note | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
2e9d639d-6e05-5855-808b-a76aafbda699 | note | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
6106368a-22bd-561b-8e36-8d67eb735bae | note | HPP CON Key - S
58d57739-e55f-5c7a-964f-54359370e5c3 | note | HPP QA Key - S
e5b4d62f-cd31-5b66-b04a-deb472efa957 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e71bfb8d-5540-5a8d-91d2-14edd0b07be2 | tickbox | Material dockets
98d74c5d-0304-55ea-960a-a796cdcbd6d7 | tickbox | Concrete pour records
| checkpoint | 3.10 - Concrete Placement
9f2de50d-41e7-5597-bbd9-e609adc2b7ec | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
764ec084-1d72-5ad7-ba25-baef327c3a4e | note | Acceptance criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
84b9244b-cf0d-5ee2-aa20-d5a7d6f92d1e | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
ea8205de-6b81-540b-8228-f57bcfe180ed | note | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
de8a9c71-290f-54cc-b315-adf85418c73f | note | HPP CON Key - S
2ad81e71-414e-5a37-9446-2c7e11fb2624 | note | HPP QA Key - S
b72f714b-8fec-5644-b2a8-b79b713d9b89 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2ba49439-f07c-511c-b936-f18ffe564ef8 | tickbox | Material dockets
25c4852b-659d-5f45-9b55-99e60acaa2d9 | tickbox | Concrete pour records
| checkpoint | 3.11 - Concrete Slump Testing
5b9f099c-20f0-5739-93aa-b745b6edbb43 | note | Acceptance criteria - Slump Test - One per batch of concrete
1b7fbf04-779b-594f-9a6a-80acc77f8d8b | note | ○ Slump within tolerances specified in AS 1379
96624dfe-946f-5afb-8816-e0f66519c218 | note | – – – – – – – – – – – – – – – –
81fb2849-189d-5116-bc2e-c2ce6f100c5f | note | TABLE 5.1 PERMISSIBLE TOLERANCE ON SLUMP
4658b425-cca7-5c1a-b6fc-bbbe498a5fe6 | note | – – – – – – – – – – – – – – – –
e1c70c06-c24b-51b4-a154-1b903baf9a20 | note | Specified slump, mm ¦¦ Tolerance, mm
16ec52d6-613b-56de-9c2e-881e7ad15a36 | note | <60 ¦¦ ±10
05116e1b-ad67-586c-ac4a-1f898a9962dc | note | ≥60 ≤80 ¦¦ ±15
1e2af528-b471-5afa-aeb4-1687404d3609 | note | >80 ≤110 ¦¦ ±20
ce890bb2-ae9f-5720-b611-3eb5a2efbb8e | note | >110 ≤150 ¦¦ ±30
ba297919-053a-58c4-bac9-e8df4d463ae5 | note | >150 ¦¦ ±40
1a676764-2fc1-55a4-acc1-98f2f376b972 | note | – – – – – – – – – – – – – – – –
d11c3fce-4d03-5c18-bb45-f063b0256ab3 | note | ○ Testing to be executed by a NATA accredited test facility
98b3aec1-f598-5dca-93d9-f0467ed0182f | button | Acceptance | Yes,No,N/A
27270519-e8cc-5459-9fb0-71d1cabd91dd | note | HPP CON Key - S
8539b4ed-6665-538d-895c-75c884d37e2e | note | HPP QA Key - S
a6d1870f-ddbf-5597-a69f-79ab50488a9b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a77dac0d-02f3-5657-9438-5f8ff8972111 | tickbox | Concrete pour record
| checkpoint | 3.12 - Concrete Compressive Strength Testing
b9ebd3f1-c936-5e3d-96c8-f4f94913f0b8 | note | Ref docs - Drawings
3123de94-a33c-5888-8743-c2d7fc42f9f2 | note | Acceptance criteria - Compressive Strength Testing - 2 x 7day and 2 x 28day per 50m3
026bc221-7673-539f-b1db-6b1c41fab104 | note | ○ Testing to be executed by a NATA accredited test facility
a6a3ea46-21ea-50f6-af9d-b6d15b2cd755 | button | Acceptance | Yes,No,N/A
fa54ee5f-7895-5887-aa14-9b1a04424625 | note | HPP CON Key - S
006dd9d9-2d97-5a79-8e42-2d3173ba540b | note | HPP QA Key - S
8899d1d4-5e51-50a3-85a4-8be961059375 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8e0972fd-b94c-5426-868a-c363ddc91103 | tickbox | Concrete pour record
| checkpoint | 3.13 - Surface finish
e4312dd8-a9c7-5709-93ae-4529afdb2a56 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2] Drawings
dbfc1aee-224b-503e-be4b-366f86ad10d8 | note | Acceptance criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
b8ae8951-6e62-5e0e-a234-85598ef899f7 | note | ○ Formed surfaces conform with surface finish requirements of AS3610 for the surface class nominated.
79fa46d6-50de-581d-8b12-ce952e0de138 | note | ○ WITNESS POINT
8943fd5f-546a-5289-972a-f632a08bd33b | note | ○ 1 day prior
4f272d95-264f-58de-a0d6-b1b6ccc69228 | button | Acceptance | Yes,No,N/A
120c236b-ef33-53fb-8622-0ae1ec5476c2 | note | HPP CON Key - W
d3f7b209-8841-57e7-be9d-97e25298a35b | note | HPP QA Key - W
| checkpoint | 3.14 - Surface Treatments
8c1fdc14-2157-5627-ab09-cd8b8c2c8700 | note | Acceptance criteria - Any surface treatments to be applied are approved for use and appropriate dose rates have been determined
1035ad11-11d2-53f3-b074-a73a9700e768 | button | Acceptance | Yes,No,N/A
8b620b08-a8de-5796-99ba-6b85e132375f | note | HPP CON Key - S
f46d2b7d-3150-5e40-8f16-130dfb8a5e73 | note | HPP QA Key - S
| checkpoint | 3.15 - Joints
e65a9e6a-0dcb-51a5-83ed-2ddcc653bf1a | note | Ref docs - As per drawings
665c6405-f1aa-57e8-8305-febada7c26aa | note | Acceptance criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
27df5007-1afd-5fe0-babf-dc6ad34a1a4b | button | Acceptance | Yes,No,N/A
7fa0db36-44a0-52bd-947b-005213c7be25 | note | HPP CON Key - S
c001d7c1-3284-573d-9a3a-b177b1f8544f | note | HPP QA Key - S
| checkpoint | 3.16 - Curing
94bb7700-ab5b-508f-8626-8e2544947b28 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
dc69f3c4-f35b-5743-84bd-921ca3b5cb53 | note | Acceptance criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
3b5d7966-3f4c-5ce4-8e9c-c657ec12d03c | note | a. Ordinary Portland cement concrete – 7 days
7bbf6599-0027-599b-b0b2-1ae95334afc0 | note | b. High early strength concrete – 3 days
c6d2b559-813f-5013-9a6b-98d060af180c | note | c. Concrete with cement or pozzolan materials – 10 days
873066b8-3106-5adf-9832-e6b1da18e0c6 | button | Acceptance | Yes,No,N/A
d9f1d4b3-54ab-56f1-a0e1-248f44e17237 | note | HPP CON Key - S
458a34d5-011f-563d-91d8-5446ac32447d | note | HPP QA Key - S
| checkpoint | 3.17 - Stripping of formwork
35b777e6-badd-5fe2-8442-776cdf8b3457 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.4.5]
9e03ef7a-fb00-5921-ac86-3c518b752a3e | note | Acceptance criteria -
1e69a203-a31d-5e78-8faa-199ffdae563b | note | – – – – – – – – – – – – – – – –
01470246-51dc-5365-9433-688f2a805d4c | note | Member Type ¦¦ Member ¦¦ *Effective Span mm ¦¦ Minimum Stripping Time (days) for Average Air Temperature during period prior to Stripping
7aad0af7-bc0c-580a-ba07-41d92fd2e632 | note | – – – – – – – – – – – – – – – –
764c8c3a-e837-5084-8516-0d622e51f631 | note | - ¦¦ - ¦¦ - ¦¦ 20°C and over ¦¦ 10°C to 20°C ¦¦ 4°C to 10°C ¦¦ Under 4°C
ef5d86d7-c2e0-577d-9610-ac8c8e5cdf9f | note | Vertical Unloaded ¦¦ Wall, column, beam side, slab side ¦¦ 0 ¦¦ 2 ¦¦ 3¦¦ 5 ¦¦7
c8eac0eb-4593-5918-bd8f-fad3512f9ae7 | note | Vertical Loadbearing ¦¦ Wall, column Or loadbearing structure ¦¦ 0 ¦¦ 5 ¦¦ 6 ¦¦ 7 ¦¦ 9
2b37da7c-c690-5be3-8e14-8990cab57864 | note | Horizonal ¦¦ Slab ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 7, 10, 14 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28
ec14358e-9018-509e-a5b7-39ca78ede5eb | note | Horizontal ¦¦ Beam ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28 ¦¦ 28, 28, 28
e6c937d4-6f9a-525a-adc9-caa35af7e11c | note | – – – – – – – – – – – – – – – –
2a1cb5f5-565e-5482-95c0-91be2c29985f | note | * Effective span is the maximum distance between supports (either temporary or permanent)
8ed4499d-1b5a-5fa2-991e-80b79412bb38 | button | Acceptance | Yes,No,N/A
093530d8-5b61-5f96-877e-8de2c2978a10 | note | HPP CON Key - S
e8e9386f-a035-505f-a6cd-493acf0d3911 | note | HPP QA Key - S
| checkpoint | 3.18 - Concrete Repair (If required)
5e9a21a8-f820-5c8e-9c2b-10cd6b69ec3e | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.7]
e06a559e-22f3-54ec-9abb-fabbb9e96515 | note | Acceptance criteria - Defective concrete shall be repaired or replaced. The materials and techniques of repair shall be examined and approved by the Superintendent prior to the commencement of repairs.
60e0d1cc-1850-5e38-b15d-fb0f3c86eb80 | button | Acceptance | Yes,No,N/A
25f88d95-00cb-58e2-a684-1a6367f86180 | note | HPP CON Key - H
70f2304a-f11e-5558-a690-c5ded96e869c | note | HPP QA Key - H
191049c2-b196-55e2-9876-7d817a847a30 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a7f5c8a8-314a-56c1-8bb2-9d2da2ad29e2 | tickbox | Grout Placement Checklist
4f4640ea-7a9b-56c2-8b80-d92ef1c69ec0 | tickbox | Approved Aconex Corro for Repair Methodology
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Backfill and Compaction
| checkpoint | 4.1 - Structure Backfill
59c6f5de-f4a6-53e4-870d-d5eaf942cc4a | note | Ref docs - Spec. 1112 Earthworks [Cl 4.10]
349dd079-d528-56c5-8a27-dc8601602217 | note | Acceptance criteria - Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
9caee80f-f5fc-52fc-813e-c44fc842d893 | note | ○ Placed in layers of maximum compacted thickness of 150mm
92a5817c-5ee2-51e0-9320-dab8ce122e39 | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
e860e39e-7d4f-5d07-a7ad-027b129c661e | button | Acceptance | Yes,No,N/A
77d67d54-d548-55bb-80bd-d008339f3bfa | note | Key - S
57645045-5a0f-51af-8eb3-3231bd1a1316 | note | HPP CON Key - S
73a549e2-4f8e-572d-81d6-6ed671d0675a | note | HPP QA Key - S
52b9d4f8-d140-543a-9706-185b1e2fc4cb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
104a1dbd-a834-5ea8-920c-91d265cdf1da | tickbox | Material Test Report
| checkpoint | 4.2 - Compaction - Backfill
b89ae186-c174-591f-9ecf-f51694aeac5e | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
5486e8f2-b6c8-576d-b245-27d6dba40a51 | note | Acceptance criteria - Minimum relative compaction requirements for backfill against structures to be:
1cb72897-a5b6-5219-8173-6d289a0f0e43 | note | – 92% for general fill
47224381-ee3c-5630-964a-f44678c1dc44 | note | – 97% for select fill
bac16d63-e9b2-5936-a73c-b3b20c1b63d4 | note | ○ Test Frequency = 1 per layer
f5223613-e16c-55f2-99e8-5535c68cc454 | button | Acceptance | Yes,No,N/A
5d1bdefc-bb83-5f75-bd07-6351eb18cbee | note | Key - S
0cb57372-04a5-51bd-9c87-90e230f48a67 | note | HPP CON Key - S
da778957-246d-578d-abc0-1c35719642c7 | note | HPP QA Key - S
c2d4c4ee-a13d-591f-a955-c98e6be4a4f7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a899bc54-24c3-5b1d-b5d8-be38f1b4fc35 | tickbox | Test reports
| checkpoint | 4.3 - Moisture Content
c4da9a38-cfd3-5f3d-a296-a79307434fef | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13 & 7.1]
3a947d67-ec5f-5219-a148-771ce7bdfb6e | note | Acceptance criteria - Moisture Content for Backfill material to be within 60% to 90% OMC unless otherwise approved by Superintendent
388a1cd8-f979-5bfd-9ace-f10312af56b9 | button | Acceptance | Yes,No,N/A
13575a25-f01d-5fcb-b96e-ae2c7bebcc1f | note | Key - S
481ba2c2-b3f9-532b-96c6-7b42c7bffb74 | note | HPP CON Key - S
b5e00f0f-4056-573b-8819-bc6485ccc290 | note | HPP QA Key - S
fa7f6cab-f070-59b7-909f-918c250c5dee | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bfdda01c-9157-5215-8bac-72dea317b87d | tickbox | Test reports
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey Report
29f9ec94-6368-50b2-8d73-c06750bd74fc | note | Ref docs - Spec. 0161 Quality [Cl 3.13] AS3610
fa1741f5-91d6-5395-a170-3d0f940ade47 | note | Acceptance criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
efc150b7-decf-50e2-a54d-1112885f0942 | note | ○ Absolute position in plan shall be within 10 mm.
1641c1da-816c-51f9-81a9-fcccb33ffe3c | note | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
a6053e4e-594f-5912-b738-1fca6ca40196 | note | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
551b5a3e-cb86-577f-ba5b-461c88d5d88f | button | Acceptance | Yes,No,N/A
06962e6e-8236-5627-bf5d-f5393da75cb2 | note | Key - H
54b626e2-40fd-52e7-8b5a-492c6610ff0c | note | HPP CON Key - H
ffef801f-4f9a-5a08-84ee-cc1b958403f1 | note | HPP QA Key - W
85b88ed7-06b6-58b2-bbf1-5543ce2dfc3c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
25a5449c-936e-5169-ae46-7c7bf59f74be | tickbox | Survey report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Concrete Test Results
64f3e2b6-82a8-5a01-9dbf-d5740038d4cc | note | Ref docs - Spec. 0002 [Cl 8.2]
f8e74bdd-7a8c-5879-a074-5a29d6194aa5 | note | Acceptance criteria - Certificates received, reviewed and conforming to requirements for each pour.
5d1f06b2-f61f-5ee5-9a48-ff9afebe4d1f | button | Acceptance | Yes,No,N/A
bccafc4d-e697-5769-89e7-7b2db3ff85bb | note | Key - S
385efe8c-ed08-501a-bf91-78225cdfa508 | note | HPP CON Key - S
0b4672ba-84e5-5265-85ce-25d0bbabe724 | note | HPP QA Key - S
a99de69a-a0f2-58e0-8989-70f8d6ca4c0a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bb72dc0e-43bc-594d-aacd-4988b628abb8 | tickbox | Test reports
| checkpoint | 5.3 - Acceptance and closure of non-conforming items
15faa6b8-fca2-57ea-8ac9-a3d8bd896424 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
6ed162a6-ba8d-5296-b135-e95de0633a22 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
623c84c6-34fd-55fe-9055-27d9cbf27935 | note | ○ HOLD POINT
507bbb34-4bb5-5c11-9375-91a90202dbda | button | Acceptance | Yes,No,N/A
e7611d8c-dc40-53ef-a940-f6a294e0b195 | note | Key - H
980564ee-0691-5f61-9388-fb07d2648b89 | note | HPP CON Key - H
532712e8-fd7a-528f-8bf0-ebbd210ca22b | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | HPP-UGL-CIV-GN-GEN-ITP-019 Driveway Entrance Pipe Crossing - Rev.1 | itp | HPP-UGL-CIV-GN-GEN-ITP-019 Driveway Entrance Pipe Crossing - Rev.1 |  | b10c2d8b-7dbe-4dec-b721-d3774207eed0
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
afb2dd00-c703-516f-941d-24b029c18f73 | note | Ref docs - Issued drawings / Site copy drawings
f937cb9d-bd60-5562-ad4c-b2e0a4f72c55 | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
cc0dfd97-3dd6-5e27-9fca-9c0b0259edb1 | button | Acceptance | Yes,No,N/A
5da67ddf-ac9b-5fab-a6e5-a7cbbddf9b7b | note | Key - S
9908bb97-3b1e-52c8-b674-6f7a209c97ae | note | HPP CON Key - S
7de78131-165c-51be-b62a-ff322b0231a4 | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
a82094aa-16b1-5c4f-a4f4-9325fea0fa4e | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
655f18d1-ea91-5a33-8f1a-c3b3c0ae5939 | note | Acceptance criteria - Prepare a lot map for traceability of the work area.
4fa17514-fd43-5331-b159-5aa29ca62370 | button | Acceptance | Yes,No,N/A
f47fae1a-6938-5219-92da-65069a002fc4 | note | Key - S
8815354f-e8af-5991-9e02-f8cf903c30bc | note | HPP CON Key - S
b5424051-822e-5f26-989e-d909e9536be5 | note | HPP QA Key - S
71da13a5-a02a-50e0-ab8e-1afedbea08cd | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bd584b66-6f0c-5534-868e-afbf9120c128 | tickbox | Lot Map
| checkpoint | 1.3 - Set out
3c4e7e44-ef48-588a-809b-ae4dd29605ea | note | Ref docs - Drawings
745f6d8e-b99d-5d1f-a50a-769e9879b4bf | note | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
2f5cd178-9774-57c6-95c0-ac5a4f923814 | button | Acceptance | Yes,No,N/A
9610e793-49fa-5e73-9104-68d138ecf0ad | note | Key - S
4e9db103-8272-59cf-a497-02ccd04df774 | note | HPP CON Key - S
9e489d0e-adde-52bb-9498-9816d00eca3d | note | HPP QA Key - S
| section | 2.0 Excavation & Foundation
| checkpoint | 2.1 - Excavation
2dbc9124-9b75-5b70-99a2-e5f872023c80 | note | Ref docs - Spec. 1112 Earthwork s [Cl 4.6]
e2fe28fe-902d-5775-a570-6f23e4bc51de | note | Acceptance criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
f371c25c-c823-510b-8ea5-c2c6663d410d | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
9d78e5c3-745e-5ab7-981f-d411421fd808 | button | Acceptance | Yes,No,N/A
dd7a93ef-15d0-51c1-b5f7-9558e356448b | note | Key - S
85a4c3b6-28a1-5418-ab33-e82dfb194bcc | note | HPP CON Key - S
7250d3f8-879b-5583-9898-7c556712618e | note | HPP QA Key - S
| checkpoint | 2.2 - Unsuitable Material
eddfd920-44db-5d64-b8fb-0a53d5cfdeff | note | Ref docs - Spec. 1112 Earthwork s [Cl 4.6]
47922249-4ed2-5f04-b2b6-f1f49ac45ed7 | note | Acceptance criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent.
d09adb6d-43bc-5de3-a1d8-27f10aa1a3fa | note | ○ Replace unsuitable with 300mm thick ballast wrapped with Geofabric material.
42e60d89-b838-5465-8dec-f1943c3e4e53 | note | ○ HOLD POINT
e352f651-d3aa-5fbe-b002-ec353e083a42 | button | Acceptance | Yes,No,N/A
b8825ccc-23b6-5a2f-8113-d3021f18f6f3 | note | Key - H
e27159e3-c72c-54d8-95e4-ca37173db11e | note | HPP CON Key - H
d7dbff26-0d08-5408-946a-b3bb015bd17f | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Foundation Inspection
63ae7e7f-13ef-5196-be1c-e2c9e64f3634 | note | Ref docs - Spec. 1112 Earthworks [4.7]
e6ad4e60-7a87-58b8-a6bf-e909f2cbe89e | note | Acceptance criteria - Foundation to be inspected by the Superintendent prior to placing blinding or commencing work.
9230cbc9-d94d-5ad3-9b0a-3f3087b126d9 | button | Acceptance | Yes,No,N/A
2c95357f-9c90-53dc-b452-cbaf5697bf0b | note | Key - S
6bcc1cec-f0b9-54c0-a59b-611015fc6eb9 | note | HPP CON Key - S
aa44d8a0-2e13-55c4-a9a1-7d52c396dcd1 | note | HPP QA Key - S
| section | 3.0 Formwork & Concrete Placement
| checkpoint | 3.1 - Formwork
8bd94c76-526a-57f2-b3f6-049a0d5c1442 | note | Ref docs - Spec. 0319 Concrete supply, construction, and grouting [Cl 4.0] Drawings
b12c94ec-86ea-55f4-b0b7-d5ed9cb413f2 | note | Acceptance criteria - Formwork installed as per drawings and adequately supported.
82c60870-8c64-5896-a104-388c0c2ff3da | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement.
038c7ab2-97c9-5bac-a9a7-edec71092ecd | note | ○ Install 2*dia. 300 stormpro pipe to levels, 50mm below drain invert.
ef67dccc-73e8-5fd8-9a5e-fa7502f51bc5 | note | ○ Formwork engineers’ inspection certificate complete and received
16b801bf-c505-5d00-b18a-03df5f198cd1 | button | Acceptance | Yes,No,N/A
67abd2b9-23ac-5ff5-bcd8-b6cfa1f39b2d | note | Key - S
a440a00b-b130-5eba-b633-188802436c32 | note | HPP CON Key - S
e9d6b72a-02fd-5fe4-9f7c-f3da7acfa53d | note | HPP QA Key - S
85fe97be-505e-5e00-b35a-c8d0c003025a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4f54f1ba-72ae-575c-84c2-e1d44b7ca3f3 | tickbox | Pre-pour inspection
| checkpoint | 3.2 - Concrete Supply Temperature
4545a08c-0e2f-53d1-bd38-19268781d185 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
f4afb945-4c82-5681-b37f-301b6534b9ba | note | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
1ea67f49-fa68-5baf-bb5d-b72595099f1f | note | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
21c8ca76-576c-5a0e-88a0-2e8e6b96bd3d | note | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
8cf64818-2f7f-5769-bb5b-dd59b4832f2e | button | Acceptance | Yes,No,N/A
ec49c010-933f-5c72-85d0-845eecbdde37 | note | Key - S
cb07ab9f-e80d-5574-9c20-c8a81ecbe365 | note | HPP CON Key - S
8b727c23-1472-58d2-a78d-b2d2a5e69110 | note | HPP QA Key - S
8ed99f3e-d265-5c61-9dd1-250e14d4af5c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8b73ce19-8dc4-5ed8-83ab-f04da84f2d7e | tickbox | Material dockets
7d8d373e-3854-5bab-a4b5-076a2e786881 | tickbox | Concrete pour records
| checkpoint | 3.3 - Concrete Placement
0e47426b-4a75-5a03-adc7-113c84882a19 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
1b77c42e-a866-567a-8864-601880c5259b | note | Acceptance criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
8eb3617b-8c9f-57a9-9192-32c6c9748b19 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
e64e932e-f2e7-5236-a4e2-141ab01011c9 | note | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
e06afe7a-a31a-5a96-ba10-a802573a1942 | note | ○ Concrete strength of Cast-in-situ units shall be min. 20MPa or as otherwise stated on drawings.
0031759c-6623-5580-8590-d45939db6d08 | button | Acceptance | Yes,No,N/A
d0b2bd23-bd6b-570c-8ac0-e2f5d8bccf6b | note | Key - S
9e2a45a6-ca63-565e-9d8f-77fad2a25d5f | note | HPP CON Key - S
cec64a74-5006-5765-a465-61d69bbc66f4 | note | HPP QA Key - S
6b294560-4886-59f0-a174-f09c450c472b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5fdc29a1-26c7-5a47-85b5-3c93654ca575 | tickbox | Material dockets
c03ece4a-d9aa-5d80-8127-84ed8a3d575c | tickbox | Concrete pour records
| checkpoint | 3.4 - Curing
d0699f78-000d-55df-a753-18a03f3b8a89 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
06d59e3a-7d9c-5dd6-b14e-e0e5a83923fa | note | Acceptance criteria - From completion of finishing cure continuously with an approved method such as either curing compound, wet curing or form retention until 15MPa is achieved unless directed otherwise by the superintendent.
db110b62-3062-5ae0-982f-5cdde7212da3 | button | Acceptance | Yes,No,N/A
48d51c59-986d-5cf1-b570-04668568d88f | note | Key - S
5e2975cd-8182-54f3-8b42-8e7aa055be8b | note | HPP CON Key - S
37fe9868-e4a0-5fa6-adde-8919ff8b48ad | note | HPP QA Key - S
| section | 4.0 Conformance Check
| checkpoint | 4.1 - Survey Report
953dbcef-2832-5cf1-aaee-3b9dc824969c | note | Ref docs - Spec. 0161 Quality [Cl 3.13] AS3610
7149bb78-c827-5772-ac12-def23626b712 | note | Acceptance criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
e3516b5d-3b34-5ce1-9579-0aff8791522d | note | ○ Absolute position in plan shall be within 10 mm.
3c7b46b9-ccda-5770-948a-6ce30625e1d7 | note | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
ea4d7a89-78f9-5c59-903b-5c95e9f4b70e | note | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
15fb992f-b1b9-59a5-b24f-597d840fa306 | button | Acceptance | Yes,No,N/A
f6c6751a-505b-5ef2-ab31-c4eb81e52fe9 | note | Key - R
d85612ef-d104-52c3-a9c6-ffb6d2be5a0f | note | HPP CON Key - R
aef68ffb-c9d9-556f-b8ba-4d1fa673e1e1 | note | HPP QA Key - R
1a32bf26-b1e7-5cef-86a9-9337948abe18 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4609fb76-19ff-55c2-bb92-b5aaaf495e7a | tickbox | Survey report
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
86bddd35-72ff-58da-98bc-9c55e734bd4b | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
973ff2a8-a1d0-553f-a48b-a2c2457d47f1 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
8cda766d-9032-5a2f-abec-72a88dd93b11 | note | ○ HOLD POINT
87c996dd-403e-5500-8659-a2357b1ac2a8 | button | Acceptance | Yes,No,N/A
10a1f8d2-f9fe-592f-b848-e7c91788ac0e | note | Key - H
12eff469-de34-542a-88a1-0cb6d6923de3 | note | HPP CON Key - H
67bac52a-906e-5aaf-a954-468bf9c35011 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-001 Bulk Earthworks & Checklist - Rev.5 1 | itp | INF-HSEQ CC0375-ITP-001 Bulk Earthworks & Checklist - Rev.5 1 |  | 88fbcd33-6954-4124-8bb4-46efae87e1fc
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
4696e360-6706-5633-9663-8bcbe15254d0 | note | Ref docs - Issued drawings / Site copy drawings
013def14-cf79-5efb-869c-2b9bbb83305f | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
b9c399fc-6343-5a03-9f4d-50ee36d84a0d | button | Acceptance | Yes,No,N/A
6135b702-35a2-58cf-bcb6-1559fb507f98 | note | Key - S
85b45940-dae0-56c1-9a06-51985d98d5f6 | note | UGL Key - S
| checkpoint | 1.2 - Lot Traceability
c3a326aa-c6ab-5aae-9640-610b03b84454 | note | Ref docs - Spec. 0161 Quality [Cl 7.2]
fd603c18-bd36-5ed4-a905-4ec863558523 | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
f7753dac-8340-5916-acf4-c75c82a06687 | button | Acceptance | Yes,No,N/A
86107e68-e40b-57ab-a460-b896d999dcf1 | note | Key - S
1317bf0e-2a16-5d3c-87ca-bd979da777a7 | note | UGL Key - S
7c49259a-b987-55b1-ba10-b19b97523ddb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Lot map
| checkpoint | 1.3 - Survey set-out
87133787-5225-5350-839c-53fd8c6bf54e | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 2.2]
3068e502-ed19-51e2-8b4b-ac8b489ba282 | note | Acceptance Criteria - Has the work area been set out as per the drawings?
1b5471f2-dfe4-55e3-8016-454f9e3c4042 | button | Acceptance | Yes,No,N/A
3d2afec8-e542-5c31-9fea-56ee0cca2ad6 | note | Key - S
8fea5ff9-dffe-5e50-9f62-4bcbdbedaf1f | note | UGL Key - S
| checkpoint | 1.4 - Establishment of stockpile sites
3beaacff-396e-5222-a76e-a8a86fa8f93c | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.1]
097571b0-da21-56ff-9638-bc9b49aaca36 | note | Acceptance Criteria - Approval to use any stockpile sites not shown on drawings.
ffd20870-488d-5961-9fb9-58d94c6d757e | note | Notice: 3 working days before stockpiling
d2459f7b-e33a-5d02-b799-8dd49de807d2 | note | HOLD POINT
db3ad070-b24a-5217-a02b-4a117238bb20 | button | Acceptance | Yes,No,N/A
2721a10a-cfa4-5c37-b169-e68cfe422612 | note | Key - H
3158d9b9-bedd-5f94-a748-fb9933bb0210 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.5 - Excavation material classification
6b50a60f-6f45-5750-87e8-045346b4e827 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.7]
b2f6099a-5fd5-5354-bce4-b114a3ccba64 | note | Acceptance Criteria - Ensure that excavated material is separated as follows:
b87a2944-89d2-5921-81c9-5ed54b5cadeb | tickbox | Topsoil
672e6764-5101-5b54-b4e4-d8d0fccc39a8 | tickbox | Embankment Material
a37e4463-265b-560e-9624-3656c6c8351b | tickbox | Unsuitable Material
cd4b3d1f-59fd-5e54-92e0-887dcce16f99 | button | Acceptance | Yes,No,N/A
e8fbc2fe-8dff-53fd-b44c-0397006406d9 | note | Key - S
43f89437-bea7-5c97-93dc-766d64367869 | note | UGL Key - S
| checkpoint | 1.6 - Fill Material Conformance
5515c456-7574-5dce-b488-ab2fa9dadd75 | note | Ref docs - Spec. 1112 Earthworks (Roadways)
9d8ec027-aaa8-5188-a32f-bbd8c439d5e4 | note | Acceptance Criteria - Fill Material to be free of roots, clay, topsoil, steel and organic material. Use primarily Site-won cuttings and supplement with imported material if necessary.
c83d6b3c-11d7-542e-93fb-a9c37031fa89 | note | CBR to be > 3%
8127a4d5-6555-5f17-9b12-c66ea492024e | button | Acceptance | Yes,No,N/A
44f7166c-cfd3-5226-a3aa-b764723a5b44 | note | Key - S
bf80df97-a76e-5f80-9f45-1f655f340e8e | note | UGL Key - S
0fb8b48f-aa51-533a-8629-f133d46bf719 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Material Test Reports
| checkpoint | 1.7 - Water management
37c9bc8c-9c9f-5d43-bc04-17afa5dc432f | note | Ref docs - Spec. 1102 Control of erosion and sedimentation [Cl 3.7]
b99a4caf-338b-5286-a552-b231835a9a2c | note | Acceptance Criteria - Where necessary, have batters been rounded and catch drains constructed to allow for potential surface runoff during the course of excavation?
741f393d-d7ae-5b2d-9375-d9eb9970fb2b | button | Acceptance | Yes,No,N/A
fa0ff31a-18eb-579a-bc83-b655b374743c | note | Key - S
e066d9f2-1ca4-577d-bbac-f017d0365d71 | note | UGL Key - S
| checkpoint-no-value | Is the area in cut / fill / both?
fc3b7499-5312-52a5-bcef-421e48500f56 | note | If in cut proceed to step 2.0 and strike out section 3.0.
1268a80e-20c8-5967-9630-9e822a0538f9 | note | If in fill please strike out section 2.0 and proceed to section 3.0
4c788961-9e69-59fa-9f41-3bb2cd645505 | note | If in both proceed to step 2.0 as well as section 3.0
| section | 2.0 Bulk earthworks – cut
| checkpoint | 2.1 - Subgrade preparation
f461c88b-7d7a-5420-a4fc-cf2847dd77ab | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.1, 4.3]
4f66a7df-f6a5-52fe-9161-ff4016c7da19 | note | Acceptance Criteria - Has the cut surface been trimmed to an even surface free from lose material and within tolerance of +/- 50mm from design floor level?
61a28f2f-c44a-548c-a55a-8e3c71bac737 | button | Acceptance | Yes,No,N/A
2aaefec1-6b57-55c6-8b92-0962653e7cfc | note | Key - S
03d4d489-5209-5b95-ba80-cf7ffb6fde1a | note | UGL Key - S
| checkpoint | 2.2 - Unsuitable material removal
95a391d7-f824-5ac8-a410-22ae62246f9c | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.6]
b8691008-62f5-5a89-94c8-24198d9b9d2d | note | Acceptance Criteria - Any Unsuitable material to be removed as directed by the superintendent
48987e77-0e37-537c-b5c1-074177fcd6f4 | note | Notice: Progressive
2a9ccd3f-adb4-5c99-93da-5d7dff8928a4 | note | WITNESS POINT
4fc7b399-e3b8-5ea0-ba25-56c40098f560 | button | Acceptance | Yes,No,N/A
0e48c763-37ff-5c42-a254-6a358ac48ab8 | note | Key - W
b70e0bed-744c-59fd-878a-4750143238f9 | note | UGL Key - W
| checkpoint | 2.3 - Unsuitable material floor inspection
79f22ddb-7cab-560f-ae79-2326e9dabb19 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.6]
7d1f0f90-60ff-58ab-9af0-ce05b999e72b | note | Acceptance Criteria - Floor of excavation to be inspected to determine sufficient depth of unsuitable material has been removed
84974ed1-bf3b-59d2-8ca9-cef3bf316b32 | note | Notice: Prior to Backfilling
9f3fb20f-c5c1-5f67-b07b-f8ce9a93c543 | note | HOLD POINT
2adf6d8c-f44d-5522-91a2-0a84a1eed9fa | button | Acceptance | Yes,No,N/A
17199164-84c4-5714-b06d-1ddce625ef8f | note | Key - H
e2c96273-c5d8-5b90-b909-3229c115db69 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.4 - CBR Testing
1d0f57bf-41c6-5435-9b71-8ab0f3341e45 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3]
df9caefa-248d-5ac3-b0c7-0f3a819a981a | note | Acceptance Criteria - Prior to ripping, test the CBR of the material in the cut floor to ensure it is > 3%
ba7a1352-70cd-5fff-8e3f-e41bdbb53241 | button | Acceptance | Yes,No,N/A
c16d7e1e-4450-57a3-9f79-3bc745e9208c | note | Key - S
b41245d3-dc88-5204-baf3-3295c02b5890 | note | UGL Key - S
4f9d0af2-5039-577a-858b-118b11e172eb | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 2.5 - Ripping Cut Floor (Not required if foundation is in stabilised remediation pad)
283eb690-01a7-5633-bcbd-24ee5ca39cea | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3]
4cf9467b-3059-56f0-9244-6d3cf45eee61 | note | Acceptance Criteria - Has the floor of cuttings been adequately ripped to a min. depth of 200mm?
861103f1-b231-567c-b570-29c28992ea1d | note | ○ The max. dimension for any particles in the ripped or loosened zone not to exceed 150mm.
4e24dc71-ec40-5c5f-8e44-1794910f0168 | note | ○ Ripped material to be presented for inspection.
3776d547-939f-5ea3-b026-f283c87675b9 | note | Notice: Before recompacting commences
9285daa6-9fd6-5fdd-88aa-ef26f0ae43c0 | note | HOLD POINT
41d23ae7-bec7-513a-a2ed-66ff60086fde | button | Acceptance | Yes,No,N/A
5e03a6ae-7c3d-50be-a58f-e95b0866972d | note | Key - H
5e8d1ed2-20c7-5dc5-8a6d-52459ac9fdbc | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.6 - Re-Compaction
fe430ead-0c05-5ec6-ac10-f6dbcd6c48cf | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.13]
183d4e54-adaa-52eb-aae7-57293678a4e4 | note | Acceptance Criteria - Re-compact the ripped floor to achieving a relative compaction of 97%
c9062d73-a958-5481-83ed-280c2a6cb2d8 | note | ○ If unsuitable replacement has occurred, compact the replacement layers to 92% and the design cutting floor to 97%
930fefed-3947-527b-85df-fc27f0086125 | note | Notice: Prior to placing subsequent layers
b3c0dfae-6e63-516a-ba33-fad41d92691d | note | HOLD POINT
8eb39b96-b627-5d88-971e-87456836f4a1 | button | Acceptance | Yes,No,N/A
323561c5-007e-5ce9-83cc-e9cb4bec9016 | note | Key - H
e7c19d9a-3849-511a-b7c8-06dd5c53363d | note | UGL Key - H
92ad1e3d-64b9-5d08-a638-c0c589be208b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.7 - Proof Roll – Subgrade (Not required if foundation is in stabilised remediation pad)
bd8b44d9-246d-52e9-8252-6661fafb7032 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
4b2d77b8-5770-577e-aee1-b9df8a4a029a | note | Acceptance Criteria - Does the layer withstand proof rolling without visible deformation or springing?
b7f687c2-49d5-515e-a1a9-103b71e983bc | note | Notice: 2 working days before next activity
aa1e615d-83d8-5bad-b2e7-53fdad3601aa | note | HOLD POINT
6338445f-b54b-5eb0-aff5-ccacec1a47d3 | button | Acceptance | Yes,No,N/A
bff96121-fd83-5b72-9198-3ce438f267d0 | note | Key - H
77f8526d-5dae-57b6-b6a6-add97a841e20 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 3.0 Bulk earthworks - fill
| checkpoint | 3.1 - Foundation Preparation (Not required if foundation is in stabilised remediation pad)
fb74d701-d333-5454-98ea-426e9dbef07f | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.7]
7f4b06ef-abe2-59bb-ad41-9730a4af6b7a | note | Acceptance Criteria - Grade and level the area, adjust the moisture content and compact the top 200mm to 97% relative compaction
db862a33-326e-5548-ae65-fe4bfe9bb8f3 | button | Acceptance | Yes,No,N/A
6afbfc88-44be-5c86-8fea-2727f858ef59 | note | Key - S
ad335d83-227f-59c0-b81e-e65caa8d57ad | note | UGL Key - S
22adc40a-b218-532a-851e-58bbaba10fb6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.2 - Foundation Inspection & Unsuitable Removal
ac808c7f-e80c-5731-8371-568452891142 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.6, 4.7]
90eef1d0-7385-5db2-85d7-2209e47385a2 | note | Acceptance Criteria - Embankment foundation to be inspected by the superintendent. Any Unsuitable material to be removed as directed.
596cf531-372e-542e-9a5d-4c778e8f379c | note | Notice: 1 working day before next activity
ed6a07b6-432e-5466-86f5-b9067b2e2be3 | note | HOLD POINT
d4ea34d2-de1b-5aff-a44f-3df24328de97 | button | Acceptance | Yes,No,N/A
40feab0d-c22d-5930-8390-a1c336bae061 | note | Key - H
cf6f0333-b8f3-525f-acbb-e4b7edfe400d | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Unsuitable Material Floor Inspection
0aa52c79-aa6f-56fd-9f3e-d6e759b5176c | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.6, 4.7]
43686d00-e0f3-5735-8a6a-e19c5ea62575 | note | Acceptance Criteria - Floor of excavation to be inspected to determine sufficient depth of unsuitable material has been removed
25f9e4af-7e9a-5319-aa2c-d16590c92927 | note | Notice: Prior to Backfilling
0269b13d-15bf-5bcd-81e2-4a10f847a47f | note | HOLD POINT
75370c17-a183-507a-a818-5864379caf0f | button | Acceptance | Yes,No,N/A
961afba1-98cb-5532-8db0-79dae7e688f4 | note | Key - H
85ed0ff9-559d-54e5-aa12-abd452227be7 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Proof Roll – Subgrade (Not required if foundation is in stabilised remediation pad)
13ff1fc6-0de0-5688-96f7-c288fdc0da1c | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
366f0571-43d8-5beb-a382-f8db6b6bd3ba | note | Acceptance Criteria - Does the layer withstand proof rolling without visible deformation or springing?
29893099-104c-5d42-91bd-f77ecd26cb5f | note | Notice: 2 working days before next activity
55ad7eb2-e006-5417-bb9e-aa151f1bddd0 | note | HOLD POINT
b6720e68-973b-5324-aa2b-1e7670760684 | button | Acceptance | Yes,No,N/A
a9a26522-08dd-55e7-8edf-126406317156 | note | Key - H
54adf87d-d559-597b-86bd-32f1145a53d5 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Fill Placement
0f8c760f-b526-5ba1-9313-697cadc9cfe6 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.8, 4.10]
a0bf6be6-e2b3-5497-b43b-bc30a0a81f3d | note | Acceptance Criteria - Has fill been placed in maximum 200mm compacted layer thickness?
93ce3dab-17a4-5502-b387-ba31c6d2d5b8 | note | (Approval required to increase compacted later thickness to 300mm)
c618a1c1-7113-5e42-baf3-0b2771b9b230 | note | Note: Maximum fill layer thickness adjacent to structures 150mm)
f8af81f7-bd30-5bb3-b992-5539f28fe4c9 | button | Acceptance | Yes,No,N/A
8d766eda-d4e0-5c81-9975-f0d61d0e5592 | note | Key - S
ad886a6a-8226-5c13-a9a5-559304799182 | note | UGL Key - S
a3e3576f-27c7-583f-8baf-2e5866ee3d61 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery dockets (if imported)
| checkpoint | 3.6 - Moisture Content
979ac656-16ac-59a9-8f53-a6181c78c3cd | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
5d2d97e7-3eb6-59f0-9ec9-26e62503f625 | note | Acceptance Criteria - Is the moisture content within the range of 60% to 90% of optimum moisture content for all fill layers
c01c5f92-8549-5799-9e30-d455adb22434 | button | Acceptance | Yes,No,N/A
325aaa53-02a0-5be9-bc2b-bd738a036ed7 | note | Key - S
e3c2dfe4-76c2-5cda-970e-08a3eb9fdce0 | note | UGL Key - S
9ac9edec-6dd6-5e01-a047-2633aa78a381 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.7 - Compaction (General)
4e03acbc-6071-5187-8681-d32ae69b8dd6 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1], Spec. 0161 Quality (Construction) [Cl 7.2]
1b2b4ad5-45eb-5def-a365-6f0667c2b820 | note | Acceptance Criteria - Compact any material used for unsuitable replacement, general fill (>1.5m deep), verges and medians to a relative compaction > 92%
1c052d3f-b9de-524c-a1a6-5a2b51b6d9e5 | button | Acceptance | Yes,No,N/A
c745cbce-8bbb-5303-a801-0cd6d612d01a | note | Key - S
8a92805d-b290-5781-8ee7-9b5f4c82054d | note | UGL Key - S
6b3f53e8-18c0-5ec6-9ad7-ba9ec36d505b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.8 - Compaction (Selected Material Zone)
a4a737d3-0d8d-5e20-8c03-dcf308762421 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1], Spec. 0161 Quality (Construction) [Cl 7.2]
3394df36-966b-5805-b085-5ace6661f960 | note | Acceptance Criteria - Compact any material used for shallow embankments, Select Fill or behind kerbs to a relative compaction > 97%
16d38a1a-f6d0-563b-96d4-76744a412b3b | button | Acceptance | Yes,No,N/A
07fac88d-0f4f-5540-9f39-ca96018be5d2 | note | Key - S
72c377f3-1238-56b1-ace8-0db945627cee | note | UGL Key - S
e7e75c42-9ef6-5bd8-bde9-f953a34353db | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.9 - Compaction (Fill adjacent to structures)
57714ef7-d9b2-5c1a-a534-2608ca273919 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.10, 4.13]
2557e20a-fbfd-5b53-b6d6-10b1654217be | note | Acceptance Criteria - Compact all material adjacent to structures to achieve a relative compaction of 92% (up to 1.5m from top of pavement) or 97% (within 1.5m of top of pavement)?
89f10f07-e954-5aba-a2c2-051f779ce024 | button | Acceptance | Yes,No,N/A
7a8032b6-4499-54e6-bb73-05b09e008da3 | note | Key - S
028820a7-5089-5242-bf24-c127ca0398dc | note | UGL Key - S
b295a7fb-a103-5bcf-9fe6-05abe0bab800 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.10 - Material Conformance (Fill adjacent to structures)
f7bfc18d-5aac-5bc1-82fd-6944495568fb | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.10, 4.13]
43c39af6-f5df-589a-bf0c-1d7b3d2d5ae2 | note | Acceptance Criteria - Backfill material granular and not exceeding 50mm particle size
a80f2c71-ea63-586c-898e-d19cbdbc1636 | note | ○ Plasticity index in between 2 & 12
16e89a58-4df0-5ea4-aed4-aeb6ec3278eb | button | Acceptance | Yes,No,N/A
9921222c-267c-5548-876f-14bd4dc403ba | note | Key - S
8989c222-6093-5db1-bba2-c7a0949cb93e | note | UGL Key - S
045403db-fc2c-5947-845f-96fe87d2fa2c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
| checkpoint | 3.11 - Proof Roll / Select Material Zone Inspection
f7efddd8-f163-52b0-8695-bdf7543398f3 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13]
8f60cc89-8d14-5ffd-a205-a2d64f54386d | note | Acceptance Criteria - After trimming & compaction, present the top layer of SMZ for inspection.
ba2ac883-1b7d-5c12-9f36-821645345d8c | note | ○ Does the layer withstand proof rolling without visible deformation or springing?
51915861-4640-50c6-bd5e-ab4acfbf304f | note | Notice: 2 working days before next activity
e3eaf345-e0a7-5bad-8de8-a6f8bdaac16a | note | HOLD POINT
27689cbe-885a-5fb4-9520-d77a9cededce | button | Acceptance | Yes,No,N/A
d33e7a56-581d-53c3-8ed9-8cfe51eaf099 | note | Key - H
d8e623de-77e2-506a-b416-b2ab7832a385 | note | UGL Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Bulk earthworks - other
| checkpoint | 4.1 - Batters
ac21fd95-b28d-5372-9caa-2eb3b137ad3d | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.4]
40a5098e-70a6-5d5d-99cb-c6f830c8a7b4 | note | Acceptance Criteria - Provide batter slopes as shown on the drawings. Clean the cut faces of any loose or unstable batters as the excavation proceeds
c7ead50c-f5b1-5648-a656-60dab4594f83 | button | Acceptance | Yes,No,N/A
3c164c4c-1b63-5741-8999-9fee218e5fec | note | Key - S
f8b8f131-8de8-52a1-822f-533706770888 | note | UGL Key - S
| checkpoint | 4.2 - Cut to Fill Transitions
89a4625b-a3f6-5060-aa13-6fa759ab592b | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.5]
88a0fec4-b27e-534f-a470-74843b15df2f | note | Acceptance Criteria - Excavate a terrace as per the figure in Cl 4.5 for the width of the SMZ to a depth of 900mm below the cutting floor
b28b1c6f-c70b-5332-8aa6-7e34abe46306 | note | Notice: 1 working days before excavating terrace
d24d9c08-e10f-5273-a733-098e4a8e0dff | note | HOLD POINT
404c55ec-93e1-54bf-bd48-c17bf9559867 | button | Acceptance | Yes,No,N/A
d173e752-03e8-57a7-97a9-6775eb21b810 | note | Key - W
12171cfb-96d4-5c76-bcb0-73df88de9b1e | note | UGL Key - W
| section | 5.0 Conformance check
| checkpoint | 5.1 - Width and alignment
694ba50e-899a-5bbc-a9e9-02fd88432907 | note | Ref docs - Drawings
6c42acac-64dc-58bb-b2ca-53432e984c31 | note | Acceptance Criteria - Has the pavement been constructed at the correct width and alignment as detailed in the construction drawings?
6fdfc552-bff0-5894-9ac7-b3879b4d8b80 | button | Acceptance | Yes,No,N/A
be85e040-cc15-57f9-8db9-01a4f09ce257 | note | Key - S
41291405-f7e3-5e59-8546-a5decdb1c7b9 | note | UGL Key - S
| checkpoint | 5.2 - Level Conformance – Top of Embankments
004278b3-f6fe-5d14-b5f5-f9c1d834a9e6 | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.8, 5], Drawings
3c29808b-09c8-594b-8507-b7521ae632db | note | Acceptance Criteria - Trimmed top of embankment to be within the range -40mm to +0mm from design levels
976d33fd-033e-5d84-a15f-007db5f93b74 | button | Acceptance | Yes,No,N/A
74bd0c03-dc7f-55cd-99c7-e4bef54dcb68 | note | Key - S
965bb813-9b26-5b71-bafa-e099876fd375 | note | UGL Key - S
6f6c8d7f-415d-580c-98bd-4dd06e70e575 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As built report
| checklist | INF-HSEQ CC0375-ITP-002 Drainage (Pipe Laying) & Checklist - Rev.6 | itp | INF-HSEQ CC0375-ITP-002 Drainage (Pipe Laying) & Checklist - Rev.6 |  | 5e2e0e6e-b5b5-4814-aea7-79d0188b0453
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
c0b03e59-3ade-572f-b4ac-40efecd556fa | note | Ref docs - Issued drawings / Site copy drawings
795cc7f9-f2dc-5a76-982b-2ce6c1884756 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
66464ad7-2abf-535d-b933-bc40ee9c5418 | button | Acceptance | Yes,No,N/A
3dba44fd-eba0-5979-83ae-c66f1b2bc207 | note | Key - S
9ad1c210-04a2-59ef-9fca-c471d6848b04 | note | UGL Key - S
69b9d476-6ac6-57f9-8a71-d0cf72fd57cc | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
32d9968c-e8e3-5274-8bce-e6f698354ac8 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
a95913d7-e725-5f72-93c2-96c466fb7552 | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
9466f2c9-978f-59fb-9cb4-728858ec1071 | button | Acceptance | Yes,No,N/A
6ae598eb-5c88-5a21-b52b-65b2a14d501f | note | Key - S
25a00ce7-de14-5e68-a348-bb35a508eb7a | note | UGL Key - S
2d1c0898-806b-5015-83c8-27364b4e167b | note | SHL Key - S
2655338b-fb95-57e4-bad9-0bbeee35ffe3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
143842ce-cd4f-5943-b23f-529fc75ff432 | tickbox | Lot map
| checkpoint | 1.3 - Drainage Pipe Material
1ad3d5cb-3de2-5fb2-b056-2142e42e45db | note | Ref docs - Drawings
10ab4a3e-4cfd-54a4-8981-eebc7ff1b270 | note | Acceptance Criteria - Has the correct class & type of drainage pipe been supplied and free of defects?
f5844f64-3780-569f-8da8-97dadda2a931 | button | Acceptance | Yes,No,N/A
0f849e77-ada7-55ef-9703-a8cdab50c030 | note | Key - S
3cfd7d22-98ee-5d11-a1f3-b85f03f77eef | note | UGL Key - S
cdf3f0cb-cfa7-5e35-af20-95417e709b25 | note | SHL Key - S
138cb1db-5cf6-5794-b597-76aa9c96f35d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3037230e-11a0-5c91-bcc9-6eb318cd5489 | tickbox | Material conformance certificate
| checkpoint | 1.4 - Embedment material
4939f515-60a9-54f3-83c5-13717ed7c65b | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
eff0a2ae-2390-5b57-ad44-1ea574a660b7 | note | Acceptance Criteria - Material has plasticity index less than 6.
62923b07-04b0-5186-92a4-e6da1d09f8c9 | note | – – – – – – – – – – – – – – – –
ecb2f58f-5835-596e-906a-20bb16a3a588 | note | Table 5.1 Embedment material grading
08408dde-93e1-57cf-a9e8-8fe68f2e906a | note | – – – – – – – – – – – – – – – –
4a393e40-fb1e-5692-8f56-91c625c71371 | note | Sieve size (mm) ¦¦ Weight passing (%)
c1c29013-0e6d-5d20-a6db-e621baaa6828 | note | – – – – – – – – – – – – – – – –
7ded47f0-3fda-55b3-bb95-964cb936e78b | note | 19.0 ¦¦ 100
3d00cf67-8fcb-5f6e-8f6e-fa1aaf574e23 | note | 2.36 ¦¦ 50-100
6140fc8a-8969-5c09-b290-0faa2c23d173 | note | 0.6 ¦¦ 20-90
2105ebe5-1a51-5e16-9151-4b0c7e75f2a4 | note | 0.3 ¦¦ 10-60
d7919e1e-d249-5c43-afb6-f5dcc893087b | note | 0.15 ¦¦ 0-25
ff20db25-28f0-5bb4-bd9f-a747d21a909a | note | 0.075 ¦¦ 0-10
b203d5a8-f832-50ad-8e5e-f766d81e7fde | note | (Table taken from AS/NZS 2566.2, Table 5.5)
23851731-9cac-5b44-b077-d069409993d0 | note | – – – – – – – – – – – – – – – –
165acb89-2669-5330-8ca0-af6964e2ae57 | button | Acceptance | Yes,No,N/A
fc7562d5-4d9a-5f62-8e62-b6bc99644392 | note | Key - S
6f0571ac-0dd9-50da-81e6-77b7205be27b | note | UGL Key - S
ec996d9e-7e78-588b-ab3b-9ef525aa266f | note | SHL Key - S
6b15abfe-a6ab-5e66-8404-7ee9e7cb7fc5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd939fea-b01b-5dc9-b214-6d8a62a25593 | tickbox | Delivery dockets
0ac25300-f833-5173-b31e-7537095fefac | tickbox | Test reports
| checkpoint | 1.5 - Underlying Lot Conformance
5f0642d1-a205-56bd-94f4-0c081649a51f | note | Ref docs - Underlying Lot ITP
7e4f3173-3e55-553d-b01a-664db5039a61 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
43105d82-1668-5bf8-80f0-abf2f3cf2c31 | note | ○ Refer underlying lot ITP(s)
436be88a-d038-51e1-898d-633adfa9ede9 | button | Acceptance | Yes,No,N/A
90259a46-8bd2-5da7-8e21-b3282b33965f | note | Key - S
d7cda47c-68ad-522a-974d-4d90d1b72200 | note | UGL Key - S
6bc4c028-63df-5628-99ba-7ec2666539a1 | note | SHL Key - S
| checkpoint | 1.6 - Temp. drainage during construction
a164fdb5-820b-5593-86c0-4357dfc8ef2f | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
91673264-b644-5ec8-b427-92817dfb0167 | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair
f75f2c25-2e72-58a2-b8a9-c63351a5ea18 | button | Acceptance | Yes,No,N/A
ec0ce591-a193-549a-9a4d-5e33ff4819b4 | note | Key - S
0d081c0f-844a-5d73-8c9a-c36822eac5d3 | note | UGL Key - S
5a6c995a-66c8-5e79-b7a4-a49f86c5206a | note | SHL Key - S
| checkpoint | 1.7 - Set out
7c185ffe-c14a-54e2-be09-75e6a80cccdc | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2] Drawings
7ac8f825-7419-5f69-9b6d-3a2d2fb83d6f | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
9700f6b3-774d-5af3-9ff2-b01969fe37f1 | button | Acceptance | Yes,No,N/A
81a90d5e-1506-5170-a054-5c1fe830c0bd | note | Key - S
08c8aadc-e89b-59dd-9b64-545f59ce3614 | note | UGL Key - S
84c5cd8d-283d-534e-8cb5-415462f7bfaf | note | SHL Key - S
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
d82095df-0f73-5737-8ba2-dd1cb1321ced | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
0e23f42a-4535-5200-aabb-e64a5e1ff2b4 | note | Acceptance Criteria - DICL & Flexible Pipes:
c3858a5f-5a97-56d0-bc5f-b1082e2c27f0 | note | – – – – – – – – – – – – – – – –
7b8339f9-79a7-5bbc-b0f2-851151bfeae9 | note | Table 5.2 Trench and embedment dimensions
216fb083-5320-5f6a-bc05-0ddda4fa4d9b | note | – – – – – – – – – – – – – – – –
adf2002e-8aee-5ff9-9df1-f3bf1dac4d38 | note | Extreme external ¦¦ Minimum dimensions (mm)
57028ebe-01e9-53ce-9198-446161bb975e | note | Dia (De)mm ¦¦ x : s : o : y
d0952fed-a6ba-5662-a02e-07fd5d7e7575 | note | – – – – – – – – – – – – – – – –
da3677dd-89ad-5469-a9c0-a4631d502c0b | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
1956efa6-a89a-598e-99bb-18dc49c61695 | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
8cab0ff9-8638-5fea-8fa8-5ea528e453f3 | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
57a501a9-9593-5956-b1be-01062a14c4dc | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
04b752b6-f811-5f93-aec8-4bb065a72f06 | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
08c9b9ae-d0c0-57ea-86b2-297e27a76e2c | note | – – – – – – – – – – – – – – – –
f2788d90-98a1-5197-b101-5a1d990cef58 | button | Acceptance | Yes,No,N/A
1b4f5e96-9f5b-5869-9c78-953e817c56a7 | note | Key - S
f1c55896-b7c6-5ebe-839b-6ec2076f3ae9 | note | UGL Key - S
32366fcf-e84e-5ca1-817b-373ab4979420 | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable Material
3a0d0be3-5b66-58b3-a142-f15ade574468 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
92d969f2-de12-56c5-89c0-e69fa6b3909a | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
5f772ed4-e1e7-563c-a2ad-3b9074d9a46e | note | Notice: Prior to Placing Bedding
c75c4a4b-075f-599f-bce0-e3bd93b23fa7 | note | HOLD POINT
c5c276f3-f56f-55b3-9907-7dfa47f047b0 | button | Acceptance | Yes,No,N/A
771cd60f-b89c-5707-a3a1-f262a4eaef47 | note | Key - H
0cf1c771-3575-5a11-ac02-d3f797970361 | note | UGL Key - H
f77068ea-71d9-5677-9139-ebd076fea80d | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction – Foundation
e0665098-64a9-5c97-9f8a-683ad85544a6 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
ce70c461-1ed1-5be6-a34c-3ab1ce58db65 | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
d49a5b63-84a2-5bb2-a535-5cb49aa5ef68 | button | Acceptance | Yes,No,N/A
76ef7931-c865-53ff-a5ba-249d6d313556 | note | Key - S
01c8a8e8-ed9f-59f8-af8c-ab3fb1a19832 | note | UGL Key - S
05ed141a-701d-5ffa-a931-1dfd18341747 | note | SHL Key - S
64c9e87b-9901-585d-afe3-dfbb972e62a3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
611d9d96-afc3-52ce-8673-cfe7865e740b | tickbox | Test reports
| checkpoint | 2.4 - Compaction – Embedment material
c1bf9871-f12d-5d43-9c37-623887ea8000 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
46bc4fbb-a440-5064-b8bd-f93bdf3ec582 | note | Acceptance Criteria - DICL and Plastic Pipe:
ce9c7172-709a-5a8c-ae33-74cd654b9d98 | note | Bedding:
83e9f72f-49b1-5a31-b516-6f2bc1de6446 | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
927e7f7f-9b9f-5466-9fe8-055933633bff | button | Acceptance | Yes,No,N/A
d8546833-6430-55c0-9621-d5133f2967d7 | note | Key - S
5f2f26ef-32a4-56f6-ae66-f3f9e8976df1 | note | UGL Key - S
20116a2c-ab80-5e06-96a2-9138532da621 | note | SHL Key - S
eded2e61-628a-5c4f-84f0-32f8d44ec404 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
377cdbd3-e1fc-51b4-af8b-76a613cbd3d9 | tickbox | Test reports
| checkpoint | 2.5 - Pipe Laying
fdee4d95-7cdd-5993-b5c4-a7cbb6abfaed | note | Ref docs - Drawings, Manufacturer Specifications
6e62ad88-dce1-57a2-a28c-1e6846c17520 | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
122fb2bb-d650-587d-a2ef-d82b33de74b0 | tickbox | Stormpro
dac8923d-d7d9-5161-a853-438a700a139d | tickbox | GRP
6bb43f92-9a7d-5eb7-88bf-b2f3330bae7c | tickbox | PVC
363ca5cc-8e45-5a3c-adc9-9dc854ba903b | note | HOLD POINT
4f4e8670-537d-5f0a-bcde-b7397dd1bde9 | button | Acceptance | Yes,No,N/A
a065e0d6-e8ad-5145-9d73-cbb9fec24c2e | note | Key - H
cb29232c-d917-58d5-965e-dca76086a3c3 | note | UGL Key - W
369d36f2-cce4-5725-ba59-7e71bd36e3ff | note | SHL Key - W
| checkpoint | 2.6 - Steel reinforcement
b11ad209-f01c-5a3b-90df-27fec2c034f0 | note | Ref docs - Drawings
6db5a4af-b1aa-5c9b-b268-4603d9dbbe82 | note | Acceptance Criteria - Reinforcement installed as per drawings.
da12caef-b5e3-5566-bcc7-4014aae463ae | note | ○ Concrete pre-pour inspection complete.
563ff45f-3397-57a3-8858-d2f29bce485a | note | HOLD POINT
9a33fdbf-14db-5985-9135-cea1bf23e9dc | button | Acceptance | Yes,No,N/A
524e01c0-bb4e-58f8-8150-63a68e2ca42f | note | Key - H
7b05f702-c6b8-57e3-9c90-3fe2e77c6ee5 | note | UGL Key - H
1d936174-ac4d-5a0a-aa77-3a60953cbabd | note | SHL Key - H
c751101d-e711-5412-a650-55d3ca11dcaf | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
64d54f43-89e4-5e75-a1d5-e3efbc8eeaac | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.7 - Concrete supply and placement
2944bf2c-a7dc-5a07-841c-c3cc5ba6cb70 | note | Ref docs - Drawings
9cef04ca-c3e5-5872-ac98-464bcd0ba8f4 | note | Acceptance Criteria - Check concrete docket to ensure strength is as specified on the drawings.
4c78f463-78aa-55d7-82a9-6e2139f4efa4 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated
75f029b0-e6fa-5c17-a427-65129454569a | note | ○ Ensure pipe is adequately supported to prevent sinking or flotation. A minimum of 300mm encasement is achieved around all sides.
9012d024-fe6e-5662-a839-f2203ffeae4a | button | Acceptance | Yes,No,N/A
ed8c6df6-761d-54af-8138-7017f9ef2beb | note | Key - S
63ec70f9-5318-56c1-914a-1fda2b9c92b3 | note | UGL Key - S
ea9cd216-fe79-5fb3-a1bb-ce25178479fd | note | SHL Key - S
59959fee-249c-5956-acc1-820b1cf3cf09 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c09035d5-fa41-5a90-bff0-bedd579ea0b0 | tickbox | Delivery dockets
| checkpoint | 2.8 - Compressive strength
f3b7c4ba-7710-5b08-ac17-5888181f13e6 | note | Ref docs - Drawings
2ba20c5e-427e-539d-bff6-b138ec60e9dc | note | Acceptance Criteria - Average compressive strength at 28 days meets the minimum requirement specified on the drawings.
e6c093ef-b636-5e77-92dc-f2992207fef9 | button | Acceptance | Yes,No,N/A
987c48d9-0008-57ad-8652-edd926a893ee | note | Key - S
c3dc39cc-8a69-5f99-a222-327347f973fc | note | UGL Key - S
43f5cf5c-3433-520b-a5fe-76c696013fdf | note | SHL Key - S
ecf770e4-b53a-5b87-a886-7802e550e768 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c539b126-9d4f-5409-a0e4-df0ddc4eea1c | tickbox | Test reports
| section | 3.0 Filling and Compaction
| checkpoint | 3.1 - Compaction – Embedment material
ebf90d80-6903-5695-a2c3-8a30dd9fa6cf | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
9bbdf193-8cde-5291-b4da-99956af7c94a | note | Acceptance Criteria - DICL and Plastic Pipe:
91ed0797-01f0-5909-bc9b-e34db24f331a | note | Side and Overlay:
e7aeeb2b-d055-51e0-80aa-884c620e01c7 | note | ○ Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
17b0995b-0ee6-5676-b9c0-fcdcf6057a39 | note | – – – – – – – – – – – – – – – –
2b257259-e1d5-5691-8c10-e708fb1e7e5a | note | Table 5.3 Minimum relative compaction
79397e50-2f64-5a91-b0a2-3813397cc084 | note | – – – – – – – – – – – – – – – –
5f147c21-4df0-5f27-b27a-e99c00dff167 | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
33bc1fc3-2258-5d36-9631-bf32aa2b4fd6 | note | – – – – – – – – – – – – – – – –
541d52f1-330f-518e-b253-4bbccddb304a | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
66a52626-edf3-524f-8126-74a81516b0e3 | note | – – – – – – – – – – – – – – – –
d009c06d-0371-5860-b569-644ae2694342 | note | Layers not to exceed 150mm compacted thickness.
1decd1dd-390f-597c-962c-c72a548fa306 | button | Acceptance | Yes,No,N/A
8be99407-8a18-5136-b8d9-c90de11821f0 | note | Key - S
1f2b0f13-75ef-5e0f-bf0d-e546a39e2bd7 | note | UGL Key - S
5ebe63db-31e9-5176-ab30-c582dcda7289 | note | SHL Key - S
74c88909-41b4-550e-bff1-0d8ab4afc536 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
60db9358-c8db-5aa3-b6e3-0887d3db9793 | tickbox | Test reports
| checkpoint | 3.2 - Compaction – General Fill
a2233e6d-16ad-5760-a197-b62ef4622020 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
b8394a5e-d778-558d-96c4-307996ba3c1e | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
acfad297-d893-581c-ab23-1917126ccb37 | note | ○ Minimum relative compaction to be 92%
3ad4eb05-d210-57f5-bae5-1491a9eda897 | button | Acceptance | Yes,No,N/A
3e4b0238-dcdb-5faf-b2be-0d8b428db2f1 | note | Key - S
76d69608-f443-5766-b129-2973970c47e0 | note | UGL Key - S
2816ce6e-e71a-5af0-827d-833042096627 | note | SHL Key - S
87cbb96f-a388-5bac-ad91-53db8e77f445 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
82c47731-23e5-53c2-9cc3-8762934a54eb | tickbox | Test reports
| checkpoint | 3.3 - Compaction – Select Fill
75cbc901-74ba-5953-8095-5dce76b15123 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
3b839a17-e66c-59cd-9400-c29d6daf3e97 | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
102549d3-4e40-56fa-a4fe-85f509e08d7d | note | ○ Minimum relative compaction to be 97%
3bb2c9fc-9026-5458-9b11-3f47f6a8f7ae | note | ○ Layers not to exceed 150mm compacted thickness.
cab7c735-738e-546f-abbd-c1aa2e21d6f1 | button | Acceptance | Yes,No,N/A
a453d585-01b5-54ba-b133-0c42b54ff0b1 | note | Key - S
dbb646f1-9bb8-5dcc-b88c-6e12c8063e4f | note | UGL Key - S
e5633a44-e8e8-5a41-847e-ee887dbbad25 | note | SHL Key - S
6661ddd1-2feb-5df2-8b80-449028b222da | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
70cee02c-2549-5bee-8fe9-2c4392310356 | tickbox | Test reports
| checkpoint | 3.4 - Moisture Content
c3064a2f-924f-557c-ba5c-5c31352b7c64 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
7e4b2a87-51a7-5acf-ad09-685695117853 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
27659e2b-28c4-5cf3-963e-783e990a4b2b | button | Acceptance | Yes,No,N/A
ab7ddd76-6ace-5a13-932d-66ce5d15b70a | note | Key - S
fc2b5e11-40db-5992-956f-e56de5d19909 | note | UGL Key - S
98457612-9b9e-5157-8a1c-9bc0af3f91cb | note | SHL Key - S
81646af7-0d3c-5143-8d7e-470cf9653c21 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
75acbd05-b79a-5b71-ab98-8bbd5f28b2c6 | tickbox | Test reports
| section | 4.0 Conformance check
| checkpoint | 4.1 - Survey Report
1fb1c047-a355-5afa-8103-3d64d8dd29db | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
be8d28a1-ba43-5074-a0ca-edd25b5e34f2 | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all pipes are within construction tolerances.
9d42a401-3fd0-590e-a8c3-00e82c3425e0 | note | Plan: +/- 200mm
f7934e9d-f72f-5ad5-95ce-b974fe729c14 | note | Level: +/- 20mm
32498b40-928e-5dac-9f6b-7237ec562fe3 | note | HOLD POINT
96292278-3c61-5d65-80c4-e26987ae07f9 | button | Acceptance | Yes,No,N/A
a8b64548-e1d7-5cab-b9b5-54f095ab8863 | note | Key - H
3cdc08db-5ab9-5233-9ad8-bfe22c06e1ea | note | UGL Key - H
089ba4df-c3f9-573d-b134-5533b3d94c03 | note | SHL Key - H
95a6f357-d86c-5c9c-9d80-d9748cb51622 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
21221b8a-db7d-5f10-bbc6-023067e3b560 | tickbox | Survey report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
8bf5e939-d36e-5af8-996a-3cec789129c2 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
6e8347ee-1342-5191-be20-5339b7e0bf0a | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
0722076d-cbe4-5909-b62d-c1a7010ed834 | note | HOLD POINT
78c117eb-7d33-552c-aea2-60106fe48ab5 | button | Acceptance | Yes,No,N/A
eb9a2844-2c0e-58c1-bc48-c3b5e9d7c13b | note | Key - H
3817d5f4-b816-575a-ba4d-7396476c92bb | note | UGL Key - H
f6220109-82c9-5d47-8b28-79a439492982 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-003 Drainage (Pre-cast Structures) & Checklist - Rev.7 | itp | INF-HSEQ CC0375-ITP-003 Drainage (Pre-cast Structures) & Checklist - Rev.7 |  | 6b5caf84-daab-4d89-86de-0f928db5685b
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
09b8a9c7-bd5e-5a97-bfd6-c2f3ebc6f163 | note | Ref docs - Issued drawings / Site copy drawings
e095affc-9552-5418-9199-87ec6a996f48 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
037aa174-7300-5b22-801b-55e5895c9cc3 | button | Acceptance | Yes,No,N/A
e299607e-8bd8-5273-896a-dec71c5c91c3 | note | Key - S
d5b70182-3cb3-540e-8555-aa2f6bf6359e | note | UGL Key - S
1850ecf0-66eb-56b5-8b7f-3b7bc2203e26 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
a285d34c-134b-5ccd-8970-8b2770602d38 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
e069c0f6-6173-5a19-bb7c-38367103b5ba | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
b6039fce-c00f-59ad-b922-2545d53cdc3c | button | Acceptance | Yes,No,N/A
c0505d40-bb65-5234-b2af-1d70e7b8d78a | note | Key - S
269ad51f-4500-5636-aa41-fc143c84f4be | note | UGL Key - S
4c5e2cb2-4e4f-547b-8ac8-2ba6ef319df0 | note | SHL Key - S
f860cc80-46d4-5520-8da2-d71e82eacf80 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7b142569-fe03-5b59-b6a1-c4ab1820e0d2 | tickbox | Lot map
| checkpoint | 1.3 - Precast Pit Approval
c9791dbe-e21a-5eb2-848b-57396446a61a | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 2.2]
89b05457-47b4-5fe1-a772-b61e6430ab9e | note | Acceptance Criteria - Submit Drawings and Installation Procedures for Precast Pits to the Superintendent for Review prior to delivery of the first pit to site
ac3a94d8-9551-5e6d-9018-db446bc993fc | note | HOLD POINT
a3cf02e3-ac64-5ff4-a351-0eb49a1a0ed6 | button | Acceptance | Yes,No,N/A
c4455a31-4d34-5893-8ce4-46eb6a65b701 | note | Key - H
363ce85b-2a18-5bf2-8db8-25e3bc7a2baa | note | UGL Key - H
96589c07-c7c4-5d7e-a79a-eff2f9bad370 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.4 - Precast Supply
1671607d-7acc-5c4f-959c-1fe25c8ef6dd | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 2.2]
6732c613-9ff2-59a4-a894-9aef40f49308 | note | Acceptance Criteria - Does the supplied pit, slab, culvert or headwall meet all requirements of the specification and the drawings
ef24aecc-7b79-55f8-84d2-e861f238b388 | button | Acceptance | Yes,No,N/A
1275aa33-f83e-54e6-b473-f7fdc8325d3d | note | Key - S
7073a6aa-b420-5c1e-9f07-2ace8de23f72 | note | UGL Key - S
1a75c5af-8257-5ec4-ae2e-5fec7c9775f1 | note | SHL Key - S
ee923638-01af-571d-8e77-9279665d9b5e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e7be3b7d-27b6-5be4-a756-e3455818aa0c | tickbox | Material conformance certificates
| checkpoint | 1.5 - Underlying Lot Conformance
58fa1030-3ad2-53f0-b29f-78e5807a412f | note | Ref docs - Underlying Lot ITP
00459470-c080-5a22-be9e-7b0fb43b0070 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
e42760e3-4b21-525f-8dc7-81d786bd5ab5 | note | ○ Refer underlying lot ITP(s)
daaed654-31dd-5d13-89a1-6b4119afb8a3 | button | Acceptance | Yes,No,N/A
7c5c4720-e88a-5885-ab54-cbb0f673023e | note | Key - S
fe8a4177-e5c5-5603-bc4f-f820a05ee797 | note | UGL Key - S
ede3dfbf-7a8b-5fa0-a343-dbdd8a678702 | note | SHL Key - S
| checkpoint | 1.6 - Set out
d969608d-ab56-5034-b7ee-01712f96d405 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2]
6ccb9e00-e6df-5aa4-b759-6df6df22c399 | note | Acceptance Criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
04487a72-976d-5230-a869-307f6007d8b0 | button | Acceptance | Yes,No,N/A
68fbfb69-1a88-58f5-b137-9a14021a5f65 | note | Key - S
3e6ea099-8048-51de-be2b-0ec55c94db35 | note | UGL Key - S
f3d93ab3-3ff9-5e56-9852-14062ea64e28 | note | SHL Key - S
| section | 2.0 Construction
| checkpoint | 2.1 - Unsuitable Material
783021d4-fb7a-57de-bbe5-98dbb998835d | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
cb4ecffa-57bb-50ae-b2f5-cd99315a1a5d | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
57dccf4c-ca4a-5d29-8150-0d47d35a357c | note | Notice: Prior to Placing Bedding
dcab14e6-3e6a-5a8c-ab4e-97558018df20 | note | HOLD POINT
89236ff0-e6c3-5df9-9c02-b56a5aee3f36 | button | Acceptance | Yes,No,N/A
0fca9dfc-8873-5a5f-9913-b23d33ee86af | note | Key - H
7277d5ac-ddb5-5da3-a0a3-885b5751c0da | note | UGL Key - H
686d5a43-213b-5887-979b-151973877923 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Compaction - Foundation
001b4bdc-72d3-5121-b4cf-11eb07bc1f03 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
14bb71e1-d171-5955-a941-b4cbee565c4c | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
eda071c6-a128-5065-abad-f35ef27f933a | button | Acceptance | Yes,No,N/A
18fc7d56-4e28-5fd0-843e-8495ca2e4213 | note | Key - S
813c429f-ce54-576e-abd8-67ab9e905764 | note | UGL Key - S
a0880baf-f8ba-5cee-bdff-c0cb526ab5b1 | note | SHL Key - S
ac40d5c2-0512-5381-9f0f-9730b03e2e14 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
31b07e80-ace1-5ba8-8855-dc3515202dca | tickbox | Test reports
| checkpoint | 2.3 - Compaction - Bedding
32810833-5c09-5400-9677-f2b9e2c25fa1 | note | Ref docs - Spec. 1353 Stormwater Box Culverts [Cl 3.4], Spec. 1351 Stormwater Drainage [Cl 2.5]
5443e9bd-7cff-5489-b303-5549cc9de6f8 | note | Acceptance Criteria - Precast Structures to be installed on bed of Select Fill with a minimum thickness of 150mm
beb2b625-2aaa-5865-8295-1ad776ef51b6 | note | ○ Bedding layer to be compacted to a relative compaction of 95%
01546156-b39b-5345-bfac-ea904146ae97 | button | Acceptance | Yes,No,N/A
e095e192-3bff-5a62-a051-ef8e91c32074 | note | Key - S
8d5f77a4-a3d9-5896-b9d0-f4c993f0855a | note | UGL Key - S
58a36643-dbf0-5193-9393-e28b7ddd6705 | note | SHL Key - S
433d818f-7016-54a1-96d7-1ab5c934480d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bd8bc4ca-eaf6-5617-a809-0b6ae4efd08c | tickbox | Test reports
| checkpoint | 2.4 - Pit Buoyancy Slabs
2af57b9b-e29d-5a79-8ad6-42eba3a0a7ba | note | Ref docs - Design Drawings
7576850d-1b4c-5eef-8b64-a59795b0b1bc | note | Acceptance Criteria - Pit Buoyancy Slabs to be installed and bolted to precast pits as per the design drawings.
5157bbf6-317d-5e25-95c1-bebb50a45806 | button | Acceptance | Yes,No,N/A
5b817281-db46-5290-b3b4-c54ae23a09e8 | note | Key - S
bab89831-d80c-577b-a4b8-a73008c05e3a | note | UGL Key - S
3a1241bb-e14e-5e2f-a805-e83b2f2e0795 | note | SHL Key - S
| checkpoint | 2.5 - Pit Installation
cc3eba54-c5a7-57d2-81a1-e29ce8f66f3a | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.1, 3.3]
a723a0ef-6f25-502f-9e00-83f7fe5f041c | note | Acceptance Criteria - Pits to be installed as per drawings and manufacturers specifications utilising certified lifting points.
a0cda77d-6e1a-5845-8fed-2d0fd498fc7c | button | Acceptance | Yes,No,N/A
fcfb0229-b37f-56c7-9420-d8184b6deab0 | note | Key - S
a9fd114d-f031-5edd-b93f-0dcb6b0e5c42 | note | UGL Key - S
b9c6b0b3-0f08-5fa2-ac2b-a8c0f235bde2 | note | SHL Key - S
| checkpoint | 2.6 - Access Covers & Grates
5634f71e-c163-58d3-b724-2922e6b31f71 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
51fcbc42-c5d0-50eb-bb42-035be3cdb41a | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
031c3b6c-16e3-5f3a-9c19-d10b9d6346a4 | button | Acceptance | Yes,No,N/A
8f8bc47a-2fc3-56f2-9962-658e4b3109b6 | note | Key - S
3f2c275b-2ee7-578f-8d55-7c9d01653443 | note | UGL Key - S
1d7f1829-fefc-505a-a48d-f35aefe8aa80 | note | SHL Key - S
| checkpoint | 2.7 - Step Irons
780205a8-3917-5c1d-9861-33f876b4c4d4 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
6708a13d-98a6-58e1-8fea-de8e95e8d35b | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
cf459b44-ad59-5d5f-bc39-7e4f932e4cce | button | Acceptance | Yes,No,N/A
bc4f1b74-a8ba-5121-b3a7-a0135b374d83 | note | Key - S
6c99a675-9dfe-50be-8cfd-6c19bc429f36 | note | UGL Key - S
24b294d3-9575-54c4-8fcf-1a1018a8beac | note | SHL Key - S
| checkpoint | 2.8 - Pit & Pipe Connections
0065ceec-f66a-5376-8ea5-31b972f9032f | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
b4351cd8-e1ed-57e9-bafd-d98d4c65ce2f | note | Acceptance Criteria - Inlet and outlet pipes to be connected into precast pit walls as per design drawings & manufacturer specifications
41003606-9b7f-55bf-9495-0b40a328e367 | button | Acceptance | Yes,No,N/A
5bce9afd-c6b5-563d-b372-bec10b50d241 | note | Key - S
055ac5be-3ff0-51fc-aafe-08d948447bbd | note | UGL Key - S
e7672e2f-fc78-5a41-8c23-6aef47b44c1e | note | SHL Key - S
| checkpoint | 2.9 - Pit Jointing
9f0e2c5e-5557-586a-979a-440cbfdd9f62 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
42fa34db-c0e5-5b49-bf88-ca3922bf34fd | note | Acceptance Criteria - Internal joints between precast pits and riser units to be waterproofed as per Symal RFI-037 & manufacturer recommendations.
1cf53b10-7fbb-54d1-b5b9-7947a714bd8f | note | ○ External Joints between pits and abutting concrete pavement, kerb or structures to be a 10mm isolation joint.
85ba263e-48c3-5496-b31f-3c772501c4d4 | button | Acceptance | Yes,No,N/A
6a950e9f-fa3d-5bff-860f-698859afd216 | note | Key - S
beefe677-b113-5737-80fd-68ab68a04c01 | note | UGL Key - S
b03e38a4-80a4-54af-a9b5-096f332fd20f | note | SHL Key - S
| checkpoint | 2.10 - Backfill
145218d1-774f-5bd6-9a9f-d4eac6780867 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.7], Spec. 1112 Earthworks [Cl 4.10]
5507f336-b1b6-5acc-b633-dc671531d8e4 | note | Acceptance Criteria - Precast Structures to be backfilled & compacted in 150mm thick layers.
aa0283a6-79d5-5d46-a649-46768f4e89fe | note | ○ Backfill to be Select fill for material within 1.5m of pavement surface and General Fill below 1.5m deep.
9a7b5597-8af8-5cc1-8b21-71276db59c9d | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
f590f1a5-9aae-5559-8d01-52f8a1834087 | note | HOLD POINT Prior to Backfill
cf59e2f3-bbeb-5d13-8b6e-87eb001b760f | button | Acceptance | Yes,No,N/A
add46eb2-ddcf-5893-84bb-6f008774802a | note | Key - H
716c6a36-488f-553b-ab3a-1b23fd03442b | note | UGL Key - W
1fae0abf-5357-5b43-b0f0-ec368b95cbd1 | note | SHL Key - S
9745a92b-448e-5844-962a-7e4be953dc72 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8ee2e93d-f704-50af-91b0-72a26612b1d9 | tickbox | Material Test Report
| checkpoint | 2.11 - Compaction - Backfill
864cdf3d-fb9b-551b-b80b-a8bf0695fc0f | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13
13dabe6e-2a02-56af-8946-d3875c3311ca | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against pits to be:
952aad7e-6def-5a26-b65f-9753d0fdaf8c | note | – 92% for general fill
2ae4234b-a16b-57e6-89c4-5d09b286695c | note | – 97% for select fill
3d8f2ddb-c18a-5531-987f-2ea68dc99f5f | button | Acceptance | Yes,No,N/A
750a5747-01b5-5e59-bac5-a3986c92624f | note | Key - S
8d4ec2a9-07d1-5c76-b62e-f65d4e538f5e | note | UGL Key - S
188a774f-dfa9-5a82-9246-4262f8868a89 | note | SHL Key - S
869c41c6-19c1-5afa-a07e-46089b735e45 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bfceecf9-17f3-5ab4-a5a1-d89a9265e705 | tickbox | Test reports
| checkpoint | 2.12 - Moisture Content
6913c316-9a96-5078-8a62-609e895a070b | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
dbd3197c-30fa-52b6-a14a-40630ae9aeb2 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
fcad517f-7306-5768-a7f7-757913a3d3b6 | button | Acceptance | Yes,No,N/A
31870570-6bfb-5a29-9193-dbf009a7f200 | note | Key - S
f7e6395c-cb5a-53cd-b76a-f9815bff85fb | note | UGL Key - S
bee9959a-3f82-5afd-b9bd-d3a524257ba2 | note | SHL Key - S
6489ad58-de2f-59df-bffb-48bbac32d4ea | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d8cee89b-9bfc-529b-97e1-e16437060afb | tickbox | Test reports
| section | 3.0 Conformance Check
| checkpoint | 3.1 - Survey Report
1fcea21b-5be9-5952-ad02-7403e5c1b57f | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
d9e24de4-46d6-5ecd-b5ea-cc3312b132c4 | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
53a98e96-7a25-5770-a0c4-eaa5640ee586 | note | Plan: +/- 200mm
db7ae03a-431c-58ce-ab91-f8794dd9425e | note | Level: +/- 20mm
548b2d94-2bad-5b69-b0de-f5249586322c | note | HOLD POINT
1a278e96-8bb1-5b32-ac5a-7b874767b24c | button | Acceptance | Yes,No,N/A
f04dc712-22b5-5aea-b957-2b59f13477df | note | Key - H
d70dae81-5293-5bab-adb4-eaad3d60c215 | note | UGL Key - W
f0ba6bcc-ea80-575e-8d53-065358d2b98a | note | SHL Key - S
e4616bd3-0aae-5a34-83ea-1dcdc5538593 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2736db49-398e-593a-a1ce-dae7eeab9abc | tickbox | Survey report
| checkpoint | 3.2 - Acceptance and closure of non-conforming items
fc7be392-28ec-5057-89a0-a89570c70192 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
094b92ea-21bd-5d2d-8c27-9cd1b700ab0e | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
27a3f015-27a2-57e3-812c-46d88185c42e | note | HOLD POINT
3b87b8af-f3f2-5be5-8162-fa4f245ff443 | button | Acceptance | Yes,No,N/A
c0184e28-07e6-540b-9afc-034d6a3ffd88 | note | Key - H
5c53803e-e059-51bf-b9cc-14336b4661d8 | note | UGL Key - H
93db51dc-7be1-55cf-87a8-4336e217b1db | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-004 Oily Water (Pipe Laying) & Checklist - Rev.6 | itp | INF-HSEQ CC0375-ITP-004 Oily Water (Pipe Laying) & Checklist - Rev.6 |  | 481449af-ca36-4750-8c6d-0c8883bd46a2
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
08adb2bb-bd96-5772-8f0c-b610d85d9d07 | note | Ref docs - Issued drawings / Site copy drawings
8da6c70f-e6e6-5c26-a41a-0e5e1ae205fd | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
8229c34a-2772-56fd-9d18-0bdea1a92ed6 | button | Acceptance | Yes,No,N/A
422c9e75-f3a9-5767-bcab-0c07bf85c600 | note | Key - S
0ce6c43a-77ff-556d-a3a0-f52b8fcfd4c2 | note | UGL Key - S
d4dfc06b-a5f5-52fc-b78f-3c1e188f13a4 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
0209090a-73a8-51b2-93d0-28939fe49d8e | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
608ea41e-3cc7-549b-8d73-adcb01876fe8 | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
1b28a4ee-dae1-57af-8274-b8c745377788 | button | Acceptance | Yes,No,N/A
ca81eb9b-f676-5c47-a033-9652a6b1ab25 | note | Key - S
722fd0b4-2f2c-51fd-9613-1a3937d4ade8 | note | UGL Key - S
cef15c17-0966-5e3b-a932-11c67a73f20a | note | SHL Key - S
b63a0c77-5c46-5979-a2c2-81dd3b143f8a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
70a9f32d-1b87-5807-b98f-ef3f1171ce9b | tickbox | Lot map
| checkpoint | 1.3 - Drainage Pipe Material
d22add74-1c33-55d1-be7e-be7379823ba7 | note | Ref docs - Drawings
e9cdd879-47f1-5820-bc9d-77a86242b089 | note | Acceptance Criteria - Has the correct class & type of drainage structure been supplied and free of defects?
7b473a95-5ad4-5ca8-9a6e-b65e6e3c986e | button | Acceptance | Yes,No,N/A
57bce863-f437-58a5-9777-7af208dc6c8f | note | Key - S
a040e73b-8084-5e01-af6b-feb75e2197ba | note | UGL Key - S
5a2f54f7-889d-57d5-b509-73667f8b80a2 | note | SHL Key - S
e794aa3f-b88c-5988-a697-3c3f0a782cd5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1881211f-4b56-538f-930b-96c260698cf0 | tickbox | Material conformance certificate
| checkpoint | 1.4 - Embedment material
7b1c6d6d-c832-59e3-af50-7f986164c5e9 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
d67df3b6-f12a-5f6e-a0d4-e85e683dc3fb | note | Acceptance Criteria - Material has plasticity index less than 6.
b07e9a41-7b9d-5137-98d5-d939ab24da0e | note | – – – – – – – – – – – – – – – –
124e5f64-47a5-5007-9858-4435a2331d59 | note | Table 5.1 Embedment material grading
a7cba0e6-b1b2-5ed8-ad57-06409ee00e50 | note | – – – – – – – – – – – – – – – –
bfbe11cc-ffdd-5d0d-ae99-5315aa6eb582 | note | Sieve size (mm) ¦¦ Weight passing (%)
7bdb831e-cf7a-5da4-8ad0-93d0876021e7 | note | – – – – – – – – – – – – – – – –
269b9187-b469-51dc-923a-d1748bef622e | note | 19.0 ¦¦ 100
8b3086e4-6423-56dd-9d92-b6a6fd451bc4 | note | 2.36 ¦¦ 50-100
dfb8d022-b0a4-5f51-88ce-1eef83f2e701 | note | 0.6 ¦¦ 20-90
fb5db0e0-71b2-536d-a2af-e2f5c6d269f2 | note | 0.3 ¦¦ 10-60
7b88f4a8-c5ad-5aa8-8a78-65c37ca25f51 | note | 0.15 ¦¦ 0-25
6003c99a-6e07-546b-82ad-a823ae6a8517 | note | 0.075 ¦¦ 0-10
6d9c18bd-3cc2-5433-b6cf-8ba1db29f1a1 | note | (Table taken from AS/NZS 2566.2, Table 5.5)
9fc2738f-55f2-572b-8d85-92616db43052 | note | – – – – – – – – – – – – – – – –
97356fd8-b2d8-5fcc-9255-088399bc3963 | button | Acceptance | Yes,No,N/A
eabb70cb-7961-5799-a443-b99da595e4ea | note | Key - S
61f92623-a574-510d-b75e-95a73d6ba854 | note | UGL Key - S
53fd27f4-09d1-51d7-b097-81ff6a069c5a | note | SHL Key - S
359388ef-23fd-5739-9f68-80a256550c55 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f3072f19-56c7-5a96-bd3c-895887f50264 | tickbox | Delivery dockets
8241ad2d-5feb-5543-8a70-005771f498a2 | tickbox | Test reports
| checkpoint | 1.5 - Underlying Lot Conformance
49474a7c-7ee0-5a76-8d55-0a4545be2697 | note | Ref docs - Underlying Lot ITP
ee991f2b-b84a-51f9-9edc-b12674fc5a0e | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
4194d93f-d98d-5814-9c51-de39a517671f | note | ○ Refer underlying lot ITP(s)
a02d96c9-3467-5933-88af-2edefbe32bb6 | button | Acceptance | Yes,No,N/A
fbde8ad3-3039-5d14-a8fb-5954241d285d | note | Key - S
ec03a385-567f-536a-968d-8ea627e6aabd | note | UGL Key - S
f01cf819-1686-5746-bbef-0dd50b0cc521 | note | SHL Key - S
| checkpoint | 1.6 - Temp. drainage during construction
9c788c72-1052-5ba7-92b1-c557e34ccba2 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
4675008c-dbf6-5472-8ef8-bdf51040aca3 | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair.
0eda91f9-0e68-57d1-92eb-cd8a3595dc16 | button | Acceptance | Yes,No,N/A
468c3db3-e061-5028-940f-69bf6c425f81 | note | Key - S
1b39ffeb-ffc6-5428-93f9-8b708e630068 | note | UGL Key - S
49cf9a2b-c490-531c-84c3-aa5b282bec87 | note | SHL Key - S
| checkpoint | 1.7 - Set out
d7e6767a-aaa7-5810-bf44-e0f82bb081fd | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2], Drawings
8515ce22-fc7c-5908-ad94-4df2400c8409 | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
c3f732b6-2561-544b-a8e9-9d105b311af4 | button | Acceptance | Yes,No,N/A
0312fcb2-8ea1-563e-b03c-15743e5c3732 | note | Key - S
7bcfb41e-e8d6-5338-b9f1-d0197803795a | note | UGL Key - S
0e23872a-4242-51e6-9c29-2a0a19ebb4e0 | note | SHL Key - S
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
f2550fc4-6a5f-5912-80bf-dab454790cee | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
b50fe8ee-bfdb-5eb9-8f8e-db0aeb42a36f | note | Acceptance Criteria - DICL and Plastic Pipe:
5759149b-cf42-5dda-99c9-b4d08ff613b0 | note | – – – – – – – – – – – – – – – –
cbfb67bf-5476-5861-89fd-75e00893631e | note | Table 5.2 Trench and embedment dimensions
71d6dd6b-8a57-57ff-beb5-9abc2b4fcf4c | note | – – – – – – – – – – – – – – – –
36f70226-8b45-5752-9044-9d88e29157aa | note | Extreme external ¦¦ Minimum dimensions (mm)
b3436101-e3c2-5d61-9e58-b521f1b19bdb | note | Dia (De)mm ¦¦ x : s : o : y
ff08e84f-9e4c-52e7-98c8-b069fd446a4c | note | – – – – – – – – – – – – – – – –
67b3601d-acef-504e-9fb2-364a9d590118 | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
0c4c9f59-cfb5-537d-be97-1f2e984ffb16 | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
3706cb86-fc09-5f53-9ec3-15947121c07e | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
f278d67b-0b46-515d-8942-63d674421a89 | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
9a2aa3e6-55e7-5788-adaf-c4ec30b27f47 | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
75544a86-ec49-519d-9d49-45d177ec0457 | note | – – – – – – – – – – – – – – – –
5742858f-1fcb-5d4b-b549-1649a22dfe33 | button | Acceptance | Yes,No,N/A
cc3712a3-6041-5c57-a847-59ea1cbefcfa | note | Key - S
3e01d7a2-9724-56ff-874d-5e3669a3e094 | note | UGL Key - S
f7a692ec-d76f-50f9-9bba-d2127a2482a2 | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable Material
e70855ab-10dc-512f-9d52-6c9201bf79af | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
cce4ce2f-5ad9-50a7-8205-30a20670b56a | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
cc30e38b-81d3-586f-a94c-37aedbc7f03e | note | Notice: Prior to Placing Bedding
cc4425f8-78bf-5cbb-8798-f32962fd1ffc | note | HOLD POINT
f5a188a8-9b11-5d5a-842c-4312de4a1751 | button | Acceptance | Yes,No,N/A
bb637bbd-ef7e-5619-b127-a70684dc101b | note | Key - H
06b09e4a-efb0-5807-8dac-c0395ea7b43b | note | UGL Key - H
89c2f39a-96db-5dbd-b701-4daeea8e7a02 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction – Foundation
2d8bc8ed-7e2b-5b0d-b8f8-4227ef4a9a4b | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
dc6196af-05f4-544b-9479-8f3f023a7578 | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
dfad7e5d-0260-575b-a120-415027517f6d | button | Acceptance | Yes,No,N/A
097cd713-cfc5-534b-96f2-3a738bddb5ec | note | Key - S
4ca9b456-1e8c-569c-8c3c-3949d5eff4e5 | note | UGL Key - S
dcddcac9-0677-5401-bdc8-8b7efa989849 | note | SHL Key - S
de5b14a4-5314-5dff-8fcc-932c397a1737 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ccd3df89-d283-50cc-93b8-e48dec9de0e0 | tickbox | Test reports
| checkpoint | 2.4 - Compaction – Embedment material
0ae1c6f8-8298-516b-aad3-192b0fd4c698 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
27aee5eb-e0ad-5f89-9701-c07f9a95f3ad | note | Acceptance Criteria - DICL and Plastic Pipe:
d41f43d9-d0d2-5914-a1d9-ecd16a1ce8ee | note | Bedding:
ce3d0b62-9def-53da-9fd7-df3e80a484a0 | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
ec4871ad-f500-5ea0-bff3-b2a948d38e55 | note | ○ Layers not to exceed 150mm compacted thickness.
ee256f17-0dcb-59cd-adfc-35be5e08831a | button | Acceptance | Yes,No,N/A
5e22af0b-4ff9-5999-9278-db7cbb88fc8d | note | Key - S
afdb65be-ce8b-57fb-b72d-c316b74ea503 | note | UGL Key - S
ccbcb957-da00-5024-a849-36b8a1faa684 | note | SHL Key - S
2f6672f1-705b-535b-be01-d46072e6ad21 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2238d18f-fe77-52ca-bba6-b874795f87b6 | tickbox | Test reports
| checkpoint | 2.5 - Pipe Laying, Pipe Joints and Protective Coating
9ffae909-fa2a-5b2e-aa3f-f650da0b7c33 | note | Ref docs - Drawings, Manufacturer Specifications
a9f4e913-9ff1-55dd-a735-5e428625c4cb | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
65a5ea4f-da25-59d6-bac6-99b1b8964f93 | note | ○ Pipe joints installed and torqued as per drawings and manufacturers specifications.
2f2bd4e2-ae26-561c-989e-a2b15ed18a7a | note | ○ Protective coating on pipes applied as per manufacturers specifications.
dab4cebe-d326-521e-b20c-e01750412116 | note | HOLD POINT
265cec24-9489-540d-a1e5-11b1adb6e4e1 | button | Acceptance | Yes,No,N/A
1870c7f8-f93f-5d51-8992-0ec486ea1ca9 | note | Key - H
3b8ac0f1-5bb5-5960-8112-4923a8bc5560 | note | UGL Key - W
fcc6bff3-c35a-5f5a-b68e-be5c5fc8a729 | note | SHL Key - W
35583ac5-cc4e-5bf9-870e-b41d295636a1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
993ae244-b113-5169-bc56-beffc847921c | tickbox | Flange connection and protective coating check sheets
| section | 3.0 Filling and Compaction
| checkpoint | 3.1 - Compaction – Embedment material
3713ec8b-8d9f-5885-89b6-4a2d131c4150 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
d6d15c49-65d4-533d-b222-952c3e6d51aa | note | Acceptance Criteria - DICL and Plastic Pipe:
2947a3c3-4c18-5aad-9cee-b8c1899c5137 | note | Side and Overlay:
024f7a8c-d30e-58cd-8841-de3d73a86f85 | note | ○ Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
e383961f-bdd4-5914-83aa-c27678311e95 | note | – – – – – – – – – – – – – – – –
1feda0ea-377a-5d74-921d-07c297275fed | note | Table 5.3 Minimum relative compaction
90445425-b450-5283-beed-dbad9371e98a | note | – – – – – – – – – – – – – – – –
2dad8a3c-5d4f-50ac-8f76-cd2324050dea | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
b5d51674-972f-5568-ba47-fd4a9afc2846 | note | – – – – – – – – – – – – – – – –
7ade0b8f-1abe-5f11-a320-6f24c8d3a48e | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
2e570b21-7bbc-5e5b-95bb-3c75c5fee453 | note | – – – – – – – – – – – – – – – –
561cd108-d249-56fc-9588-5d05f2244a52 | note | Layers not to exceed 150mm compacted thickness.
5f108bfe-c7bb-52e9-8831-0c581e31f978 | button | Acceptance | Yes,No,N/A
89becd64-43f3-51a7-954c-f640ae452016 | note | Key - S
cd57602d-8c6c-57a4-b2da-844b05bf924d | note | UGL Key - S
671cca38-2d89-55d3-9e09-93db1c51a6fb | note | SHL Key - S
6a408a4d-a68f-590f-94b0-e767bcc8757f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e8163bcc-1ea3-5fdc-ab55-7517abc666dc | tickbox | Test reports
| checkpoint | 3.2 - Compaction – General Fill
3641b63d-4a32-5cb8-90c4-35a3003a9a40 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
b387c5ff-0720-59e7-915e-cc38315c851a | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
d764eba3-9d02-5368-81db-a5ccbd2b009c | note | ○ Minimum relative compaction to be 92%
58163e41-4322-56c9-9188-4bd29a2cd967 | button | Acceptance | Yes,No,N/A
e8d82ec0-45fd-535f-be59-6e857ccb3860 | note | Key - S
538e6e1d-5b74-5221-aa28-db3d61aa3bc6 | note | UGL Key - S
033039cc-659e-51b0-a24c-688ca447edf4 | note | SHL Key - S
2b5f4592-c14e-5ed4-8bc1-07aaaad8cd74 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1a5a2f14-e4ea-5459-8df8-f50cb67d11da | tickbox | Test reports
| checkpoint | 3.3 - Compaction – Select Fill
c6bdbf5d-991a-557c-a093-489404aa3cc0 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
c1d156d2-8773-554d-929c-a40fc829ec53 | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
e8c8be93-956f-5232-b1c9-e9bba6331665 | note | ○ Minimum relative compaction to be 97%
e1db8c4e-e33c-592a-b88a-5f1c294c68f5 | note | ○ Layers not to exceed 150mm compacted thickness.
81f4569c-e8f7-50eb-95e4-4fc7421d7a81 | button | Acceptance | Yes,No,N/A
d6fc8b17-e7ba-5bc9-8d61-40ad9e57fe6b | note | Key - S
83a975ba-26dc-5772-b17e-cf511b70a698 | note | UGL Key - S
2dc1df7e-41da-581e-8b3e-bbba2716dcfc | note | SHL Key - S
69b0c61c-8722-5da7-9289-5c94a4981953 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7f913d44-9d56-520b-b5ce-59de25ec05ef | tickbox | Test reports
| checkpoint | 3.4 - Moisture Content
446ca5e0-ba5f-5f46-a823-6cf6212aefcd | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
647f5f4a-1842-56dd-b401-2ef80b22ea8c | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
d31ecb59-1d95-55f7-8bbc-2ccc3f11a382 | button | Acceptance | Yes,No,N/A
a65a60f2-0ccc-598e-bf93-7699d5473681 | note | Key - S
8fbbf796-3242-501b-a370-1ad0dd34fcd4 | note | UGL Key - S
976e1f2d-122e-54ed-a5f0-ea4eabfb7328 | note | SHL Key - S
0536ac45-32ae-5f5b-93be-9ae4969b6fd8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7f36196e-05c1-5d15-80dd-bb419eaa8a94 | tickbox | Test reports
| section | 4.0 Conformance Check
| checkpoint | 4.1 - Survey Report
51d273bd-7b24-592b-bc30-f3590539523c | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
e0bd05ec-4bb2-5cda-81a4-9dab541af18a | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
a6835ab4-3abb-52ad-ab6c-640671bb2071 | note | Plan: +/- 200mm
cb43bf8b-71f5-500b-951e-6b7adff5d9a3 | note | Level: +/- 20mm
6775ba81-e3a1-5794-ab44-636778e88499 | note | HOLD POINT
febdd185-15a9-5d95-ae6e-a3f1bf1ccdbf | button | Acceptance | Yes,No,N/A
7606c9ec-adce-525d-9ed6-f277f1cbdd9b | note | Key - H
6de49d22-786c-5bd1-b6a1-698b88cbbe86 | note | UGL Key - W
d30497b1-135c-56ee-aac5-65ea9aad9943 | note | SHL Key - W
86e113b8-99cf-58d3-9f24-6e201ae0367d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2fb6d66c-e755-57ea-9993-58c0cac4c020 | tickbox | Survey Report
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
e4ce0638-d949-5ec1-8634-64c1e624738d | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
0fc03dc0-861d-599d-b104-451d09a833f4 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
3e7c628f-f6ba-5182-8847-580223bba8b7 | note | HOLD POINT
f4026d98-b4a6-5f1e-a1de-31e574b2d40a | button | Acceptance | Yes,No,N/A
c2cb9002-5524-599b-9513-65d5f629a9d3 | note | Key - H
fb446174-6f8b-5eb0-9f34-8b9ba4a3b6ea | note | UGL Key - H
b4770109-7f33-5506-b832-e07ecd4c6135 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-005 Trade Waste (Pipe Laying) & Checklist - Rev.6 | itp | INF-HSEQ CC0375-ITP-005 Trade Waste (Pipe Laying) & Checklist - Rev.6 |  | d733d7bf-8d5b-4f9b-beb7-dad07f97e591
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
61facac9-e3dc-5b4c-9155-100c10f3f3fd | note | Ref docs - Issued drawings / Site copy drawings
35b272ff-64b1-5b53-9dd3-15a81efb97eb | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
a1479f5a-ce6c-5c2f-86ea-5991e3e46757 | button | Acceptance | Yes,No,N/A
bcaca99b-a26a-5af8-8b3e-dd61219aacc8 | note | Key - S
124ef8ff-d241-5f2f-b59f-703b1f9e7d70 | note | UGL Key - S
a8a2ee59-c0c4-52c5-ae09-76c5dd0670c1 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
16982c54-3040-573c-9e97-0e2d74b92314 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
10151db4-d628-579a-98a0-744232c1739b | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
8ef016d9-4e99-511d-ad47-77e230b4af94 | button | Acceptance | Yes,No,N/A
e9347d70-f21f-569e-a536-78393d5b943e | note | Key - S
1a5e639d-3167-54ef-8bb5-27ea027e4960 | note | UGL Key - S
7939ec0a-e366-53bc-b9c0-e0de98ac3543 | note | SHL Key - S
492ba1e5-ba76-579b-bc1f-e5fbc9e72264 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
eabac4e8-3d7d-58a7-abac-6178d39d4121 | tickbox | Lot map
| checkpoint | 1.3 - Drainage Pipe Material
3628a0d4-a4b3-5bfa-a780-cac22db7c83b | note | Ref docs - Drawings
f7e7f162-22ed-5004-a5a0-1b1a1febf1fc | note | Acceptance Criteria - Has the correct class & type of drainage structure been supplied and free of defects?
513d2c68-91c5-5563-9004-decb6a3533a7 | button | Acceptance | Yes,No,N/A
fa500248-eacd-577d-9cfc-60f387573cdc | note | Key - S
24f75e1b-a9a7-5a94-b23d-49afaf7053ea | note | UGL Key - S
286d914d-271d-5888-8e26-d2ec638f515d | note | SHL Key - S
f227a9f2-0e60-53d6-b3c4-4a464fcbdc52 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7e40a5d0-a454-59e8-acdf-3f8c7901be06 | tickbox | Material conformance certificate
| checkpoint | 1.4 - Embedment material
a330ad52-9747-51a8-aa9d-a7e395a5a864 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
1b711836-42b5-5b7a-bc70-022a42af65ec | note | Acceptance Criteria - Material has plasticity index less than 6.
0ec9f40c-c411-5f13-befb-c286fdc3bbab | note | – – – – – – – – – – – – – – – –
c2a7ec02-989e-57a9-89c4-8e88156835f1 | note | Table 5.1 Embedment material grading
30d5622c-53f9-59f6-8848-56de2a4e2156 | note | – – – – – – – – – – – – – – – –
041ad20c-d80f-5e36-87b1-290e9b81e12c | note | Sieve size (mm) ¦¦ Weight passing (%)
e2aa3b40-f6f5-54d1-9726-da9bc7feec14 | note | – – – – – – – – – – – – – – – –
0c10928e-a0c0-5b2c-84b4-694ccb312fce | note | 19.0 ¦¦ 100
e1efc8c9-01f8-5e84-866f-b82115ddc2ee | note | 2.36 ¦¦ 50-100
d083f9c0-7c0d-51e9-9276-e0f7ed9e02c4 | note | 0.6 ¦¦ 20-90
a9276b93-6ae2-5a87-9c22-6267916daa85 | note | 0.3 ¦¦ 10-60
63167605-c8de-5700-b97e-2b3678f23ed1 | note | 0.15 ¦¦ 0-25
58c3a3f8-0a3a-5156-b318-2fb09e0bbcb4 | note | 0.075 ¦¦ 0-10
4ab8ce50-9686-5473-97b7-53748951c426 | note | (Table taken from AS/NZS 2566.2, Table 5.5)
7cce10e1-a990-5f7a-a865-b92b16c8a661 | note | – – – – – – – – – – – – – – – –
586ab23e-1335-5e03-ba53-d6b7b85b0209 | button | Acceptance | Yes,No,N/A
f99a20eb-8090-5fa2-b959-a6eb7e4e9e9d | note | Key - S
0d833831-2575-55b4-b851-0fd62d95064f | note | UGL Key - S
a4591bf2-b135-57ca-8087-8432dbcd9b46 | note | SHL Key - S
8f81dfc8-6404-5503-bceb-f8145e8ac6b1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e76e7139-1b23-5b40-8ad5-547baa4a5e20 | tickbox | Delivery dockets
1d7edbd3-1660-5c50-9523-f7284067818c | tickbox | Test reports
| checkpoint | 1.5 - Underlying Lot Conformance
48458496-dc29-55a0-b321-d9b3c0541c12 | note | Ref docs - Underlying Lot ITP
9b157007-af1c-5fce-890f-8df0a0843689 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
2b5b25a7-df96-58d2-a3c7-a4a29524b644 | note | ○ Refer underlying lot ITP(s)
2a5384b5-aea9-5711-905e-b2cb25805fc9 | button | Acceptance | Yes,No,N/A
4c1de4be-911b-5e06-948a-b2bb3f80a84c | note | Key - S
83de4c13-ee74-5fb3-915a-8a3030d47f7c | note | UGL Key - S
eab8133a-1d74-5035-9b1b-39a50c67c749 | note | SHL Key - S
| checkpoint | 1.6 - Temp. drainage during construction
50d54d77-aa53-5edf-be30-2841f9ee5122 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
fd0effa3-5b6e-53cb-beeb-b7be2f1dbb50 | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair.
a0acbacc-2eff-5b1b-98c5-aa2cd53c2335 | button | Acceptance | Yes,No,N/A
ddc39fcc-09ec-5ecb-a9d0-ef0a9d96a1f3 | note | Key - S
0237c8eb-63dc-5bbd-a3e3-77c4968e096f | note | UGL Key - S
85ec4ea7-8370-597a-9768-104e26f6b00d | note | SHL Key - S
| checkpoint | 1.7 - Set out
e476485e-5e5b-5cf1-9374-d8b19fae90ae | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2], Drawings
905cfc32-f23b-55d0-bba2-7e2ce12d0c34 | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
c9e0d9cd-efd7-54d4-94bb-13070a469a63 | button | Acceptance | Yes,No,N/A
6fb78b81-f365-523d-bf46-a6a5c608d1b8 | note | Key - S
73e28545-fd47-5e20-8a53-2c466000dc3d | note | UGL Key - S
7bb631eb-2386-5e17-9eca-268046ef55aa | note | SHL Key - S
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
878dec8a-9762-50ba-a671-d2ea2bf1a8bd | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
7051af7e-6be8-534e-9339-49ef18db683f | note | Acceptance Criteria - DICL and Plastic Pipe:
91097225-e32e-5ba0-851d-a8c8c8eda2b5 | note | – – – – – – – – – – – – – – – –
af0ea196-c850-57f0-8857-18ea8e41e466 | note | Table 5.2 Trench and embedment dimensions
3386acac-99b1-5bba-8be5-9f3669966f9a | note | – – – – – – – – – – – – – – – –
a6de63b7-b14c-5abe-8364-efbee72e6869 | note | Extreme external ¦¦ Minimum dimensions (mm)
a80e6273-e75f-57d9-8640-dbcf639ad46f | note | Dia (De)mm ¦¦ x : s : o : y
0d9e9d9c-cc6a-5691-a219-774b0994c611 | note | – – – – – – – – – – – – – – – –
f2263322-f663-5136-84fc-34cbc24800c8 | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
5d19b4d1-f514-5fb8-80d5-441abdfdfc2f | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
671938ff-95df-5559-8fc2-f4ad9e33d106 | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
e5ee3bc1-0512-560d-8b19-4871b1733323 | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
9f676a0b-f371-5da4-9671-abd75f6b94b6 | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
e87a978a-ea49-5ba3-87af-cac9e5375df5 | note | – – – – – – – – – – – – – – – –
4426939d-7031-59e3-856c-857d29e6fa5a | button | Acceptance | Yes,No,N/A
ebdabf2e-2e8d-5d16-8475-b578971eacbc | note | Key - S
f12cbfb9-8c11-5ef7-983d-ad20490367f7 | note | UGL Key - S
eefe3761-37c6-5a30-853d-7b73b33486d6 | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable Material
3feb7b30-3194-5f10-8f08-c800813cb412 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
3503c098-e841-51e9-96d2-738eaa876214 | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
bbb5c848-dffc-584f-87e2-ec5f4d41ddcc | note | Notice: Prior to Placing Bedding
300e46e5-faac-5707-bcd8-86c2631bcf8a | note | HOLD POINT
a9d55456-16c8-583f-81bb-61263ba7b7ba | button | Acceptance | Yes,No,N/A
48a4a65e-ac65-5336-9b45-c9485dc9f7a4 | note | Key - H
dbea6244-aaaa-5d90-bc95-8052e7babd54 | note | UGL Key - H
4f86f875-5e12-5a9e-bfff-af2e2fffb6e7 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction – Foundation
5f709cea-f991-547b-aad8-839f7756ffc4 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
0211d37f-17be-530f-b663-2b2dda4efa71 | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
0b8d2ab0-95f3-5c97-8fdd-1dab451f0245 | button | Acceptance | Yes,No,N/A
0c6e9c54-91f9-5e9a-9cad-0a402f9bece9 | note | Key - S
d39b00aa-0f6b-5e95-9104-6fcbf2dffc4d | note | UGL Key - S
fe6010ea-e543-5209-a179-c3f640841b53 | note | SHL Key - S
f4d6198d-a74e-53c0-bdd8-c5456dba9c89 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d1a1ec00-8c3e-557c-bf0a-fb2952b8f423 | tickbox | Test reports
| checkpoint | 2.4 - Compaction – Embedment material
6e01f189-2cb3-513a-b9da-4ce878e6f3cc | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
f6ee1d6c-7498-5397-8cb7-9200757b9b44 | note | Acceptance Criteria - DICL and Plastic Pipe:
02569b82-4749-5eb0-9888-988d3dd34a8e | note | Bedding:
1bd41751-d66e-53c1-bf7e-cec57b0ae24b | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
0e193389-72b6-5640-949a-c065cf68fe37 | note | ○ Layers not to exceed 150mm compacted thickness.
2fb664cc-9058-5de0-9453-32688f43b2fd | button | Acceptance | Yes,No,N/A
e9037cfa-2b79-5154-a028-d735b43f6b4e | note | Key - S
d877f2a2-059f-502b-a3bb-efdc119c3c6b | note | UGL Key - S
914c5a50-3dd5-5585-97da-a47f375d9572 | note | SHL Key - S
485fd6eb-0fa3-548e-a617-2c3cec2f0a5e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d7479dc3-999a-5dd0-b370-5934527ad6d8 | tickbox | Test reports
| checkpoint | 2.5 - Pipe Laying
14a50dbd-5377-5007-83ed-0faff49e4254 | note | Ref docs - Drawings, Manufacturer Specifications
2b99f398-74e0-567b-857f-2883cf27d416 | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
35ce6004-c936-5758-89eb-623b6bd4ccf8 | note | HOLD POINT
9a3f0f0e-c257-5d43-b2c0-2fec169fc723 | button | Acceptance | Yes,No,N/A
6b68db4e-0df1-56ae-801f-53b597e4a2d3 | note | Key - H
b8523d44-e022-5bd7-986d-b1b57b0be489 | note | UGL Key - W
46a53c0d-b9f0-5285-a6ca-2cf58167cad3 | note | SHL Key - W
| checkpoint | 2.6 - Pipe joints
c2efa52e-6d45-56b6-9830-10c0293552ba | note | Ref docs - Manufacturer Specifications
5c193d32-b816-51d3-8bd2-c51eca023eed | note | Acceptance Criteria - Pipe joints installed as per drawings and manufacturers specifications
24e5f5d2-ee90-5bd5-ba5f-ebb6bc8d9734 | button | Acceptance | Yes,No,N/A
14e20436-1db1-539d-886a-fbf8ac828991 | note | Key - S
9d6754fb-7098-5aeb-9f8d-d2e62ff647d9 | note | UGL Key - S
8ed63abb-b341-59d6-81a7-15b0fdef05f6 | note | SHL Key - S
| section | 3.0 Filling and Compaction
| checkpoint | 3.1 - Compaction – Embedment material
1543b433-cdc6-5a80-bb28-974077570148 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
4aa9dbea-e5bb-5522-8651-f728b67877f3 | note | Acceptance Criteria - DICL and Plastic Pipe:
872208a1-9712-5ceb-9ec6-8bf4ae2cdf37 | note | Side and Overlay:
05a1e4c7-6aae-58ac-84ae-74b5fec5dd35 | note | Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
128248b0-595d-5cae-b491-b99608df2df2 | note | – – – – – – – – – – – – – – – –
5fde0226-d1fb-5771-bbf8-5463cb54a8c0 | note | Table 5.3 Minimum relative compaction
0e830e34-310c-5d1e-b65c-37d38414c1da | note | – – – – – – – – – – – – – – – –
1b30095c-702f-5521-904d-a5b920929962 | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
bbbbc9d5-a1a0-5d08-8d40-6582a771ddff | note | – – – – – – – – – – – – – – – –
efb0d61a-f515-5be4-9f3c-e30e0063e52e | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
227990aa-2a80-5c73-b0ad-de8b94c98a68 | note | – – – – – – – – – – – – – – – –
622f93fb-237a-5345-9510-f3c53a596de5 | note | Layers not to exceed 150mm compacted thickness.
063a1f7e-a886-5394-9f80-3ca407631528 | button | Acceptance | Yes,No,N/A
fb1d0930-b97c-5813-8924-27830e0d08f8 | note | Key - S
c9a9ceaa-2a9a-5ff0-bbe7-bf4b7d6a773e | note | UGL Key - S
cc7f66c1-1277-5f9d-8755-3fb51315d63b | note | SHL Key - S
7969f9da-4abd-59c6-9e79-061bb2b007f5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c7699a8f-41ad-5b1c-a371-441c85a5afdf | tickbox | Test reports
| checkpoint | 3.2 - Compaction – General Fill
d1a2553c-d7f4-5afe-920e-08c9f9c495d6 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
12b41f59-469b-5813-bb23-27bd08d2508d | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
5630da14-a461-5584-9399-b6b5c585e5c2 | note | ○ Minimum relative compaction to be 92%
f6b285ea-1852-5dd3-a7f9-9efc5bf1fd56 | button | Acceptance | Yes,No,N/A
4346bbec-56f8-52fa-bd27-7e73c7fc14f6 | note | Key - S
4d7f54f7-b879-5446-aa68-8d5d3078250c | note | UGL Key - S
64dfc4a9-f428-58aa-a97d-2683efd21ab5 | note | SHL Key - S
ec8a7189-a423-531a-8d70-1d8ac5a52380 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8d1d212e-9f2b-5c4c-b27a-852e7c40e884 | tickbox | Test reports
| checkpoint | 3.3 - Compaction – Select Fill
fe9c7797-6ca5-5a4a-a96f-283d3a36da77 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
5c69ce6b-9ead-5c79-a22e-4d6c78c3bc84 | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
f486a7e4-e4c4-5d54-8ef9-e259d12bc487 | note | ○ Minimum relative compaction to be 97%
c12c466b-aa47-5567-84f2-50c61ea51679 | note | ○ Layers not to exceed 150mm compacted thickness.
3bdf3481-cece-5310-9ca7-0363a74f71a6 | button | Acceptance | Yes,No,N/A
69188c1e-8b74-52bf-9da9-ee25f969b255 | note | Key - S
3360d85e-afdd-53e2-9c29-7173be0e83e3 | note | UGL Key - S
a4e67042-88ef-5d5f-9ef5-265f8ca6b7bd | note | SHL Key - S
b073d468-c1f8-52e8-a3f6-196faa31bc52 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
69427aea-90ca-5ee5-a1ed-1a4ffe4edb85 | tickbox | Test reports
| checkpoint | 3.4 - Moisture Content
46a7962a-f3da-5e0e-a90f-dc7fbebcf440 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
0049f6b7-3338-5f77-88e4-d5eed2954950 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
39d9d994-e63c-5e32-8720-3ee754646991 | button | Acceptance | Yes,No,N/A
2a132d63-09ba-50d0-aaff-158afe4cf08f | note | Key - S
48f4013a-904f-58ec-8ed0-e01fa08031f1 | note | UGL Key - S
ea7f8406-e09d-5db8-a4f4-6e0b20b09ae0 | note | SHL Key - S
76b18279-7721-58be-9093-8301375fc6a7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a2f4fa73-6b27-5b28-be61-fae6acadb903 | tickbox | Test reports
| section | 4.0 Conformance check
| checkpoint | 4.1 - Survey Report
7565097b-e223-58c2-a4db-035f37f1be4d | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
fe739ef8-83ae-56f7-ac78-520500f9c92a | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
ad92ce90-6548-5609-a6f0-3bc55ba0670f | note | Plan: +/- 200mm
cbc991eb-3b12-5558-b209-256d43052627 | note | Level: +/- 20mm
4f2394a1-b6e9-52c8-94fa-6a360a5b62eb | note | HOLD POINT
7db28fcd-3abc-534d-acf8-76c86bb0c1d5 | button | Acceptance | Yes,No,N/A
d6500556-6d7e-5b2d-84d1-606445311462 | note | Key - H
e4c78f02-95ce-5084-8924-60912e7fc580 | note | UGL Key - W
3bb1894d-014e-5034-a71a-7a57d1c8c401 | note | SHL Key - W
8b608ebf-3628-5fc8-bd0d-33d8f5a7ce63 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
30abe145-f226-564f-80f0-65ecef61a06c | tickbox | Survey Report
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
61245c85-96aa-5499-9f8a-b8ed234fc910 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
14dcb91f-370b-530f-83aa-96a2349223ab | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
bf72dbda-eb97-5419-827b-08bd9b126a56 | note | HOLD POINT
6a7531a3-ec48-5126-8b78-1ea1a9735c94 | button | Acceptance | Yes,No,N/A
2df17620-649d-532f-93c1-455f9ba36116 | note | Key - H
21c5c2fe-4b44-5d1f-864f-ecc25f0ec446 | note | UGL Key - H
d2b051df-1bad-5790-bad1-c91e196113f8 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-006 Kerb and Channel & Checklist- Rev.5 | itp | INF-HSEQ CC0375-ITP-006 Kerb and Channel & Checklist- Rev.5 |  | 422d5cbd-0911-401f-8a4b-6b4b5f38d37c
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine lot size
23ea0b50-77b5-5c36-a330-9f9dec534cb7 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
bf4552b6-5f5e-547b-a658-3b91c4a12d7c | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
dbd59763-1149-51b8-874e-d93885ac1474 | button | Acceptance | Yes,No,N/A
6d112e99-e523-57bf-a1de-fc365598b2bf | note | Key - S
8ab1b5a5-23ba-551c-9936-7df42f7d5c26 | note | UGL Key - S
21be28a7-26f7-5a0d-bafb-6a360373a43c | note | SHL Key - S
3326b6ce-6937-53c6-afa1-accc83a7260b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
83fa7cff-54c5-57a8-86d1-ede15aab5be2 | tickbox | Lot map
| checkpoint | 1.2 - Concrete Mix Design
83b8110f-5c7b-5050-94be-ec03f1917cf7 | note | Ref docs - Spec. 1121 Open Drains [Cl 3.1]
2407ff25-909a-5c2f-b194-52226b4d21b6 | note | Acceptance Criteria - Submission of Mix Design and compliance certificates for concrete constituents
818245e8-c747-5c13-a510-6da7ddac521d | note | HOLD POINT
d81e9743-cf6a-57c8-8b12-d61629348187 | button | Acceptance | Yes,No,N/A
92113e45-14b9-5e16-a026-c0d9b2c79594 | note | Key - H
0ca1712e-4eb4-5496-a250-a08433e010e5 | note | UGL Key - H
aa0597ba-42c4-58fa-b461-e688a0c71495 | note | SHL Key - H
7cbb6f73-13fd-5f54-a663-c305ddb6f748 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ae6978c0-77fd-54f9-bd59-fea3718ba871 | tickbox | Material conformance certificate
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.3 - Joint Fillers & Sealants
cd06b79e-8038-5bd3-8131-ee241899aa34 | note | Ref docs - Spec. 1121 Open Drains [Cl 3.2]
8e307295-83e9-5cfe-8786-c616626b4831 | note | Acceptance Criteria - Submission of Compliance Certificate for joint fillers and sealants
ac5b3ce6-91a4-5686-9011-1dc3f9e4d24c | note | HOLD POINT
8ed8321a-6c06-5db1-bfae-bb2b4eb35423 | button | Acceptance | Yes,No,N/A
2e89feb4-5321-5f04-b6bc-a48bb51e203c | note | Key - H
e329f753-b3e0-582c-999b-b5b90a9021d7 | note | UGL Key - H
61b370bd-a1a6-51fe-ae98-120ab2a2519d | note | SHL Key - H
70d4d324-4b50-5e5d-88f0-9e1ab4c87c49 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c56c580d-2afe-52b4-9425-1a92cb21c1ba | tickbox | Material conformance certificate
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.4 - Kerb & Gutter Methodology
2caa9e64-6524-55c7-a3fb-ab4bfc7baa50 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
50b36497-e570-5cfb-92de-1eaad8091b85 | note | Acceptance Criteria - Construct kerb and channel in fixed forms, by extrusion or by slip forming to AS2876.
a1f8ba27-9b5a-5e11-a201-6aa67f5de930 | note | ○ Submit details of method proposed including type of extrusion or slipform, concrete properties, equipment and finish.
7d7f5dbb-7663-52c0-9ba3-13ba692f576b | note | HOLD POINT
6e727449-e18f-5e1d-8d3f-6e7da7f1ebc8 | note | Notice: 14 working days prior to commencement on site
be09df0c-e116-53c8-b8b1-281bc50260ab | button | Acceptance | Yes,No,N/A
a6c811dd-1474-5e19-944c-ed6788968865 | note | Key - H
48676d81-2510-5a0d-bf2f-0fe2013a9c75 | note | UGL Key - H
6f1e5d4d-2cf0-55c3-ad92-e768a75b997a | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.5 - Underlying Lot Conformance
f4fea250-d06c-5167-b81c-f9c3f216097f | note | Ref docs - Underlying Lot ITP
646f62ea-e06a-5445-9fd2-ee3f45685908 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
42d23c79-4e3a-5767-83c8-16ba1185a139 | note | ○ Refer underlying lot ITP(s)
6c5b9bdd-eaeb-5239-9759-8e62da0a3a13 | button | Acceptance | Yes,No,N/A
04480635-2f43-578e-a13f-baefdb86d8be | note | Key - S
0a3971e7-272f-5ba6-b924-2ed25d73e1d9 | note | UGL Key - S
dee5b9b7-2191-5e48-96c8-e3c88b13331b | note | SHL Key - S
| checkpoint | 1.6 - Survey set out
77abcd3a-40c7-57c9-99ae-38ffe3f200fe | note | Ref docs - Drawings
90edc993-5b78-5c9c-a17a-53d22f3a31bf | note | Acceptance Criteria - Set out the alignment and level of the kerb
d0ea18b2-a1a5-511d-974a-6b0e92e94d48 | button | Acceptance | Yes,No,N/A
a52b960c-fb88-5c40-9cd0-17707e89b74c | note | Key - S
102abc9c-d4d1-57ab-99fc-d5c4746cbb8f | note | UGL Key - S
53dcbdbe-1de7-5ecd-8dc6-2f4d1fcf43c8 | note | SHL Key - S
| section | 2.0 Kerb and channel placement
| checkpoint | 2.1 - Foundation
33a63628-28fb-5d3a-b586-1b620df210bc | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
63d2795c-dac3-5061-a292-f561326173bf | note | Acceptance Criteria - Shape and compact foundation material to the requirements of the respective pavement course
719cb626-5cd5-53b3-8107-f6124dcaa2c3 | note | HOLD POINT
c653fc30-322b-593a-97c8-c5800c785a76 | note | Notice: 1 working day before forming
f1a849c0-6749-5a9f-823e-27e3cf2c2d00 | button | Acceptance | Yes,No,N/A
14fd45c0-8818-5a48-8966-1c98f18df920 | note | Key - H
05d45c9a-9802-5ee2-a3eb-44978f7d3539 | note | UGL Key - H
7c25a614-81d5-5116-bf78-b618f771c6f7 | note | SHL Key - H
33306e45-55b3-58aa-984b-b08a7b8bcbc0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
65d5c97a-b9a2-590a-9f22-d8fb5e7b060e | tickbox | Test reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Trial section
1ada370d-8446-589a-80e8-cc102a3d0302 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
26b8b368-3bcb-5f64-9516-f48d5912c317 | note | Acceptance Criteria - Construct trial section to demonstrate the Contractors capability of forming equipment.
48d6fd31-c229-530b-b2b1-922fda532728 | note | HOLD POINT
23b2e091-ac36-58ed-9611-ace02f7c8327 | note | Notice: To be completed on 1st section of kerb,
451548e3-dde0-50bc-b639-c2f03e1361a8 | note | 3 days prior to commencing next section
1ad99bfb-a3e6-5705-a95f-026a1a8f181f | button | Acceptance | Yes,No,N/A
f4f87e73-c47e-5dac-8cb2-dc49b5316c19 | note | Key - H
4e275058-8f0d-52c2-857e-52cfd89ecc2f | note | UGL Key - H
298ef5c2-2ae3-598c-afd0-172f7e06424f | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Concrete supply and placement
6099a512-0efc-5168-8916-ee9a0d5929f1 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
a98a0acf-5d60-554e-b419-bc3872a869de | note | Acceptance Criteria - Check docket to ensure strength and slump is as per design requirements
384f623e-a70f-5ecc-81f9-c278296ab75e | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
ef6f7f8f-c3e3-52ee-906e-634d257f68ee | note | – – – – – – – – – – – – – – – –
aa951040-7ab7-53f8-a06a-e7ee4c9c0d63 | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
e2561c21-9663-51d1-8d85-dcfddb52003f | note | – – – – – – – – – – – – – – – –
de080aa2-af0b-58a3-a9fe-96f42be61153 | note | 10 - 24 ¦¦ 2.00
dfef807b-df7a-59c1-864f-1f704815d66d | note | 24 - 27 ¦¦ 1.50
4987f7aa-d964-57f1-bc4d-afebd4958fe6 | note | 27 - 30 ¦¦ 1.00
dbeb0c66-b74d-5843-b3c8-00752defc128 | note | 30 - 32 ¦¦ 0.75
ad708570-4d65-5318-ae09-3366756a11d3 | note | – – – – – – – – – – – – – – – –
d07fc7e4-6d9a-50df-8a73-642d62790c71 | button | Acceptance | Yes,No,N/A
8212656c-6b1c-59d1-91e6-95bbb88dbdc2 | note | Key - S
501f781a-e86b-5f99-978d-954a171793f8 | note | UGL Key - S
ba9306c7-f1c3-58ed-b74b-356d9af40ebf | note | SHL Key - S
71d3fffe-840a-5970-b76e-7666239b443b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
30fa5370-6220-5269-9957-9a72678f54d7 | tickbox | Delivery dockets
| checkpoint | 2.4 - Concrete sampling
972a3878-27b4-5bed-a96b-df9d32dc3db9 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
7f65886a-c3fb-5eba-8232-ad3306f53766 | note | Acceptance Criteria - The nominal rate of sampling shall be taken as:
322636c0-f9c7-5d85-bf7b-2cb26efdd3d0 | note | (a) Compressive strength: See table below
cb5f28b8-0172-54c6-bf9d-ac0f341f8acc | note | – – – – – – – – – – – – – – – –
fe1e0e03-44a4-58b8-a0ec-a1f1c3b3f367 | note | Number of batches for each type and grade of concrete per day ¦¦ Minimum number of samples
92b1f8a1-fb27-5323-a047-80e7019f702c | note | – – – – – – – – – – – – – – – –
05869597-a5fa-5696-ba3f-4d6cbf0971f4 | note | 1 ¦¦ 1
75030b7a-9d53-5292-a2c9-4a6243e750fc | note | 2-5 ¦¦ 2
55d680fc-aa4b-572e-a1ec-31cabd965549 | note | 6-10 ¦¦ 3
7d4f0c7d-8997-5f92-afad-c005916ebd34 | note | 11-20 ¦¦ 4
5982802d-e046-5ed2-ad97-02f0189088ac | note | each additional 10 ¦¦ 1 additional
956dfb24-9854-531d-8dba-f3ee36d2ee93 | note | – – – – – – – – – – – – – – – –
973d37ca-2095-5887-9ef5-67ef14bf2ed3 | note | (b) Slump: One per batch of concrete
f9f7e46c-cd14-5ce9-bae9-7e0a8af4866e | button | Acceptance | Yes,No,N/A
cceb2992-5576-5235-bcc1-03f9f903bc1a | note | Key - S
78c9a28e-9975-548b-a28c-525b5cfc0022 | note | UGL Key - S
e8aefd4f-2b15-582a-bdde-00511421a5e1 | note | SHL Key - S
a8edbf9e-95bc-52b0-9291-698633c6768b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
834f1182-e975-5e9a-b66b-5971c9c845d6 | tickbox | Concrete pour record
| checkpoint | 2.5 - Concrete testing
428d0f33-aa8a-5907-b56c-79e0e04fd683 | note | Ref docs - Drawings
d1402de4-d388-5599-951c-7873d7992be3 | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
b850ce4b-9651-5978-8cab-23f51615a807 | note | Slump within tolerances specified in AS 1379
3d940112-e77d-5dc0-a06a-b0c6c60fddde | note | – – – – – – – – – – – – – – – –
4ff66f1c-2ed8-5051-a179-3053a58cb4f7 | note | Table 5.1 Permissible Tolerance on Slump
f863eea6-6d3b-59b3-b626-a3c5beb984ab | note | – – – – – – – – – – – – – – – –
c618414e-37d4-52f1-aa88-30676b33c984 | note | Specified slump, mm ¦¦ Tolerance, mm
9eb0fc28-06a6-5504-8d15-d01775ad831b | note | – – – – – – – – – – – – – – – –
c7bec765-8f13-5b3f-a9a7-28c3a2b4c800 | note | <60 ¦¦ ±10
28739fc6-3010-564b-88a0-f585e8fda8f1 | note | ≥60 ≤80 ¦¦ ±15
34fea913-774b-5538-9f18-35b511af98cc | note | >80 ≤110 ¦¦ ±20
d41cf3ff-b8ed-52cc-b56b-adc1b30ee0ec | note | >110 ≤150 ¦¦ ±30
fbd562ee-e237-550c-b6a5-ae0417ab9f39 | note | >150 ¦¦ ±40
cf123a84-6859-5ddd-91e4-e0e9eafe6cf3 | note | – – – – – – – – – – – – – – – –
e702f67d-19a4-5923-9f4f-f4f145b1e0dd | button | Acceptance | Yes,No,N/A
b8e24fc4-fa96-559f-a38f-f9ebfa7da4bc | note | Key - S
23125f5d-20b2-51a1-a638-04064a4d5ee6 | note | UGL Key - S
09ee832b-4b01-59e4-8a6d-55bece884774 | note | SHL Key - S
6ae1fe41-188a-52af-abe0-14c133f04590 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
60c7433d-ca22-5502-8b4b-f38df2e02df7 | tickbox | Test reports
| checkpoint | 2.6 - Finish
1a5490d7-2b7b-5385-a990-3eae7076d974 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
9d6a7ef6-e9a8-53c5-bbc8-d1fcd9594a0d | note | Acceptance Criteria - Finish true to line: The top and face of the finished kerb and channel.
98a60b8d-4142-51e8-b7c2-65a2ae91751f | note | Top surface: Uniform width, free from humps, sags and other irregularities.
2acf4b50-70aa-5e5b-b803-d070e8c3b8cc | note | Type: Steel float finish or as otherwise shown on drawings.
e80b9b2e-f2ee-5922-95bb-aec9497f0f64 | button | Acceptance | Yes,No,N/A
f6bfd661-ce00-5e7a-8ebd-1e40ef0db7ed | note | Key - S
ff3a4aae-8342-5efe-82f4-0d004e635c21 | note | UGL Key - S
016019c4-e03a-5532-918a-b792782454c4 | note | SHL Key - S
| checkpoint | 2.7 - Joints - Contraction
42a7eb96-0708-5a6a-9a5c-e3cf5447fbb3 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
11fc12f5-8533-5525-9431-33d4d7422409 | note | Acceptance Criteria - Contraction joints to conform to the following:
ab3d3907-a593-5d7b-adfe-68e768f75193 | note | – Width: 5mm min.
715edca4-25f0-593f-9ca8-421eb49089d3 | note | – Depth: 20mm
120ccc2c-145d-55f2-8e9c-a2430583acbb | note | – Intervals: every 3m for a min of 50% cross sectional area
268bb8d4-26bc-51ab-a19c-a6b592156839 | note | – Tooling: 20mm depth / 5mm width
873644a5-a92a-58b2-abb3-05dea1eadad6 | button | Acceptance | Yes,No,N/A
f1dca3d3-92fc-56e4-be6a-ea3326108d2c | note | Key - S
94d86eef-9fdd-5c84-bd18-bc1074729ffd | note | UGL Key - S
c4fde604-3358-5359-97fb-d2c429a664f7 | note | SHL Key - S
| checkpoint | 2.8 - Joints – Expansion
0c3397c9-8d12-5753-9c18-e55a3fe26141 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
f4ff86c5-9a5a-58d0-a6aa-9c899089f40e | note | Acceptance Criteria - Expansion joints to conform to the following:
9932a94e-1dac-5a21-a84e-6e51b341d9dc | note | – Width: 15mm
c2f9b354-145e-5c04-97a1-07e306d5d330 | note | – Depth: Full depth of kerb/channel
c223ced1-75d5-5f32-a097-50f9090271a9 | note | – Intervals: Max interval 15m
f97a127d-fb17-5347-9704-cd5110dd9f5e | note | ○ To be provided where channel/gutter abuts against pits, retaining walls, overbridges and both sides of kerb laybacks unless otherwise shown on drawings.
52bcbef1-51fc-51b1-a634-4a5eed97ade6 | button | Acceptance | Yes,No,N/A
cdc9e428-849a-5573-b646-7fc23e91929c | note | Key - S
3ce33a93-4232-5811-9164-9bb2428d833a | note | UGL Key - S
d8f4eaf9-4bd4-5c67-99ab-dd684d9b8da7 | note | SHL Key - S
| checkpoint | 2.9 - Backfill
4b7ba6dd-4e1a-5507-9e83-098203af3eff | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
1fd07d26-dfc0-5c9e-baf2-2a8c393e5290 | note | Acceptance Criteria - Timing: Backfill behind kerb no earlier than 3 days after concreting.
3f1f73a1-2efc-52e0-876d-dbe5ba141443 | note | Material: Granular material, free of organic material, clay and rock in excess of 50mm or approval material
d2e72fb4-7004-5849-8815-0b87f9beca82 | note | Layers: Compact in layers not greater than150mm
ddc25e45-bd59-50f4-97c0-ccd4b3eedb74 | note | WITNESS POINT
ea8fe023-fe9b-5080-b8a6-c8c301503618 | note | ○ 1 Working days before backfilling behind kerb
7ebb9358-7d59-59f2-947f-bc285dc89217 | note | ○ 3 Working days before to backfilling gutter pavement
12b37733-ba2c-5e82-85e4-a590b0bd82a4 | button | Acceptance | Yes,No,N/A
c95924a7-c561-5766-8cb6-f610974f6857 | note | Key - W
0f1a0b01-f7a0-5b27-b0f7-30b8e13b7832 | note | UGL Key - W
ad44044b-31ac-5fd6-9ea6-8874d9b436f2 | note | SHL Key - W
| checkpoint | 2.10 - Backfill Compaction
83ca36ff-91bc-5538-a776-cad6dd424233 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
544b48e9-56de-51f7-9f79-25836937bc74 | note | Acceptance Criteria - Compaction: As per pavement design drawings or otherwise 95% relative compaction in conformance with AS 1289.5.4.1
3e1d5c0f-099c-5484-b940-5b2cdbb99958 | button | Acceptance | Yes,No,N/A
21e47768-75db-5dd5-bca1-b7985b78d7d4 | note | Key - S
e0319f1e-b7a3-525e-9fff-0a7e048d3bac | note | UGL Key - S
5480c889-45e6-53cd-8607-4df0a1354fd6 | note | SHL Key - S
c8be9ec4-593b-5f9d-951c-c6b6e2aab6d1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e26cf7c4-b0f4-5b1d-a8a1-14c324b510a7 | tickbox | Test reports
| checkpoint | 2.11 - Gully Pit Tie Ins
34d95e1c-73b3-5282-bec1-d03600cd298c | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
1a0c9023-6245-5810-a98b-d37c3627d426 | note | Acceptance Criteria - Adjust gully pits or precast units to suit the new kerb and gutter profile without reducing hydraulic capacity of the pit.
3e09c2fa-858f-5336-8346-d7c6d623b99d | button | Acceptance | Yes,No,N/A
17c6f77c-4254-5ed5-bae0-1ae7cc99b6d9 | note | Key - S
69cc825d-b3b7-5487-95af-59df96935f84 | note | UGL Key - S
10049363-7b77-50d5-82d5-a6d45129828c | note | SHL Key - S
b9db0955-8138-5b5e-a908-4c3d1311abc1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6ae6be90-fbe0-5310-8cd1-ec09d7ccb77a | tickbox | Test reports
| section | 3.0 Conformance Check
| checkpoint | 3.1 - Survey Report
2c44dc5e-4c60-5e7d-906a-cd85c4197521 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.0]
e947a803-ddef-560e-9d8f-12b24c1d3847 | note | Acceptance Criteria - Survey report verifying kerb and gutter has been constructed within tolerance:
039c677e-702e-592d-adc3-752b837a86fa | note | ○ Finish levels of channel/gutter surface: within ± 10mm of design level
f879bd76-5645-58dd-ac58-fb6d5579e7d8 | note | ○ Surface deviation of kerb face and channel surface: ±5 mm from edge of a 3m straight edge, except at laybacks, grade changes or curves, or at gully pits requiring channel/gutter depression.
84b05d44-9cc4-5b55-a76b-b6148b1ce9a0 | button | Acceptance | Yes,No,N/A
ec81a7c3-3ba1-5972-b0a1-a61086d9b06c | note | Key - S
5c0b86e3-6e80-5663-a5da-d90d5ddb717f | note | UGL Key - S
4dabb84d-be00-51ef-bd18-9cc0f76fa965 | note | SHL Key - S
905d8661-4faf-559b-8585-3110f3e8019d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e47a40db-8119-52cc-9fa6-a87b7729543e | tickbox | Survey report
| checkpoint | 3.2 - Acceptance and closure of non-conforming items
c22eca06-6982-55a5-97e6-9b384a1a062d | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
3a2a7c71-416a-5c7f-b493-d815302c9f58 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
ef584c52-1766-51c0-99a9-d72bebfa7bca | note | HOLD POINT
f79b3de3-7f39-59bf-bd4f-410617543579 | button | Acceptance | Yes,No,N/A
0520858a-01cb-508c-a6e7-0eb5b7004b77 | note | Key - H
182a516b-46d4-53e0-a3cc-b88e707ba279 | note | UGL Key - H
3a0fb9b8-ca02-5e42-8704-96d5b6bc772a | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-007 Open Drains & Checklist - Rev.6 | itp | INF-HSEQ CC0375-ITP-007 Open Drains & Checklist - Rev.6 |  | 2ba1c65d-33d9-4f70-b00a-487e128eebfd
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
cb1af059-92ef-57b0-b189-d829063a61f0 | note | Ref docs - Issued drawings / Site copy drawings
d9c6bc60-adca-5c0b-abd6-848338a60a33 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
ceb05951-4058-5384-b24b-fa8732646761 | button | Acceptance | Yes,No,N/A
a9b016f3-56bb-5d9d-87e5-f82fea58eae0 | note | Key - S
3c97ec97-2afe-589b-a2f3-8393c0ea0d4d | note | UGL Key - S
055f3f57-8536-5ede-bc8a-25ec973188b4 | note | SHL Key - S
| checkpoint | 1.2 - Determine lot size
133b1472-e4a3-567c-85be-c436467c7f6d | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
9af5b6a6-1fa2-55c2-b256-9b138fa2d577 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot of map
19b13a98-3135-5798-9bc2-7cbf345335b4 | button | Acceptance | Yes,No,N/A
a5fc2a47-c325-54c2-b56d-2e775fbf319c | note | Key - S
81ccc1ad-752e-5c2b-83a0-ca10198633da | note | UGL Key - S
a2ca0971-77ac-5365-8f60-8e8d02e4e4d8 | note | SHL Key - S
11996465-0c9c-53b8-b0ce-16902be48f55 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
21187f9a-ef77-5a5a-bde6-f17ce714207f | tickbox | Lot map
| checkpoint | 1.3 - Concrete Mix Design
af6fce5d-2639-5f6e-82a3-bce33f568dd3 | note | Ref docs - Spec. 1121 Open Drains [Cl 3.1]
0aae758d-6e55-530d-b390-253e5de7ea14 | note | Acceptance Criteria - Submission of Mix Design and compliance certificates for concrete constituents
248a4d81-0bb4-5325-9195-df24c0443c5d | note | HOLD POINT
2ea28e9c-60f8-5215-8d73-da07fb600bf9 | button | Acceptance | Yes,No,N/A
3ef9a6c9-9e44-5cc8-866b-1b6c13aa3276 | note | Key - H
b8df22db-8685-581c-bc38-bfb9ecfa07cf | note | UGL Key - H
1ed66390-e1f7-5b2d-a45c-cea1ecdec522 | note | SHL Key - H
4c6081a2-b14a-55fd-9115-c72880928a94 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3c2426de-ad70-5719-98e9-5f3ccec4c91a | tickbox | Material conformance certificate
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.4 - Materials
91cba01d-a891-5a1c-89e7-abb586fa44d7 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 3.0]
eb299376-870b-5666-84da-53cabbdadd76 | note | Acceptance Criteria - Submission of compliance certificates for joint fillers and sealants, proprietary products, wire mattresses, gabions, rock fill, and geotextile.
7c4c48f5-6257-5904-866e-e80b2f97fe26 | button | Acceptance | Yes,No,N/A
944093b5-696d-5111-a5fe-78f799d18221 | note | Key - H
e0c5752f-e17e-50c6-850b-2151f450c75b | note | UGL Key - H
90ad517a-ce99-5e47-8a0c-41ebbaf0931c | note | SHL Key - H
1ea92a57-09b0-51bd-9085-3c2017dfa9fd | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2653d2db-9eaa-56f8-b1c5-ae8222602760 | tickbox | Material conformance certificate
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.5 - Underlying Lot Conformance
77b10b66-2b53-5fcf-bc0c-acf645783192 | note | Ref docs - Underlying Lot ITP
108b5f32-8fae-557f-b445-cea81627277b | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
db295ecc-494b-5a18-ab95-71501fa4ec3d | note | ○ Refer underlying lot ITP(s)
1144325b-76f6-5540-a939-c26f103ad271 | button | Acceptance | Yes,No,N/A
564b0563-a0cb-5200-8f9e-5cce844153b2 | note | Key - S
4ff0d40e-153a-5663-9db2-27294bc71584 | note | UGL Key - S
d29777b6-40ca-5f37-a902-6f1e0625453a | note | SHL Key - S
| checkpoint | 1.6 - Survey set out
0f9ccf4b-4037-5a22-abc5-f51653f385d3 | note | Ref docs - Drawings
4c8a7962-0516-5b4f-9a68-6adca57f7420 | note | Acceptance Criteria - Has the set-out alignment been reviewed by the Superintendent?
6e9f0ba2-13f0-5f5b-a0c5-f04d8690d548 | button | Acceptance | Yes,No,N/A
959e75d4-2002-57cd-a579-50a7d77352c2 | note | Key - S
a8508106-cb3b-5b1e-b23b-4dd3fb9592f0 | note | UGL Key - S
852c7b59-099c-5bf1-9d8d-259748ac4b72 | note | SHL Key - S
| section | 2.0 Open drain
| checkpoint | 2.1 - Excavation
e5e80ee7-7fe0-5695-bb9a-56c60ddec7a4 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
5e064644-c056-58b5-8752-283e9ffb1e2c | note | Acceptance Criteria - Excavate to dimensions shown on drawings or where not shown to a depth of 300mm and minimum water way area of 0.2m2
2e9cd7a1-223f-5e97-8a3b-77fa2e7fc3da | note | ○ Cross section: V-shaped or trapezoidal unless otherwise shown on drawings
9d6b7051-491f-5203-962e-2ddc7b5d4e4d | note | ○ Batter slope: Not steeper than 2:1 (H: V)
45837fd8-69d9-585e-bb80-182623af7ae0 | button | Acceptance | Yes,No,N/A
e5c6ffb0-084e-587b-bea6-9bd02e2b0a2d | note | Key - S
9ee8fc5d-bbaa-5148-a22c-ff3435979ce5 | note | UGL Key - S
bd8b0796-e20e-5a09-a741-b362357e085d | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable material
49de9350-9176-533a-afea-25c6df3af6d2 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
3e240359-f176-5029-a361-c15f30cc1f60 | note | Acceptance Criteria - Notify the Superintendent of any unsuitable material and seek direction for removal. Dispose and replace material as directed.
0b2abcf3-492b-55e0-80c7-5ca27706a9b3 | note | WITNESS POINT
b5d14a2d-a7be-5d22-bdcd-b14254be2151 | note | Notice: Progressive
db2914d5-7379-552e-a69e-ac75a0f41fa5 | button | Acceptance | Yes,No,N/A
c7757f45-74b8-5e18-84df-6134def22836 | note | Key - S
6de31129-2f10-5661-90c4-a76467581349 | note | UGL Key - W
0bd38e2a-6b19-5bef-aca2-2b22ea8534c2 | note | SHL Key - W
| checkpoint | 2.3 - Embankment
803698b6-26c4-5205-83b4-31a878145b5a | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
760fb443-4c67-5cb1-b571-9cd63cf3735d | note | Acceptance Criteria - Construct embankment in compacted layers of max. depth 150mm.
9716d428-6a4d-564a-ae6f-020810815f52 | note | ○ Revegetate the embankment after completion if necessary
435acaef-a5c9-585c-9a55-a443f7dccc4b | button | Acceptance | Yes,No,N/A
ff1e99f1-999d-574d-8e74-4d92a642fe9c | note | Key - S
e359fa76-8ae4-57ec-bd8f-80a2af2ab5fc | note | UGL Key - S
abf13b88-94d9-5062-be3a-b57ce6649302 | note | SHL Key - S
| checkpoint | 2.4 - Embankment compaction
c8c10ade-353c-519a-87dc-b106dc802567 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
293de267-5f32-5e73-9600-7a1f1bd6e60d | note | Acceptance Criteria - Compact to a density equal to the naturally occurring material or alternatively to 95% standard compaction
1d6f0899-27fd-5e6a-ba21-d0549227b119 | note | WITNESS POINT
ab2a937f-abd7-5f96-b121-5f005fe68766 | note | Notice: Progressive
58dbda59-c317-59a8-a02c-7ef9346fe036 | button | Acceptance | Yes,No,N/A
e2aef0d0-2fd0-50ff-a324-0ab4e315ac98 | note | Key - W
57bada76-1c91-569f-8a69-1c42e565e8d3 | note | UGL Key - W
2fe61b54-f180-5538-9068-b485251aa001 | note | SHL Key - W
8947e3dc-428d-5de5-bac7-e8706dbb6e1d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4a1d49e1-0ae6-5abe-8dee-8ddd54cec111 | tickbox | Test report
| checkpoint | 2.5 - Open Drain Construction
2c7873a9-1f2a-5fcd-b499-7f25b24e7239 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
003b368e-8e76-5cd4-90e5-414ad92eed9a | note | Acceptance Criteria - Ensure free flow of water and minimum grade of 0.5%. Discharge into natural depressions, culverts or pits
90fa97b9-f04e-5731-826e-a16cb76164e6 | note | ○ Compact any surface to be lined to 90% relative compaction
03c71929-b78d-5cec-8abe-679613fea72e | note | WITNESS POINT
a802e533-6177-5b61-99d5-4ecbc5292931 | note | Notice: Progressive
21a79f0f-06a1-53f5-8bbc-96a64cc5708c | button | Acceptance | Yes,No,N/A
175d45e5-e5fd-5123-a15a-1fd47e0b132a | note | Key - W
569a0b49-9bd7-59d8-bb1e-35cdc599bb52 | note | UGL Key - W
c4f39158-c35b-5614-bf3f-52b1ef4ce113 | note | SHL Key - W
| checkpoint | 2.6 - Open Drain Lining
2c25122c-635b-53de-b814-c05a889f4b23 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
0ec70c4f-f677-5366-8c8c-f14a9cc15a57 | note | Acceptance Criteria - Unless shown otherwise on the drawings use the following linings:
7381146a-af9b-53d8-b3a5-5e103744cc55 | note | – Organic fibre mat and vegetation for grades 1-5%
b3e224d3-1076-5b6a-a5c4-c7324ba3f3a2 | note | – Concrete for grades <1% or >5%
2e9b46a4-0930-54e7-ae77-d2b000bff565 | button | Acceptance | Yes,No,N/A
e763a409-26a3-5c34-965c-cd0fbcd5e38c | note | Key - S
a486ab9b-a597-5fbf-9893-33aaa84e67f3 | note | UGL Key - S
41d0cfef-efcb-5d2e-ae54-a33526a9fa35 | note | SHL Key - S
| checkpoint | 2.7 - Proprietary Channel Linings
740f63d7-f77e-5208-9cfa-87bad5560f63 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
342851de-10b7-54c0-b7df-29fb674a65ab | note | Acceptance Criteria - Install as per manufacturer’s instructions
ea9e9b93-6d62-5fe8-a3b9-cdf5fb181c1f | note | WITNESS POINT
f5fdacc7-55f7-5d30-bb6f-6b0b15b2f3c8 | button | Acceptance | Yes,No,N/A
e6fe022f-eef2-5085-9370-b64d9b4eeb18 | note | Key - W
f04a5ee3-63c1-5b1e-930b-77013699c3f8 | note | UGL Key - W
6b954ac5-cc90-5d89-a386-70abdbcb5a78 | note | SHL Key - W
| checkpoint | 2.8 - Concrete Lining Construction
15f52d11-a9e9-5e95-aad5-221ac80172b8 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
0c7fb856-8a44-57c4-9c4f-ccfddd4af81a | note | Acceptance Criteria - Minimum thickness of 100mm or as per design drawings. Free of humps or irregularities
d462b4dc-9ce9-57b6-af64-e53a131b2ddd | button | Acceptance | Yes,No,N/A
2cc5dad1-a9b4-50ee-bf2a-51b721896fcd | note | Key - W
f1a671bd-169c-5518-affb-da523fed4aad | note | UGL Key - W
1803d635-5a1b-5cb5-be4f-9149796a7c64 | note | SHL Key - W
| checkpoint | 2.9 - Concrete Lining Weepholes
4dd3f88b-8c8b-5ff6-9fff-527c2caf52f0 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
af382a64-9af7-5ce6-8d5c-3a8bc166010b | note | Acceptance Criteria - As per design drawings or at 2m spacing in non-horizontal elements
2f03c3d9-aeef-5e92-90bf-d7941b0577d5 | note | WITNESS POINT
b89ba3d3-dd7c-50a5-8b4f-e520b55fc369 | button | Acceptance | Yes,No,N/A
70389a67-3578-540d-9380-dc2358532fbe | note | Key - W
1258e541-163d-5559-b609-83e011a7a458 | note | UGL Key - W
d34ab789-19c4-53ab-b1e2-9fbccad0db9f | note | SHL Key - W
| checkpoint | 2.10 - Concrete supply and placement
ef90a5ec-3c23-5a4f-b221-1c777a298a76 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
78a42a42-e8b5-5bb0-9def-9be3836bc91f | note | Acceptance Criteria - Check docket to ensure strength and slump is as per design requirements
09d18e90-7a07-5dd4-afcd-7d9d89353098 | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
db29c4e1-65b5-584f-9139-880908734a9e | note | – – – – – – – – – – – – – – – –
d1d6bb38-debc-53e0-ab13-4dc48c1001d2 | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
3cba222e-57f8-571f-a0f6-6fe534497194 | note | – – – – – – – – – – – – – – – –
36dddae3-ec22-5f8a-8cd9-28c37f78a39a | note | 10 - 24 ¦¦ 2.00
e31da2ba-ec86-5047-93c7-96dbab6eabac | note | 24 - 27 ¦¦ 1.50
8bbe6dfa-f3a2-5218-a79a-300fb4a4b298 | note | 27 - 30 ¦¦ 1.00
e2cb0770-a07c-5a14-9685-c7d30ed978c8 | note | 30 - 32 ¦¦ 0.75
33db4320-0fac-5aa8-9060-d51acaa50235 | note | – – – – – – – – – – – – – – – –
a2a2d937-b253-5849-a534-ac91d84abf31 | button | Acceptance | Yes,No,N/A
4f977cdb-b95a-50e2-ad4a-fe99d17e023f | note | Key - S
d8b505b8-9016-52a7-930e-7aea313bca28 | note | UGL Key - S
6aace5a1-e7a6-574a-aa48-7d4241e09a97 | note | SHL Key - S
fba6dafc-8587-508f-97bb-f2d7b2187e00 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
afbf4759-886e-5b8c-abfa-f8fd3225eeeb | tickbox | Delivery dockets
| checkpoint | 2.11 - Concrete sampling
e4e63284-81a5-5027-ad09-43dcf9a9f88c | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
dee8856f-d3c1-535f-b885-326e8409b279 | note | Acceptance Criteria - The nominal rate of sampling shall be taken as:
f76a399c-d92f-5663-81ed-3a22cc49cf5a | note | (a) Compressive strength: See table below
b262d1ee-1a07-5ab6-8fb9-ac430dffb779 | note | – – – – – – – – – – – – – – – –
aded2ee9-e894-5d9e-8478-369c1899cfd8 | note | Number of batches for each type and grade of concrete per day ¦¦ Minimum number of samples
16867d9a-e97a-5a51-a7b0-ed797b968621 | note | – – – – – – – – – – – – – – – –
d894025f-7b70-5c75-a7dc-bcced2fa7be1 | note | 1 ¦¦ 1
8e3fab72-322c-58a8-b181-fb63b62b76f3 | note | 2-5 ¦¦ 2
7a19848f-21bb-5e09-a23f-390aa95dad79 | note | 6-10 ¦¦ 3
ab1a25b7-edfe-5638-882d-974ec3fdc9ce | note | 11-20 ¦¦ 4
f3ce4932-e9ae-532d-9d50-baf8867b7491 | note | each additional 10 ¦¦ 1 additional
e7b7c8d8-aa05-5c11-99a7-2a25ef76c225 | note | – – – – – – – – – – – – – – – –
cb9276d7-4432-5f5a-867b-70e19a4a55f4 | note | Slump: One per batch of concrete
c00ff1c1-f157-5980-b74b-79b51b8a8668 | button | Acceptance | Yes,No,N/A
90769fbe-ee68-52ae-be12-cd72546e813e | note | Key - S
c2da4c6e-7f26-5324-a371-bbfee19dab76 | note | UGL Key - S
2db1aa6e-5323-528b-bf13-7abce2dd1b6d | note | SHL Key - S
e4da179d-2f79-50e7-96b5-79fa27727707 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ad586d73-5d78-5dfb-bc28-f2b108725273 | tickbox | Concrete pour record
| checkpoint | 2.12 - Concrete testing
93a418a7-ea30-57a6-9f66-2407878af263 | note | Ref docs - Drawings
3ff747eb-936e-5da3-b0f6-1e202ca67ac1 | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
85b2be7e-64ef-5dfd-86f1-8303431a2806 | note | ○ Slump within tolerances specified in AS 1379
bc9f60ef-a480-5f83-ad08-0d7853fa1e81 | note | – – – – – – – – – – – – – – – –
cebd25fd-453f-54b1-840c-917c8bceeaaa | note | Table 5.1 Permissible Tolerance on Slump
3b78b4a4-dc94-50bf-b156-ee5fdd849993 | note | – – – – – – – – – – – – – – – –
18a61c8d-be18-5904-b935-e7d4f7604c51 | note | Specified slump, mm ¦¦ Tolerance, mm
c1c51386-4b3d-5f31-b68f-71e393823386 | note | – – – – – – – – – – – – – – – –
4fa20b7b-98b7-5839-9dfc-aa37200c86ac | note | <60 ¦¦ ±10
d6f81e58-64d6-582a-b366-be1e45d67225 | note | ≥60 ≤80 ¦¦ ±15
bb5c8c7f-b789-57c8-bbcb-b10bb9546dbc | note | >80 ≤110 ¦¦ ±20
5b4ac936-dd49-54bd-bacc-01a13b3ed015 | note | >110 ≤150 ¦¦ ±30
844e13c0-7ca5-5410-8a6a-40a45c7378c6 | note | >150 ¦¦ ±40
a7308dda-9e35-572a-98e1-c95648f93a1e | note | – – – – – – – – – – – – – – – –
ad063fb4-d9eb-5d9c-9a61-20e95f5d9ab2 | button | Acceptance | Yes,No,N/A
27a9add7-677a-52b0-8350-9f68369e8bab | note | Key - S
37b2bd35-1d36-5890-8739-da8b3e7f6276 | note | UGL Key - S
5b72b9b2-f9ba-541c-aa41-677d24223d88 | note | SHL Key - S
f9a8b9cd-02bb-5249-a0f6-ee6836cfd3c8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
faba44b9-0931-5163-a8ac-3e4eb3e3cae6 | tickbox | Test reports
| checkpoint | 2.13 - Joints - Contraction
99579e45-ba05-5c35-8c79-3750b2021a0b | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
009dd210-fe5b-50e6-92f8-6d0fa152ceff | note | Acceptance Criteria - Contraction joints to conform to the following:
7ae65602-788d-5d6f-8266-39255e111bea | note | – Width: 5mm min.
366425e8-351c-572b-9c63-8ea29bfd3731 | note | – Depth: 20mm
02fd72fb-85ec-5f74-b178-980862d6652c | note | – Intervals: every 3m
6fd6b844-5f67-5ec6-9aaa-eab71c88adf6 | button | Acceptance | Yes,No,N/A
6420ad94-59dc-5d21-bcc2-84faecb3f042 | note | Key - S
9855a15d-ab68-51ba-a9e8-9cea0e3294ef | note | UGL Key - S
b68260f4-d8dc-5b24-ba36-1b8208efdcdb | note | SHL Key - S
| checkpoint | 2.14 - Joints – Expansion
2ded28ea-3428-5654-a3da-db97da144d73 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
5d95604e-d29e-59dd-9c1e-38f98f8cd3aa | note | Acceptance Criteria - Expansion joints to conform to the following:
68766d70-8e3e-5e26-b6bd-d0003e202750 | note | – Width: 15mm
3cbd8c56-533f-5392-8875-be11306401b8 | note | – Depth: Full thickness
066e7660-3dd2-5eb7-ad5f-59f45d3b9ec4 | note | – Intervals: Max interval 15m
fc4d87f8-27e1-5f39-b556-b920a256ab77 | button | Acceptance | Yes,No,N/A
2fc91c3c-1168-52d8-8226-9d3fb4514b29 | note | Key - S
f4cdeba9-c322-5d8e-a7cb-0ddb6f5c97e3 | note | UGL Key - S
2b449869-12a1-55cd-82ae-c10bd71f52e0 | note | SHL Key - S
| section | 3.0 Rock Mattresses and Gabions
| checkpoint | 3.1 - Foundation
a4c08c9b-4d96-5edb-b9e0-288d55d4ecd4 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
1e5b09b5-a8d6-5577-b9c7-d6bc96ec6d6d | note | Acceptance Criteria - Shape and compact foundation material to 95% standard compaction
668f7ef9-5b5e-5804-85dd-fa294051e70b | button | Acceptance | Yes,No,N/A
8cce07a3-9927-53df-aef0-e11de59af3f4 | note | Key - S
ebb23c3d-46f7-5a59-a76a-f3903cdf3ee8 | note | UGL Key - S
0030be6d-de02-5afc-95ce-1aa97fac8ee8 | note | SHL Key - S
70c74a33-d48b-5b89-ba87-3be0f961fce7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b4d577d0-866f-55ed-80f4-3810023678d2 | tickbox | Test reports
| checkpoint | 3.2 - Geotextile
3710c70b-5c32-53d8-ad88-2c49173e4a4e | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
8b1b96ca-81a0-500d-91cb-9da6ab8eb97d | note | Acceptance Criteria - Place geotextile between the foundation and any wire cages
af18b41b-9880-5fde-ad63-a86f01f1f1d9 | button | Acceptance | Yes,No,N/A
d0cf404b-bafa-5994-bdf4-4320e2723c75 | note | Key - S
24ef7cfa-3420-53bc-8bd9-f8d7fabca122 | note | UGL Key - S
1b145bac-e834-56a6-94ea-f3b05ac3329b | note | SHL Key - S
| checkpoint | 3.3 - Assembly
d98c3284-3fa3-5299-89b7-6da3fb2db71c | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
c425f4a3-8a5e-54f9-8fb9-d48a7e477df5 | note | Acceptance Criteria - Assemble and lace the rock mattress or gabion cage as per manufacturer’s instructions.
45a9e933-66d3-5919-aab8-1f7ab51ed598 | note | ○ Secure the end of a new cage to completed works or with galvanised star pickets driven in to the ground.
f8012629-57ea-59c2-9490-1d3155eae0d3 | button | Acceptance | Yes,No,N/A
dce0694c-0792-59f6-b40d-c0dc9afd1230 | note | Key - S
0381c0e8-29c8-572d-8359-a3213833d3c5 | note | UGL Key - S
f584064e-3221-572f-bc58-6f55afe3c47b | note | SHL Key - S
| checkpoint | 3.4 - Filling
6fbe8148-2605-5423-8e92-445b1be2eeb4 | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
a18a75d5-e23b-5567-b764-fb44d287a83b | note | Acceptance Criteria - Fill boxes whilst under tension and only release tension once fully laced. Ensure cages are fully filled and uniform.
d015c483-1019-59b2-8fd5-bbe80d510ef8 | button | Acceptance | Yes,No,N/A
8147712b-477b-5350-afdc-9d5a87d4544f | note | Key - S
c33e72fb-44a2-5c97-8a55-4ad7314d933f | note | UGL Key - S
fe7764ec-0e30-5534-a00f-b36c2a430e73 | note | SHL Key - S
| checkpoint | 3.5 - Completion
470d146e-e51e-5455-bba6-86e43fea0e6d | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
79d85a87-a08e-5a8a-9619-faeb5f5e5fdb | note | Acceptance Criteria - Inspect rock filled mattresses or gabions upon completion
ad3c0801-f9ec-5bf2-b998-20b8e5617bbc | button | Acceptance | Yes,No,N/A
bc4086e5-10bb-5d5f-bb6c-4cd6be78388c | note | Key - W
65255746-a61a-5c44-866a-2c81d163e113 | note | UGL Key - W
90aea2d4-8679-5cc0-b089-5cada4d82309 | note | SHL Key - W
| section | 4.0 Conformance check
| checkpoint | 4.1 - Survey Report
643d6ab1-e5bd-575e-b415-8039be7600fb | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.6]
f563f1b6-bed7-5eed-a4b3-ce1eea012d2a | note | Acceptance Criteria - Survey report verifying open drains have been constructed within tolerance:
167f9eac-bf83-549c-acb3-2d2336f35a20 | note | ○ Finish levels of channel/gutter surface: within ± 10mm of design level.
c6c8c8a0-c21a-5c6a-953a-a3bb45e19bc8 | note | ○ Surface deviation of kerb face and channel surface: ±5 mm from edge of a 3m straight edge, except at laybacks, grade changes or curves, or at gully pits requiring channel/gutter depression.
6f683276-58e1-571f-b447-caa29b89e1a2 | button | Acceptance | Yes,No,N/A
83f5d7b1-be53-59fe-9520-2d7b434536f3 | note | Key - S
8927fafd-175f-5f68-a4c8-091264bb2f85 | note | UGL Key - S
b5aead4e-812c-5b83-b4b9-b33b171ad8d2 | note | SHL Key - S
c1f60aef-fcf8-5d69-a5dc-9348380de1fe | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
30a9d259-efaf-5ed1-aa57-8949443f3052 | tickbox | Survey report
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
20b71d5d-ae83-5539-aaf0-6167d0877637 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
a679a8cb-8e00-5e3e-a7aa-43494bea5307 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
f0311737-4b34-5d44-8ec6-32eb37a2ae0b | note | HOLD POINT
c067e98e-e4e6-5b46-ae85-49f42258e8b2 | button | Acceptance | Yes,No,N/A
a968e1ad-61c7-5124-80f0-ce16d93e5b12 | note | Key - H
8d1f0790-8f5f-59af-888b-e270521a1925 | note | UGL Key - H
92fc4f6f-7243-5843-bc42-61508c34af67 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5 | itp | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5 |  | 473bd0bf-a46e-4e88-bb8d-8d19f9a5445d
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
7d430a6f-2ca3-56de-b8fd-79cec8d4de87 | note | Ref docs - Issued drawings / Site copy drawings
059f6269-66e9-53f2-bc66-f362e7da08e8 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
ebc1b194-60e9-5b26-aca4-f2dec5a9ef86 | button | Acceptance | Yes,No,N/A
c0ee44d2-facc-5d38-b4a4-48c943157346 | note | Key - S
b3baaea6-0642-5888-a75a-9efbf1be5ea4 | note | UGL Key - S
a590d0d6-f468-51c3-9dd7-dbc88e2523bf | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
92feb3f5-a4c1-507a-8b1b-d9ad88352147 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
4e28a19b-8d63-51cf-ac93-abb32269243d | button | Acceptance | Yes,No,N/A
86ec8f9d-e1ce-5d7b-85e7-f2070a5bc1b2 | note | Key - S
85a65a63-cd3c-5866-81cd-c3ca119daa32 | note | UGL Key - S
70d09dc7-cba0-5204-b551-fa546710fa16 | note | SHL Key - S
fbbbd502-4279-512a-81cc-7d6c3bc94640 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
02d27176-fe56-5c83-94f5-fa4f750a0cf5 | tickbox | Lot map
| checkpoint | 1.3 - Underlying Lot Conformance
5a11f012-608e-58bf-9665-7a74364258a1 | note | Ref docs - Underlying Lot ITP
f4a5b1d4-559f-52b5-b1b4-74b0a052c1be | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
96a6f65d-93c1-589b-8f08-16c1574b8e5d | note | ○ Refer underlying lot ITP(s)
f54821da-8ff8-5130-b42b-e0aa2886aef2 | button | Acceptance | Yes,No,N/A
ba6987d2-8994-5b88-8068-9dbad17723e5 | note | Key - S
65be1dea-4cb9-5f56-a851-9a30671bc192 | note | UGL Key - S
e64a4717-a8fc-5dee-ad0a-d5a210845295 | note | SHL Key - S
| checkpoint | 1.4 - Set Out
1abc94a0-14a5-55c4-8768-46317993bbbe | note | Ref docs - Drawings
f0525d99-6a04-592f-9fd7-03589c11a104 | note | Acceptance Criteria - Peg location of proposed underground services with levels from pit to pit. Peg property boundaries
43935b5b-ffb0-5be1-8308-ca317487c195 | button | Acceptance | Yes,No,N/A
54bd7d20-a341-56c1-a18b-6a4ffe615be4 | note | Key - S
aa3bbcaa-f7b9-5277-9fc4-500b9f7c86f1 | note | UGL Key - S
2f1ff0a4-d1c8-5cd7-9215-9f8ba90936a1 | note | SHL Key - S
| section | 2.0 Material Conformance
| checkpoint | 2.1 - Conduit Supply
16147b78-2330-525f-9c65-545f8ab36bcd | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
b2c556aa-71ae-5e10-b1bc-da0dabba971f | note | Acceptance Criteria - Conduit system shall be a Category A wiring enclosure for an underground wiring system to AS/NZS3000 and AS/NZS 3013.
b3fdfe6c-fb91-59c7-b924-676275e72563 | note | ○ No corrugated conduit or similar shall be used under any circumstances.
62c9206d-dc6d-5400-b355-6322e2210e78 | note | ○ HV & LV Conduits: Shall be orange heavy-duty uPVC, sizes as per drawings otherwise min 150mm (HV) and 100mm (LV) to be used.
786b8562-aa30-57ab-b348-5d78deb2c340 | note | ○ Comms Conduits: Shall be white heavy-duty uPVC, sizes as per drawings otherwise min 100mm to be used.
34e9d706-1a20-55c5-8603-75f54fd13ae2 | button | Acceptance | Yes,No,N/A
41d038b3-c53b-55ee-83d7-bb8bddbb68f9 | note | Key - S
bc9e6b36-f57b-5271-84e4-09f9f15848f0 | note | UGL Key - S
df982772-33df-5549-892f-8b7dd2f761a9 | note | SHL Key - S
6b198f2f-5dff-5ed1-9d88-c841bbdce317 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7412b1cf-55f8-5992-8b49-a9805b48bd58 | tickbox | Material certification
| checkpoint | 2.2 - Pit Supply
1289a539-c38a-5d98-877e-edcdf3c2fc8b | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11]
7e58a724-3b8d-5ade-bc7e-0666a6c66aa2 | note | Acceptance Criteria - All pits are to be reinforced concrete complete with concrete lids. All lids shall be gatic with min load classification of Class D in accordance with AS 3996.
731a5e9f-4a9b-5b0f-b20b-5241cbc53006 | note | ○ Pits lids shall be fixed to prevent unauthorised access.
d539c4d7-f83d-52f9-9384-b52175a3dd3f | button | Acceptance | Yes,No,N/A
e914ea11-b83e-5499-b59f-54bc3e81f833 | note | Key - S
49f0769c-34f3-5841-bc24-9c5d22e1b296 | note | UGL Key - S
5ce04435-10b9-51ef-910d-3c628ab130bb | note | SHL Key - S
f51fa354-3672-5952-89f9-867716a5b685 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e23588e0-4039-56bb-917e-d5ef4fd88375 | tickbox | Material certification
| checkpoint | 2.3 - Embedment material
cbae44da-45ab-518f-bca7-e2374dd7d3a5 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6, 6.11]
e1b14b72-098b-5496-abc3-0c5e47805b7d | note | Acceptance Criteria - All conduits shall be surrounded by a min of 100mm compacted sand unless shown otherwise on the drawings. For power conduits, this compacted sand must have a min thermal rating of 1.2°C.m/W.
668a40c2-2fc7-58a6-9b7a-af1336ab4b0c | button | Acceptance | Yes,No,N/A
37dab6f5-ece6-5908-8bd2-bb1c0444628e | note | Key - S
1fe021c0-14ae-5ad4-9c30-05c8abfcfe64 | note | UGL Key - S
70909ef9-f931-5d0f-a027-b2a35ea26ba1 | note | SHL Key - S
459ec7eb-6050-58ec-8461-1ba61188a28d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
191aa402-7284-58cd-bd01-fde69a648477 | tickbox | Material certifications
| section | 3.0 Excavation, Installation and Backfill - Conduits
| checkpoint | 3.1 - Excavation
bed79d57-6067-5493-9412-4efa24a9b0ae | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
ce606fb7-b226-5f48-a2ee-4d75d1be7d93 | note | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
66f76344-c1b2-5d60-9fca-8e545d82a56e | button | Acceptance | Yes,No,N/A
43119d15-4a7c-5123-bec2-f0ad250a4453 | note | Key - S
e8692ce6-582f-568e-9f0a-51e51b5d6a0f | note | UGL Key - S
92e5255a-9252-5a53-ac97-ee2764b6f5cc | note | SHL Key - S
| checkpoint | 3.2 - Place Bedding
8bd52178-c5c7-560f-a79c-27ae647f01eb | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
e9648bfe-ebd0-5270-8382-79772878f540 | note | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
f8314024-4da0-59ce-b0a5-2307ace2ebdf | note | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
821a90ed-8707-5d23-a4c3-09c36817c76c | button | Acceptance | Yes,No,N/A
a53b5118-cc90-589f-a719-c7715e0a7fe9 | note | Key - S
75d18ce6-6f05-5c5f-8986-552d16a63d47 | note | UGL Key - S
6432f6d0-a674-539e-b78d-d78d6ca25c12 | note | SHL Key - S
| checkpoint | 3.3 - Conduit Installation
cd98c5a5-017e-5d83-b1ed-115c71e60489 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11, Cl.17.1], Drawings
0aa726f4-4c4f-5be2-8e8d-928b344733a1 | note | Acceptance Criteria - Conduits to be installed as per the drawings in a straight line where possible and with no changes in diameter between pits. Joints to be sealed with a solvent cement or glue as per manufacturer recommendations.
c303aa32-6be4-582b-90a3-07beb8b3c8bd | note | Minimum separation to be 150mm for DN150 conduits and 100mm for all other sizes unless shown otherwise on the drawings
fcaac8d9-a4cb-5cb8-94e2-ba3b7b58fb0b | note | Minimum depth of cover to conduits to be:
9928cb2f-eaf4-5b24-bcd7-bd8f9e6a5d48 | note | – 300mm for COMMS
c38a3967-76f6-50f8-92d5-6ddd886c3c79 | note | – 500mm for LV
47688c84-8db3-50bf-bebb-92e3aa9d4414 | note | – 900mm for MV
e6ffa39a-8341-5a14-b0aa-0a23e0d2227c | note | WITNESS POINT – Prior to Backfilling
0298276d-1f0b-550a-add7-7d6bafa22dc3 | button | Acceptance | Yes,No,N/A
fe0f87ab-6c3d-5c37-9d50-06275d6a58d9 | note | Key - H
fe174e6d-ee72-5a24-a3ff-2ef50f96f6d8 | note | UGL Key - W
ac25e264-d4a3-571d-a513-3eab21496f79 | note | SHL Key - W
| checkpoint | 3.4 - Conduit bends
eb286f2c-aaf9-59da-93a1-2e60ef4bec51 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
832ed589-f863-545c-8602-28b7bb8ba020 | note | Acceptance Criteria - All conduit bends shall be long sweep bends with a maximum 90-degree angle.
90d95227-d893-54a8-b12f-a61e5a93682a | note | Min bend radius shall suit the min cable bending radius of the largest cable in the conduit and generally not be less than 1000mm.
2e1cbf9e-dbf2-537a-b6b3-47784ded7453 | button | Acceptance | Yes,No,N/A
439e708e-13b4-5b12-a2e9-2b398b9c8a5f | note | Key - S
88d26208-5e03-5822-8574-332bb19be397 | note | UGL Key - S
94f560f4-ade5-55b2-9ed6-2966fb7ea552 | note | SHL Key - S
| checkpoint | 3.5 - Marker tape
835b1b95-de99-5b7a-a011-41409f50d662 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.9]
c62a70cc-2447-5912-97ab-6790cdc19480 | note | Acceptance Criteria - Orange Polyethylene marker tapes, 150mm wide and 0.1mm deep, shall be laid in the trench directly over all underground conduits at approximately 50% of the depth of cover. The tape shall be marked with the warning:
e55aa324-2f54-59ee-81a2-78d86cb9e05d | note | “WARNING BURIED POWER CABLES”
d7fb8d2f-4b31-5db2-909f-eaad490547c6 | note | or similar in black letters that will not fade.
a709e204-90d6-5e81-8920-1d8a74d97e04 | button | Acceptance | Yes,No,N/A
cdb2f9cb-4ecb-55ae-b13d-e0d30234fc46 | note | Key - S
473a51ed-3f9c-59d4-b311-a83b3d9fe3f4 | note | UGL Key - S
e6ae85b0-aedb-5ae1-85d1-5d653e8d83be | note | SHL Key - S
| checkpoint | 3.6 - Backfill - Conduits
81278cda-0962-505d-80ed-3517d8f49588 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
75a67e55-2db8-51f9-a03b-342430d7d62a | note | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
c405819e-9ce6-5900-88bf-0d0f4bba6a93 | note | ○ Layers not to exceed 150mm compacted thickness.
a6c82b98-b1c1-5ee7-903b-75e3ee462d2a | note | Key - S
80f7812b-8a29-5cf5-8a9a-b969cefa28f5 | note | UGL Key - S
ce990f00-50ea-5b2d-afbe-9bc0fa408fad | note | SHL Key - S
| checkpoint | 3.7 - Compaction
c0bf998c-5026-5256-8c75-9ddf24d8e05f | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
75057d40-e99e-5561-8f19-c7a996449f30 | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
0f0cd3d7-38cc-5060-be9f-9fc5f21e8743 | note | – 95% for foundations
e1300c7b-d0ee-5db1-8a07-b2723c510033 | note | – 70% for conduit encasement
f2868c86-9443-5ec1-8746-dc47472782aa | note | – 97% for select fill areas
71be7640-0baa-5bee-b77e-53b6cb6c3e95 | note | – 92% for general fill areas
c5b2d35e-22b5-5c3a-9f18-f8d9ef122dc6 | button | Acceptance | Yes,No,N/A
89dd4925-520f-5af2-bd7d-48587975c7f3 | note | Key - S
ab0172e0-1f56-576d-9b0c-3455acb29ba7 | note | UGL Key - S
43af223b-ba38-54c1-9421-5621f26e3355 | note | SHL Key - S
2a3527a3-1990-5d4c-b05d-631d5ff6d780 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bed4de77-e7cd-5819-95e1-1a14248f88e3 | tickbox | Test reports
| checkpoint | 3.8 - Cable Markers
f11380c1-0b15-52b5-94e5-81816ef230ab | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.10]
9c6f56ad-e928-5df2-b3f5-b2a5337d0251 | note | Acceptance Criteria - Install Concrete Cable markers on the surface of all underground cable joints, at every change in direction, and on straight runs at least every 30m.
9c9d63b0-a7ca-5b3e-a2fb-add0755d2b52 | note | ○ Markers to be a 400mm square and 100mm deep concrete block with a brass label attached. Label to identify conduit type and direction.
24d0e565-7955-543b-afe5-69c4b32bc75e | button | Acceptance | Yes,No,N/A
8f115051-aeb0-531c-b762-796695018241 | note | Key - S
3df851a6-e636-5661-859a-a7c8421a3c18 | note | UGL Key - S
a0abeba3-c463-5578-b032-418744d25831 | note | SHL Key - S
| section | 4.0 Excavation, Installation and Backfill - Pits
| checkpoint | 4.1 - Excavation
2de300ac-42b4-5d8a-a9c7-cab37ae38691 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
2fdc59ef-440c-56cd-8d9a-cc9d68bcc2f0 | note | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
9b946bdf-4279-50fb-827d-ed2bc6ca2786 | button | Acceptance | Yes,No,N/A
94db1377-1160-52ed-ba77-0982ab20af68 | note | Key - S
018a0ecb-8aba-5713-aa16-b5f9b630e8c4 | note | UGL Key - S
20259e89-42ba-53e1-b13c-fcbf03d9025b | note | SHL Key - S
| checkpoint | 4.2 - Place Bedding
dbcf26d5-140c-59e2-8061-e214fc88e208 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
b75b1195-4f20-566a-9253-ee848935841b | note | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
cc3fc3f5-252c-5cbd-bfcc-126af905c18c | note | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
7218d8ca-fc1e-5fa2-9ede-e87a8509d0bc | button | Acceptance | Yes,No,N/A
e79a8dc7-cab7-5900-884f-224c0385752a | note | Key - S
90242fb2-1616-5258-8544-d1945344e27a | note | UGL Key - S
44c2b3d8-9270-5001-af5f-5cc00a1d40b8 | note | SHL Key - S
| checkpoint | 4.3 - Pit Installation
ad2a4141-fd2d-50d8-9cbf-1d9e44700b5d | note | Ref docs - Drawings
eeee6359-8934-5c5d-9c26-a7eda004377e | note | Acceptance Criteria - Pits to be installed as per drawings and manufacturers specifications.
c3771c3e-a71a-5029-95a7-85c2262fa45c | note | ○ All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall.
655222b2-dbfa-5576-be40-1f3236df6a7a | note | ○ All pit joints and bell-mouths are to be mastic sealed or glued as per manufacturer recommendations.
b18f2a3b-eee3-5fec-bc74-42b32bcd8579 | note | WITNESS POINT – Prior to Backfilling
5393e6bb-5dee-5c5a-9f7a-9f4a63c7552b | button | Acceptance | Yes,No,N/A
b77782a1-c967-5ddc-8354-29dbc4ed5a45 | note | Key - H
6c4e54e4-f35f-5a6b-b515-85e4c46247e2 | note | UGL Key - W
935dd72f-959a-5146-a6a7-06ea4a42505f | note | SHL Key - W
| checkpoint | 4.4 - Pit Drainage
1d832f44-769e-5196-af0b-f41fbae18216 | note | Ref docs - Drawings
c291b9d6-344e-546b-8dd7-4e63a0b1884b | note | Acceptance Criteria - Pits to be installed with a drainage system as per the drawings to prevent pooling of water
3863c267-e66f-5fc5-a163-ebec5e7665f0 | button | Acceptance | Yes,No,N/A
54fc5548-1e4c-52ea-894f-36247b533460 | note | Key - S
0980740c-f1e3-5c13-98b2-d71a78da8d5f | note | UGL Key - S
0d3aeee4-b766-53e1-a5c7-2b7d428b926a | note | SHL Key - S
| checkpoint | 4.5 - Step Irons
ea66fe06-2643-503c-969d-597fe4c7f0ee | note | Ref docs - Drawings
d0728c1d-bc98-5523-a7dc-45357b31e67e | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
11427d63-49cf-52d6-9b66-fa814c4225bc | button | Acceptance | Yes,No,N/A
a7b987a0-410f-529b-a186-d07692bcc412 | note | Key - S
f5b768ac-11c8-515c-be77-c2ce9452baf0 | note | UGL Key - S
27f98708-d0bd-5209-9ed2-989156743aa0 | note | SHL Key - S
| checkpoint | 4.6 - Access Covers
cbefda3f-ba82-5d50-80c4-a09c8431e48e | note | Ref docs - Drawings
db688475-2924-5d7a-b615-a1fbaf41952b | note | Acceptance Criteria - Pits to be fitted with Class D Concrete Infill Gatic Lids to AS 3996.
ef21cea4-440c-5c93-9004-736f87268b10 | button | Acceptance | Yes,No,N/A
21d76149-1da3-5779-9a44-8b11ea9ce3cf | note | Key - S
87e66778-ec5f-5ab0-b3f7-a9e7409d6387 | note | UGL Key - S
3c237bd9-1940-527d-9df9-85bdbcb2d5b9 | note | SHL Key - S
| checkpoint | 4.7 - Brass Marker Plates
0c088bb1-3009-55fe-bbeb-65398ca3b63c | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
da43766c-a59c-5bbf-8112-a9d19a48dd24 | note | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
a1d14a4c-c9a8-5a5f-86e1-ad4653ac5683 | button | Acceptance | Yes,No,N/A
b652b5c6-b62e-503e-bdb6-951ef6822506 | note | Key - S
d8293475-6968-56f0-8814-12650fcc3064 | note | UGL Key - S
56a521c2-eeb3-5719-acae-6336f1089753 | note | SHL Key - S
| checkpoint | 4.8 - Backfill - Pits
84fd2348-ca56-5607-924e-e5b9804d7abb | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
7737919a-8946-5729-9cb3-8259db9bc831 | note | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
d2eee582-9b80-5417-b831-0011c0744cce | note | ○ Layers not to exceed 150mm compacted thickness.
6d69e21d-489e-5d27-a0cb-0dfbb1a6b575 | button | Acceptance | Yes,No,N/A
07a7861e-58de-53a4-bfdc-e5aa04ffc8de | note | Key - S
0d0ef195-98d1-58fb-9698-fccb77b67c63 | note | UGL Key - S
149a03eb-0fcf-53e0-9c69-3cf0467bf042 | note | SHL Key - S
| checkpoint | 4.9 - Compaction
0be40808-bbe0-57d2-ad79-7414bc5e37cc | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
04900907-d585-515b-a487-57165d16f9a4 | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
893efe38-083a-5825-86c7-4a02170b5c25 | note | – 95% for pit and conduit bedding
e2f4f3fc-748f-5072-b836-6bd05ecaa286 | note | – 97% for select fill areas
bcda238a-f31c-5943-9443-5628d440958c | note | – 92% for general fill areas
0e5cc0f6-951f-51cb-842c-17c94cdec072 | button | Acceptance | Yes,No,N/A
048c5ecb-9eb0-56b3-a66a-f6e40bb3678a | note | Key - S
f0bdcfdc-f1d6-50fa-8602-489c2f5ea4ba | note | UGL Key - S
a35bb144-49b9-5194-b1f6-e553b36d8c18 | note | SHL Key - S
0cffa7b6-d642-57c9-8e46-6bf400e2d41a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
90779270-c252-5be0-b862-60d875e92e53 | tickbox | Test reports
| checkpoint | 4.10 - Rope and Mandrel
4c8af62a-cada-5c4b-8bc4-62efef1849ab | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7.5]
774ff7ed-a9e4-593b-be24-1ce2654eee31 | note | Acceptance Criteria - Draw ropes or wires to be installed in all conduits that will require further cabling.
7a2cb33b-6a9c-5c5c-a3b2-1dae4c2afe7c | note | ○ All conduits to be mandrel inspected prior to cabling to check for blockages.
459a8f82-bacb-5162-a4ac-0239b64a5dc7 | note | WITNESS POINT – Prior to Cabling
dac4c2bb-5447-5acb-ab50-24cc2e6b747e | button | Acceptance | Yes,No,N/A
6df40e9d-85a5-59a3-aaab-c5cce396839e | note | Key - H
f3e0e90c-d7fd-516d-abe0-d379d13a6df9 | note | UGL Key - W
3877ced6-2f91-581c-8a25-9f72fc267b0a | note | SHL Key - W
| section | 5.0 Conformance Check
| checkpoint | 5.1 - Survey Report
839c2651-c6c1-5444-ba1d-14796f923f25 | note | Acceptance Criteria - An as-built survey of the conduit and pit system has been completed to ensure all structures are within construction tolerances.
6dfaa406-2121-50b8-bb0b-f5f87dbb6150 | button | Acceptance | Yes,No,N/A
cb9efa2d-24f6-5f64-a66d-4281c1977217 | note | Key - R
f36390bd-a6ba-535b-be62-891d747cf2a9 | note | UGL Key - R
75754d84-52d5-54be-bda9-a55229b398c2 | note | SHL Key - R
eba7ff6e-f052-5ce7-b3e2-6aab3c3ef649 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d55a88d3-997f-5ddb-9c23-1f50bcf9c879 | tickbox | Survey report
| checkpoint | 5.2 - Acceptance and closure of non-conforming items
2e6c91e2-360a-5df7-995b-d9d0b19e19b6 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
8f57ed3a-204d-5d87-adca-3cb7e1774bff | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
d6a13e52-c085-5168-b333-83c5189b9b1e | note | HOLD POINT
04fc6eb8-a3d3-5183-8276-1bc9f8ce5954 | button | Acceptance | Yes,No,N/A
8ee7234b-63dc-5529-ae32-2f80fbc19f95 | note | Key - H
988850ca-276b-5f1d-884b-caff378a6518 | note | UGL Key - H
6a9302b3-3700-5f95-adad-6e0bfabfb773 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-009 Unbound Flexible Pavement & Checklist- Rev.7 | itp | INF-HSEQ CC0375-ITP-009 Unbound Flexible Pavement & Checklist- Rev.7 |  | 6ccde3b1-383b-4d54-87c8-72ede1e37663
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
8a057f01-850b-5c26-8fc4-63d79c5d41fd | note | Ref docs - Drawings
bb28ac68-4d40-50fd-9c36-6db19c321a4c | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
c97c5970-47bb-54cd-af9e-b4a1d5094617 | button | Acceptance | Yes,No,N/A
da47f3cb-7da6-5f7b-925a-4a96e38e7cc2 | note | Key - S
29be0142-ac5f-5b74-94af-09d53084e164 | note | UGL Key - S
e9640473-d615-5edb-b85d-996491db979b | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
aefd6173-5b7c-547e-8d42-e33b60a826df | note | Ref docs - Spec. 0161 Quality (Construction) [Cl 7.6]
50c0de5c-a050-5cb2-88af-bec3ee915e6b | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
4c0381e9-e98d-5048-9d5d-2689ed964302 | button | Acceptance | Yes,No,N/A
c93ab9ca-d662-5193-9c91-78109cedd892 | note | Key - S
f007ec21-2358-5968-a076-95c240829e2f | note | UGL Key - S
140e5389-5975-5304-a868-d8d98a733dd1 | note | SHL Key - S
1c36246c-f577-575c-a769-bd1517a3b341 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5cf598fa-9b05-5bf8-90d9-ae8248d6ad17 | tickbox | Lot map
| checkpoint | 1.3 - Material Classification and Source
72e6d435-1907-5b11-81e3-d42641cf6bec | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 2.3, 3.0]
26a81325-134e-59ad-912e-b7c77a51dbfc | note | Acceptance Criteria - Is the correct material being used?
51a2cf90-2949-5c23-bedb-dc9d5a934c5e | note | ○ Has the material to be used been approved by UGL (Material certificates to be provided)?
2ea5b7c6-3888-54e0-a2e1-bf18d347d309 | note | HOLD POINT
3a564a03-8083-513b-92e2-228e3e9ad5c6 | note | Notice: 14 days before commencing
5ae90004-2432-5be8-beb7-1668dcaac2e1 | button | Acceptance | Yes,No,N/A
80960097-4a10-57f9-bc19-eddeffdfb5f8 | note | Please tick the appropriate box:
81348a95-56ec-5eca-90e5-846283d3e0e2 | tickbox | DGB20
f358d177-2ae3-5035-a801-39d4b8fabb12 | tickbox | DGS20
30b93fae-b3d9-5a1c-a251-db7d206308c3 | tickbox | _________
939482c8-20ca-533e-ad22-2f4ecbf66d95 | textbox
bb75851c-e636-545c-b868-18f5402ee48a | note | Key - H
1061b288-54ed-573d-802b-b14fd36b9ab8 | note | UGL Key - H
7659d112-e6a4-5789-a57d-6a80015f5e77 | note | SHL Key - H
7d8566d0-52f7-5a2e-b05c-7363233d5d79 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8364ed1b-7292-564b-a36d-e87f35463ae5 | tickbox | Material test certificates
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.4 - Set Out
5b640af7-da0f-5674-b12f-a29d3b39884e | note | Acceptance Criteria - Is the work area clearly pegged out for line and level?
2188346c-b86f-57fe-8efe-06dcad2d8a1f | button | Acceptance | Yes,No,N/A
1eec752b-4f77-5517-a6ee-4666446ac683 | note | Key - S
31d4fe20-cf57-5760-802f-cc73a950b57d | note | UGL Key - S
c8b3591f-e72f-521b-83e5-a9dfe40470dd | note | SHL Key - S
| section | 2.0 Pavement construction
| checkpoint | 2.1 - Delivery of Material
f8436422-0e98-5f34-8449-ae9af83ed3da | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.2]
ec74fa6c-98c3-52cf-acc1-56af92472c13 | note | Acceptance Criteria - Inspection of delivered materials for approval
2a032ae0-53df-5ca3-b278-16a0c9e788a0 | note | WITNESS POINT
432befe5-fdc9-5466-815b-16af97275278 | note | Notice: Before placing
0063de23-bed9-5525-a69d-6fe04e7911eb | button | Acceptance | Yes,No,N/A
fe41e074-4ca6-545a-956e-8384efcb23fc | note | Key - W
c2c74132-0e2b-53b1-b515-301ff09858ab | note | UGL Key - W
97fa13fc-f4d4-5e12-b86b-26de2b3d74ed | note | SHL Key - W
72a0e4f7-d3d7-52a4-8185-edfd8c65bc76 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
552710d9-ed21-54e9-a638-f63987b30204 | tickbox | Delivery dockets
| checkpoint | 2.2 - Stockpiling of Materials (if required)
f8d2a80c-d3f5-529c-8c48-5660aa491153 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.2]
445b78bb-ecef-59f9-98b2-ad507863b640 | note | Acceptance Criteria - Is the material being stored in an approved stockpile location?
5bf48f82-7ace-51c1-b501-651165fc5e03 | note | ○ Stockpile foundation to be clear of vegetation and extraneous matter and shaped to form a crown to drain freely.
142a78ae-f781-592e-ae98-2632c690384d | note | ○ Stockpile total height < 4m
6b5f54bd-ad79-5ee4-b031-cd039585979d | note | ○ Shape of batter: Side slopes not greater than 1.5H:1.0V or less than 3.0H:1.0V
b5084cb1-eb27-519a-a4f1-1b4bcfe8a2e8 | note | WITNESS POINT: Ongoing
5ce8fab3-83fe-56cf-b96e-61af4bc6522f | button | Acceptance | Yes,No,N/A
bed15e81-f8e0-5b6d-baba-7c53d638a03c | note | Key - W
5ced5dda-a571-5f39-be21-7e8aaf49d60f | note | UGL Key - W
8f0ecfed-a35d-5786-a605-c79c8488c80a | note | SHL Key - W
| checkpoint | 2.3 - Spreading Material
7d165d30-fd25-5dd9-b702-7b4fc2adff91 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.3]
3f7ca4ee-553a-5787-9476-dc18857fee69 | note | Acceptance Criteria - Prior to spreading, previous layer to be inspected by the Superintendent for approval.
c9bd8177-b3c7-5ba0-9967-d96f2cb5d35a | note | ○ Refer to ITP of previous Layer.
35f83acc-023f-59d0-a29e-7c6264f52422 | note | HOLD POINT
49a29732-3d22-55cc-b368-d5d5ab596027 | note | Notice: Prior to spreading material
c942c98e-8b10-552f-9d3f-44e835a75796 | button | Acceptance | Yes,No,N/A
d72ef7d1-e141-579a-bf93-0dc917070454 | note | Key - H
0ff3b186-b846-5572-b165-4b201484f414 | note | UGL Key - H
6f4f86f5-158c-542c-8756-f0e8dd5b6893 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.4 - Moisture
b13a1a5b-e5c2-5768-b69d-d5379eefcb37 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.3]
a8f20e05-99d2-5a81-8a63-b463f46eb57a | note | Acceptance Criteria - Has the material maintained at optimum moisture content (60 to 90% OMC), with additional water being added if required during compaction?
8b14c15b-9f07-53f4-8596-d862a9b42146 | button | Acceptance | Yes,No,N/A
5c9dde09-0af6-5803-82cc-ad6aff550694 | note | Key - S
de02fc0b-3a1c-50c8-8b9e-41799bddc4f9 | note | UGL Key - S
598f39cb-4c00-5669-9f4e-eadb09eac9e6 | note | SHL Key - S
f9777d6a-094c-5c8f-8169-6a130e007414 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1b889c1b-347b-5896-9381-8d59105fd6e6 | tickbox | Test reports
| checkpoint | 2.5 - Compaction
ea2f0c91-58fb-56e9-8d30-d0102b3820d4 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.4]
f2e76ab9-4791-5efb-8d2b-e844dbc28954 | note | Acceptance Criteria - Is compacted layer thickness between 100-150mm?
fffdf57b-e9c3-5ba2-9bf4-8662643f60e9 | note | ○ Has the layer been adequately compacted to a minimum relative compaction of 97%?
b5119c4e-9aaf-5ad8-96d0-f2453100a77c | note | HOLD POINT
454ceaaf-c90a-5a8b-88fd-ba67f5cdd487 | note | Notice: 1 working days after getting results
03342863-9e87-5aa2-ae09-9bd025a097a4 | button | Acceptance | Yes,No,N/A
f4b3ece8-aa72-5acc-b64f-fd0bcb607509 | note | Key - H
b8f42153-1320-5de8-ad8b-45e9dd5a19d7 | note | UGL Key - H
65c4de17-8b74-54de-ac55-be2f752a9a36 | note | SHL Key - H
7abf514a-68f6-59e5-8060-feec59033655 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
12ce8c47-8fbd-5c37-9cb3-7183c72087c3 | tickbox | Test reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.6 - Removal & Replacement
5c423068-c40d-5299-aece-a0038a9482a3 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.7]
568b6f2c-3a90-5027-ba28-09744ab2c6a1 | note | Acceptance Criteria - Superintendent to determine the extent of any rejected pavement to be removed. Before replacing the material, area to be reinspected by the superintendent
9998ecec-ebb7-5935-a508-ca367256a22e | note | HOLD POINT
aa10fa51-1b72-59ad-bfc7-221226501a1b | note | Notice: 1 working day before next activity
c903c59c-64ca-56c8-b8e9-b4a0254a84e0 | button | Acceptance | Yes,No,N/A
118b04fb-3727-501d-b8c8-670672f67258 | note | Key - H
c4ba6664-2c0d-5b57-ac4e-2840dbacb572 | note | UGL Key - H
15c8c085-077a-5db8-83ac-09aff43dce81 | note | SHL Key - H
4bf5bc9f-104e-578a-ae04-38c8337ad1c3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1bc61ece-3d9b-590c-bf1b-f7ccab6277fb | tickbox | As built reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.7 - Maintenance of Base
3e33cf93-fe8e-5863-8f25-042cfe084d22 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.8]
220354cd-e992-5960-9198-224a52dff90d | note | Acceptance Criteria - Finished surface of the base course must be maintained and appropriately drained until the wearing course is completed.
29a09df0-ad90-5335-af5d-38f147433600 | note | ○ Cover base course with primerseal within 7 days of acceptance unless agreed otherwise with the superintendent (see 1143 Sprayed Bituminous Surfacing)
d0ae8caf-1ffc-5bcd-8f02-d5ea528a5a0a | note | ○ Non-essential plant to be restricted from using the pavement until primerseal is applied unless otherwise approved.
f779cb51-e260-5e5e-82f0-5259f55419f2 | note | WITNESS POINT
d14c8a4b-8b36-570b-8a01-2da7a2ebff1e | note | Notice: within 7 days of acceptance
99f8124b-7c07-5b56-b2b4-80bb49488beb | button | Acceptance | Yes,No,N/A
41530e2f-e992-5c0e-bab9-bf1fd60ec11e | note | Key - W
96a04ce8-11d6-56b2-aa13-5a1acb3f40bc | note | UGL Key - W
ccd3fc3b-6a21-5ae9-b03c-008e29a06b28 | note | SHL Key - W
| section | 3.0 Conformance check
| checkpoint | 3.1 - Pavement finish
f02ad8b9-32ba-5989-ab7e-593199e6c95e | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
9cfb4893-7494-5247-a560-6f25e889fbd1 | note | Acceptance Criteria - Has the pavement course been finished to a smooth and uniform surface parallel with proposed finished wearing surface?
f66f2f7e-b739-572d-95af-1494ac86d9ca | button | Acceptance | Yes,No,N/A
bda17945-e23a-5e0e-9ee4-1b8c57084688 | note | Key - S
97a0255c-8b9e-5970-9b5e-d9d77924d771 | note | UGL Key - S
b2cbf1ee-2a6c-552a-b202-af473333d572 | note | SHL Key - S
| checkpoint | 3.2 - Width and alignment
59f6ebcd-3924-5d4e-a430-f9706f9e7452 | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
fa6f8655-1abc-552d-ba12-b64ae92af41c | note | Acceptance Criteria - Is the pavement width and alignment within tolerance: 0mm to +100mm measured from the design centreline (limited to 50mm per side)
61702b5f-e80b-50c3-aa21-0b4eb8fd6712 | note | HOLD POINT
103865dd-780e-5442-9e42-7e91686f63eb | note | Notice: 1 working day before next activity
a50b2a0d-1b73-502f-a0c0-3db9be8d607a | button | Acceptance | Yes,No,N/A
28b6040c-f03a-5437-aa5a-4130f172234e | note | Key - H
3a67f88c-d18a-5ecc-9d05-07704a0a69e4 | note | UGL Key - H
44cbd6da-8a86-576b-a816-39b0580ecffe | note | SHL Key - H
62a35657-05e6-5bb1-be01-41a295abf105 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
88f1f926-e1d6-54e3-aa30-deee655a95a2 | tickbox | As built reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Surface level of pavement courses
24e584b5-2931-5928-9721-ecddd8652d0c | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
fa3005a3-4915-53fb-8c51-c226f5c7b767 | note | Acceptance Criteria - Is the pavement surface level within the following tolerances:
79a35f1e-6e4b-5e34-badb-9d69a62bfce8 | note | ○ Base Layer Surface tolerance: - 0 mm to + 10mm
b67a96be-40fb-457a-a551-1a472906494e | note | ○ Subbase Layer Surface tolerance: - 40 mm to + 0 mm
a2c92769-0325-54e6-ab4c-624932d6fc51 | note | ○ Top Base Layer adjacent to Kerb and gutter: ± 5mm from lip level of gutter less thickness of wearing course
bf4cc4c4-38e8-5194-991f-4d4716fdeb5d | note | ○ Surface deviation: ± 5mm from 3m straightedge laid in any direction, after trimming and immediately prior to seal
16fd1967-a0ec-55a7-aa72-da47310a6617 | note | HOLD POINT
759f62e8-7c82-5b8b-af31-8106358ce237 | note | Notice: 1 working day before next activity
7a3febc8-c442-56e3-989a-7951b4f0875f | button | Acceptance | Yes,No,N/A
7ba5dff9-e126-5013-a85d-a683274bf802 | note | Key - H
2c8d26b8-9759-5b91-b121-85a9db7efee3 | note | UGL Key - H
9e05373e-829c-51de-a8b1-f1777d1605c0 | note | SHL Key - H
638a7427-4e09-5f8d-b428-74235a214b7e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
be3de7e0-6aee-529f-9355-eded121fb66d | tickbox | As built reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Acceptance and closure of non-conforming items
7395eb40-ed2d-5c02-b423-e1233bec44cf | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
d003d2d0-cd1d-51c1-9a20-3b547640119f | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
68b8cd7a-c02d-569d-9f03-94b0f995f111 | note | HOLD POINT
864c4de3-0c9a-5c5c-9b49-6f9fa1834dca | button | Acceptance | Yes,No,N/A
36671fdd-0573-513a-923f-3f706ed378cc | note | Key - H
e5843071-9e9f-5615-9a07-e9b20ad6c713 | note | UGL Key - H
24acb938-f609-54d0-a1b5-eae9b2bbe10c | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-010 Asphalt & Checklist - Rev.3 | itp | INF-HSEQ CC0375-ITP-010 Asphalt & Checklist - Rev.3 |  | 07fd1739-3cd2-4468-b82e-ce3eaa1d74fc
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
8b521ed9-7662-5896-8505-bd58f3557f5d | note | Ref docs - Issued drawings / Site copy drawings
859f3fc5-f72e-53ac-b7dc-82dd33d87728 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
583bc2a1-2c0d-5539-82f2-19934689195e | button | Acceptance | Yes,No,N/A
2cf26ec4-39f0-5406-a419-111db80df5d8 | note | Key - S
fd84de87-d34e-58a5-8b6a-dbd8a82846b5 | note | UGL Key - S
c3b37027-e624-5c93-b9b0-57cdbdabe56f | note | SHL Key - S
| checkpoint | 1.2 - Determine lot size
f7745aad-a272-54c1-84c8-d7d38f65302f | note | Ref docs - Spec. 0161 Quality [Cl 7.8]
6ef52324-8f3d-5ee9-8fa1-05aa6f1d95a7 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
3bde29ae-ef82-5357-8c27-7c5fedb2754d | button | Acceptance | Yes,No,N/A
bda9a801-dcc8-5cd1-91e3-5ace2a115f40 | note | Key - S
76de787b-929b-521b-ab7b-e908e1b16d75 | note | UGL Key - S
7ff77f10-7690-5d21-9da9-839a864220fd | note | SHL Key - S
4ed16aff-40bd-5d1e-941a-86dd27eb77da | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
826d393e-93ea-591d-8cd0-1c75d2bb37f4 | tickbox | Lot map
| checkpoint | 1.3 - Set out
6219cf74-449f-59fc-af25-40dfc92f41e9 | note | Ref docs - Spec. 0161 Quality [Cl 3.13], Drawings
a7dbba5c-55b1-5e38-b2e4-ee1a3987c34f | note | Acceptance Criteria - Has the pavement been set out by an accredited Surveyor?
b59a8e4b-7704-5876-9b84-3f8b1af9b116 | note | ○ Set out comply with drawings?
5918bf82-de0b-5229-a11a-2025f820e1ae | button | Acceptance | Yes,No,N/A
fe80df2f-8a27-56bd-82fa-91e7105dde58 | note | Key - S
ec95b0f7-01d0-518e-ab79-049d4331de86 | note | UGL Key - S
7e08768b-64e9-50d5-8d19-ede75c33439e | note | SHL Key - S
| checkpoint | 1.4 - Mix design approval
f26bc0c0-1fb9-5670-9a3c-58dd59751bf2 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 2.4]
3bae8603-1f21-548d-b433-9ac94c0939a8 | note | Acceptance Criteria - Provide all mix designs. Mix design is to be assessed by the Superintendent for compliance.
fa63228e-1ed7-5b88-ab34-7fd2d5e98cce | note | ○ Mix design to be approved by Superintendent before use.
0612e515-6941-592e-b1d2-f7eb2654d8a3 | note | Notice: 14 working days before using mix
1b6881f5-43e8-5ab5-b731-9976e109a15a | note | HOLD POINT
80341d04-6964-5a45-beb8-95fd4df41c60 | button | Acceptance | Yes,No,N/A
df7fd1f5-833f-5e47-8038-011253702a8e | note | Key - H
c0e10a1b-0cb7-5038-b45f-80bf369d8e05 | note | UGL Key - H
d512979e-0a7e-5f1d-803b-41e416340039 | note | SHL Key - H
c9d2c77b-a9c4-5d54-aaf7-5d3c9aa4016c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
62928efd-5ffd-56e0-8078-af5ceed39b0b | tickbox | Mix design
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.5 - Tolerances of mix production
ed27058c-513f-5814-82a2-882943ca8160 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.1]
d6f0829c-bcf6-5851-987a-8f8d94cc4e2c | note | Acceptance Criteria - Is the Binder within 0.3% of total mix?
4bf8c551-e5fd-5a97-a1cb-ebe0b29fd911 | note | ○ Has the daily particle size distribution been within tolerance?
2aa03937-012f-51e9-9d9d-c078eb4c2fab | note | ○ Has the daily moisture content been within tolerance – not to exceed 0.5% on completion of mixing?
7b6f2f36-b2a8-55e0-8d54-5159129cc624 | button | Acceptance | Yes,No,N/A
7f352cdb-1807-50ba-8772-eea3390ebd70 | note | Key - S
f7623238-d572-5d55-af91-7ea4869f0df7 | note | UGL Key - S
ad4d115d-020d-51ac-bf46-d2ac0089f418 | note | SHL Key - S
72edbd1b-028b-5183-866a-a713fba500cc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0097cea3-4aa7-5dab-b09e-f368751c1a41 | tickbox | Test report
| checkpoint | 1.6 - Production temperatures
8d2f26a1-a703-5b99-98f8-863d5611035b | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.2]
19e4d441-7b99-5fcd-b815-13f3d90f1443 | note | Acceptance Criteria - Do the temperatures listed below comply with requirements for max. temperature?
eef3c871-cb17-5ac1-9509-ed2cfbcdd807 | note | – Class 170, Class 320, Class AR450 Bitumen delivered into mixer – 165ºC
48d62586-9334-5b7d-b970-08162b75ffd7 | note | – Class 600 Bitumen delivered into mixer – 175 ºC
683aa177-ca61-508a-8272-7c6ffcb3b250 | note | – Aggregates before binder – 200 ºC
9c5ccf56-0320-524e-937b-04f424199a0f | note | – Asphalt at discharge point – 175 ºC
db60cb45-ba60-559a-bb06-8330f1127506 | button | Acceptance | Yes,No,N/A
ef811113-f851-5373-8de0-ee6a9f80ccf6 | note | Key - S
426bb2cf-af9f-5a40-ac69-c83d67a65af7 | note | UGL Key - S
0cbae04a-8d59-5c90-a61b-fc7f9c24d33b | note | SHL Key - S
ecae07ed-8979-599c-b4f2-6cbe7fce5442 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9efd3428-e751-55a3-9d10-fa4a17c6d6a4 | tickbox | Test report
| checkpoint | 1.7 - Certification of specification Compliance
38b3cff9-37a2-5abc-b1df-20bde532e89e | note | Acceptance Criteria - Has each delivery come with a certificate of compliance?
9904636d-b84c-5b0e-96a0-0313bd919137 | button | Acceptance | Yes,No,N/A
798d2633-4bfa-5331-8f5b-7724f701f23b | note | Key - S
ec4d409b-b55f-504c-8aed-8d75f3cb5230 | note | UGL Key - S
12f7763a-fd37-5ad9-9fe2-b7a24f99cc15 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
104e799d-21e9-5ea2-9c9d-7530cc02f5d7 | tickbox | Certificate of compliance
| section | 2.0 Preparation
| checkpoint | 2.1 - Conformance of previous layer
9756e67a-82cd-586a-a595-2ad5b8d3a357 | note | Acceptance Criteria - Has the previous layer passed acceptance criteria? Refer to ITP of previous layer.
68be4587-485c-5ba7-9e3d-1283a83c9c91 | button | Acceptance | Yes,No,N/A
4a919f5c-ef15-5325-910e-b7fca293ba21 | note | Key - S
4318d43f-0662-5825-be45-67eaa9023522 | note | UGL Key - S
0649d373-2a64-5f35-a656-5c60de574c03 | note | SHL Key - S
| checkpoint | 2.2 - Joints
a7398b08-ae70-5673-8595-e1b067900eac | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
97470b1a-d00a-5633-b98f-b642a3fff057 | note | Acceptance Criteria - Transverse joints shall be offset by not less than 2m in adjoining paver runs and from later to layer.
a2ddd95f-2419-5667-afc8-2961a8624a67 | note | Longitudinal joints shall meet the following requirements:
d6a5ff50-ee40-5894-b523-c17c086e9af1 | note | – Wearing course joint coincide with location of intended traffic lane lines
0afcfd20-7d3b-5e8e-bcc1-5dbbad94ce39 | note | – Intermediate and base course offset from layer to layer by not less than 150mm provided that no joint is placed directly below a trafficked wheel path
b16687eb-96ac-5866-a5fc-c28ff4690de2 | note | – Parallel to traffic lanes
f0e66604-1f2d-54e3-aba9-27081561c43e | note | ○ Location of planned joints is a Hold Point.
32dfa3ff-3cc3-5ccb-bf66-7089b7e4010f | note | Notice: 7 working day before commencing
5ae9eb62-75ca-568b-a385-16b371f54b45 | note | HOLD POINT
85211aa7-81fc-54dc-ad7b-7f03bd4464fc | button | Acceptance | Yes,No,N/A
78546ddc-9b73-552c-bd2f-f38ea153ea2e | note | Key - H
bd72c196-d59b-507b-bc69-9b9c9c866d5e | note | UGL Key - H
4517ebbc-710e-57f3-a37f-dd347a9d0dc2 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Prime application rate
fcf7443f-f1fc-5333-8923-de0f1c379b87 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
de6b2ff3-e15f-5369-b90f-0ea329e41f6a | note | Acceptance Criteria - Unless otherwise directed, tack coat is to be applied to provide a uniform application rate of residual binder of between 0.10L/m2 and 0.20L/m2
a5fea104-e91e-595e-b1c6-affa4e7dd1ac | note | ○ Is the application rate for tack coat between the following?
5d71cc18-490c-5736-a1d4-3aab33cd8909 | note | 0.15 to 0.30 litres/m 2 (60% bitumen content)
80f2cc6f-30e2-5868-b77b-e248fe913fe3 | note | 0.30 to 0.60 litres/ m 2 (30% bitumen content)
1b52a630-2993-5636-b305-9852b98bfa9f | button | Acceptance | Yes,No,N/A
949f6d4b-ca15-539e-ad2d-95b1bab59fd4 | note | Key - S
7a4331a0-9f43-5c82-b69a-5755675670da | note | UGL Key - S
2130067a-d4a8-52fb-9109-ee324b30dfc9 | note | SHL Key - S
| checkpoint | 2.4 - Approval to proceed
0d4a5655-eed8-5fbc-923c-428b09c7e153 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 2.4]
5e286f86-b856-57d2-a3e8-3a5aa9e97eca | note | Acceptance Criteria - Has approval to proceed been obtained from the Superintendent?
2237ecd8-e004-5a6d-b3c3-f5a72ffa9c12 | note | Notice: 7 working days before commencing production
3ae4c6e4-4acc-5210-bc7e-f7a28c49fa0a | note | HOLD POINT
867faeb1-8098-5e61-b300-f7be6b1cfdf8 | button | Acceptance | Yes,No,N/A
ff20d91c-3c67-5ba3-b8f6-5c6aa185f948 | note | Key - H
796b3d99-d020-5097-af77-36a1eeb48e69 | note | UGL Key - H
6343a640-2edf-5028-b532-18ae22812404 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 3.0 Placement of Asphalt
| checkpoint | 3.1 - Conditions for placing
11f5254a-75b9-5a42-8cf6-bbdb9bff7afc | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
bc392876-ff12-5ff4-91d0-2521a322f23c | note | Acceptance Criteria - Is the area essentially dry and free of surface water?
1c3b83b0-7a60-5b3d-b6e2-6e3ec8529094 | note | ○ Does the surface temperature meet requirements?
7c6c5119-dc40-5d3d-a46b-d6b412004fdb | note | – Intermediate and base courses: 5ºC
76753cb6-a6a4-59fe-975a-f0a698bf7090 | note | – Wearing course: 10ºC
5075e9d0-9202-5347-90b6-328b337954ab | button | Acceptance | Yes,No,N/A
bff6132e-8889-5728-82a8-81a15eca3197 | note | Key - S
d6e16ecb-772f-5fda-8f15-3220758ba7df | note | UGL Key - S
47145dbb-daa6-5ef0-a819-4066fed54f13 | note | SHL Key - S
| checkpoint | 3.2 - Spreading
2670cfb6-0d56-53f2-a2de-4963c617f5e5 | note | Ref docs - Drawings Spec. 1144 Asphaltic Concrete [Cl 3.4]
09b3295d-aeef-556e-b415-079a0cdc2bd4 | note | Acceptance Criteria - Has the asphalt been spread in layers at compacted thicknesses as per the drawings:
d24ff81c-afaa-526b-962f-ed9573068fb7 | note | – Wearing Course: 40mm
a624d6eb-a47c-5c90-9169-b043285a53f1 | note | – 7mm Primer Seal
8adb2fe9-7b50-56f2-819c-21bf2b131cb2 | note | ○ Has all asphalt been spread with a purpose designed asphalt paving machine to form a uniformly smooth asphalt mat?
b193a0da-f36c-5326-a9b5-f95896f98ad1 | note | ○ Does the width of a single paving run not exceed 6m?
b92ef0af-b461-5dfa-83f4-73cc60bafe1e | button | Acceptance | Yes,No,N/A
c03f2958-67f2-51fc-af97-d4839720d876 | note | Key - S
095722c9-10a6-5d14-8bfb-78d5fdfc130c | note | UGL Key - S
eb059e84-5ab7-5f9d-a512-e92e0c7345fe | note | SHL Key - S
| checkpoint | 3.3 - Compaction
d5f5cd82-afbb-5850-9682-c330e8e1d5e0 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4, 3.5]
b060dc59-8620-53fb-98ed-0fb4ba7f5de5 | note | Acceptance Criteria - Uniformly compact asphalt to below requirements as soon as the asphalt has cooled sufficiently.
1e0738df-9754-5f4e-baf7-a83cfdf834af | note | ○ Confirm Frequency of testing and target requirements
2c1fbc99-e486-56a2-81f7-de98a9afe74f | note | ○ 6 cores per lot
7d482035-1373-5d74-b426-74db69bb788c | note | ○ 10 nuclear density tests per lot
7ee0636d-b592-554b-92eb-1f437b28ae28 | note | Tested to the following criteria (acceptable values to be calculated bases off formula in standard):
6a8ad818-5726-572e-b70f-83327e128a32 | note | – Density ratio greater than 94% for thickness less than 50mm
d493789d-6067-57c0-9f63-f790456a10ba | note | – Density ratio greater than 96% for thickness greater than 50mm
7967a33f-fdeb-51f7-9714-391358ab4396 | note | Notice: Progressive
0f14293d-d521-541e-930f-6b405bdb3e54 | note | HOLD POINT
90c2dc2f-12c0-52da-8496-7b1fd4ce3935 | button | Acceptance | Yes,No,N/A
866645c8-450f-5542-b86a-9990e1b12420 | note | Key - H
b9146d52-e344-52b5-be22-039df9357d6a | note | UGL Key - H
661a5740-0ddf-5c17-a39e-7425e4b92c63 | note | SHL Key - H
bdf350fb-f1f0-5fc8-96ee-581a20868b78 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
dd65b3c4-5599-5806-9b5a-f3c0c84f9f74 | tickbox | Test reports
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Finishing
| checkpoint | 4.1 - Surface finish
ab7d3b3c-db88-596c-8cda-f2cf4ffee238 | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.5]
86a8bdc0-a3d8-523e-aca1-0a0ba0e82006 | note | Acceptance Criteria - Asphalt shall be consistent and uniform?
5bc22015-8654-5313-9021-d7f3b1c05ec5 | note | ○ Top of asphalt shall be not more than 10mm above specified level?
9e79b1e6-524d-536d-9499-5bf7113111cf | note | ○ Asphalt against the kerb and channel shall be flush or not more than 5mm above the lip of the channel?
33fa4170-1573-5153-8686-ca883a6b1225 | note | ○ Do no points on the finished surface lie more than below (medium to light traffic roads):
06d077c8-a7b1-52e0-86c4-ab4daf366126 | note | Parallel to centreline
562fd82b-c421-5237-9375-42657bd22d14 | note | – 7mm below a 3m straight edge for wearing course
62be2f78-03b2-503b-aa01-b77ce3ce1230 | note | Transverse to centreline
40362b99-6402-5da0-8076-b5e8e9e6f503 | note | – 10mm below a 3m straight edge for wearing course
5c53008f-9b76-515e-9a3d-1f5efe2cde0f | button | Acceptance | Yes,No,N/A
d65f3e07-be60-5429-a62a-2df56b664204 | note | Key - S
11de4bf3-948c-5746-8a90-2c52a7a36c2a | note | UGL Key - S
da81a204-e6cc-5afb-b15d-12c12670ad3e | note | SHL Key - S
| checkpoint | 4.2 - Survey pickup (Top layer only, N/A for all intermediate layers)
ef95502c-3898-5775-b4e9-7d90ba5c486a | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.5]
03573f23-f321-5089-9870-0ab9ea044868 | note | Acceptance Criteria - Has the prepared layer been surveyed in accordance with and verifying specified requirements?
1fb302d8-97b9-5b55-806e-221d25d1d3ff | note | ○ The horizontal location of any point on the pavement not to vary by more than ± 50mm from the corresponding points shown on the documents, expect where alignment with existing is required.
79ed943f-a84a-50d9-98e7-cfd0e4efa8cb | button | Acceptance | Yes,No,N/A
429ecb42-e12f-5663-9467-41e7f29f42f8 | note | Key - S
99639c07-a4fb-5d64-9fba-9fe14cf072f4 | note | UGL Key - S
6503ba2a-45be-5c15-809f-7048c24aa7ee | note | SHL Key - S
9c3331ad-33cc-542b-ace8-ec3b29e4f1a3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
124de1e3-d778-592c-852a-86bbff968811 | tickbox | As built reports
| checklist | INF-HSEQ CC0375-ITP-011 Drainage (Cast In-situ Structures) Checklist - Rev.7 | itp | INF-HSEQ CC0375-ITP-011 Drainage (Cast In-situ Structures) Checklist - Rev.7 |  | b326d542-6f60-47e1-b80a-8f936d22d315
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
b4330d9a-ff27-51fa-a9d7-b75d35fbcc6d | note | Ref docs - Issued drawings / Site copy drawings
fb2f14e1-b116-56c8-80f3-62abaa94459c | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
f3bebeb3-5632-5e0c-84d7-5408a7ce9c29 | button | Acceptance | Yes,No,N/A
16f639fc-1cca-5b09-a352-d3f41c0c3781 | note | Key - S
2181298b-95c1-5504-bd40-f99bb6c67440 | note | UGL Key - S
56a4e974-1724-559a-a1ce-ea7c680f0b69 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
c021c42b-f697-505b-ae78-9b15b20d79d8 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
ced49139-ebc5-5554-bfac-3579fdedfd8e | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
2cc4bbc6-1973-56f4-8710-4f89b15dc6dc | button | Acceptance | Yes,No,N/A
dd5899c8-7b9a-5697-98eb-87352ca1013e | note | Key - S
92a87bb9-7f15-54ba-9d54-48d27ee1b9fc | note | UGL Key - S
0df97870-74e7-5bd2-9795-5fee64531441 | note | SHL Key - S
09415c81-8375-5cec-8e05-9adaefb91b4e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
186440cb-101f-5b78-8096-4dc1065fde80 | tickbox | Lot map
| checkpoint | 1.3 - Set out
1decb66f-6e95-5c30-b94d-d71359983699 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2]
2f49cf5d-fd34-5f4e-b8b2-b2d120bab394 | note | Acceptance Criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
a60808a7-a9da-51f2-9907-abb5185525aa | button | Acceptance | Yes,No,N/A
e7e42383-97f5-53ec-8407-6038c439e209 | note | Key - S
54c8e17f-7d7a-53fa-b045-eeaf4c21608b | note | UGL Key - S
e4f73d71-45fb-5aea-a111-5938d18014bc | note | SHL Key - S
| section | 2.0 Excavation and bedding
| checkpoint | 2.1 - Excavation
89fa53eb-a244-57df-af79-15e309075640 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
3929a98d-3530-5847-a42e-20323434c0b1 | note | Acceptance Criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
6406d9ef-6732-5454-92df-874f0731e192 | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
f26b3de7-f505-5304-8d01-bee0bc636f55 | button | Acceptance | Yes,No,N/A
16eb51a3-c3bf-5e06-86c2-8cea21050a2b | note | Key - S
0d80c7f9-1983-5a17-bade-5cf537fec72e | note | UGL Key - S
d9d53534-5f67-53ca-9eea-2aa02b4224d8 | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable Material
e8b21db5-e0a2-5021-b701-3346170c4075 | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
1ffc03e8-b80f-5622-915d-a00cbb21e229 | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
fe0b8ad8-2349-5c1d-a86a-4eafa0a515ff | note | HOLD POINT
ebff2412-5eb6-5514-94ea-5e6abf0faa6e | button | Acceptance | Yes,No,N/A
6ff0bf35-6113-5c39-81ac-e9a5eba5e975 | note | Key - H
30a057f7-b584-59bb-ab37-0dea51f62616 | note | UGL Key - H
c4274d5f-4798-597b-9dc8-9311df6e1072 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction - Foundation
b8ab4afa-f945-5e40-90ef-e62700c8e0cf | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
47fa45f8-5f2f-5310-bf01-a2d419fbe878 | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
b9ded0d5-4979-59e1-bbd3-88f07e0a1ae2 | button | Acceptance | Yes,No,N/A
b75e0453-bbec-5b4b-ba35-0339de4c071c | note | Key - S
31266d5a-f90e-53ea-91c9-f49d3721e7f9 | note | UGL Key - S
f862ea4f-d501-5876-82eb-56ec74c6e482 | note | SHL Key - S
048202a5-5d71-59a8-8110-5936131042f6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
38e79ea6-af4d-5422-ad11-f31cfc8a29ee | tickbox | Test reports
| checkpoint | 2.4 - Foundation Inspection
1759df0a-7122-5d77-bc43-453efa6391fe | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
ddaaf121-b0be-5261-8aa5-742e321eecaf | note | Acceptance Criteria - Foundation to be inspected by the Superintendent prior to placing blinding
50e0f992-0e0c-5328-a772-7adedaf29d64 | note | HOLD POINT
3f70b98b-10b8-583a-8409-488e0f5c1f41 | button | Acceptance | Yes,No,N/A
46a85f3a-ed83-507e-a99e-c9ab28a39b38 | note | Key - H
d7bbd712-8f8d-5670-bce5-1a25fe68fd95 | note | UGL Key - H
8c96de65-3612-5c0b-848a-44c2c8dafe37 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Blinding
190e2ea4-e804-5c7f-8375-4b2a59d38ec1 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
76bac32e-0a41-5d31-8ec9-9462f26e91bf | note | Acceptance Criteria - Blinding (15MPa) for Reinforced Concrete Bases to be a 50mm thick mass concrete layer.
74b4f274-35b5-5b33-929f-dd366810ac4e | note | ○ Unreinforced bases can be poured directly on the earth
729fd8d1-7e0c-565c-8f97-5291a85370ef | button | Acceptance | Yes,No,N/A
46e1d911-ff84-54ae-ac64-7078705093bb | note | Key - S
7bf97374-f12d-526e-8d06-8a3e3e991fe7 | note | UGL Key - S
361974f4-e2b5-5773-ab47-c89d4856c281 | note | SHL Key - S
| section | 3.0 Cast in-situ structures
| checkpoint | 3.1 - Formwork (Base)
093980e3-8aca-5639-b3cb-d0c4e46047ca | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
fa2644eb-4774-50b7-a8c4-176d86a39295 | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
7ac211a5-3612-5d2b-a05f-d10c983a71ad | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
b8930497-1ae7-5c15-872c-53346e47174a | note | HOLD POINT
7b5ce84d-e00a-5ea5-b5bd-148088ef3b34 | note | Before Placing Concrete
9480154c-77e6-5d7c-a6f4-08c2a9d82b71 | button | Acceptance | Yes,No,N/A
eb24de67-e03c-5dfd-b21c-51220e1f172a | note | Key - H
1203b3b7-428f-59f9-be75-1a47e249541d | note | UGL Key - H
7d0f4715-564a-5f8e-9bbe-f4f621a22bc2 | note | SHL Key - H
dd311c6b-0ca1-5157-b590-bb0c2c94a298 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
53604dd8-c58e-5459-864b-de1eca210a77 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Steel reinforcement (Base)
7f6e2671-fd94-55dc-828b-e3541d8fd2f3 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
e0ef7b28-2670-5be0-aaf5-2eccf4289a6b | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
3b9338c4-0933-5c94-b92d-ed6dc7a2e8fe | note | ○ Concrete pre-pour inspection complete.
ff757bf6-0c2b-5fcb-bfe5-aef8175ab80b | note | HOLD POINT
fba25cf8-1c8e-5d72-a025-8be1fde81c75 | note | Before Placing Concrete
1e975776-47a1-5930-8a25-7c1d7f8ea801 | button | Acceptance | Yes,No,N/A
2bceb529-e11b-5822-8365-2ba7fbad8e1d | note | Key - H
5a8b6ec2-e08c-536d-9f37-ab457589ea4a | note | UGL Key - H
2be77881-a1b3-5bd9-a2ea-a2fbcbadd940 | note | SHL Key - H
d75d420b-dcfe-5aba-9381-bce17a97d30c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d3b8d330-09a1-5553-985e-d7dbdd7c92cf | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Formwork (Walls)
9fd7d194-7b7c-5027-b45a-3b0c022fe68d | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
6f914e52-7941-5904-838f-b7cdb3febeb7 | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
019292cc-f271-5111-bb7c-6bca9134ebaf | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement.
6e48350b-6911-54a4-9222-ed6a52865a2c | note | HOLD POINT
241204f5-9b66-5819-b7a6-34389540adff | note | Before Placing Concrete
018b8538-2c51-5b35-a7c1-319e91768139 | button | Acceptance | Yes,No,N/A
efc702fe-f193-5618-a8fc-0ae836983d0e | note | Key - H
58955405-f3c3-56cc-bfe9-afbaafa1b19b | note | UGL Key - H
eeb03852-3864-5b7b-a9e2-a8ac2d530c2e | note | SHL Key - H
3c1f85c7-1405-5595-b10e-e6aa204e6a8f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ed329e55-d0a8-5250-9134-af303766222b | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Steel reinforcement (Walls)
a69bba4f-3cfa-5de1-a582-58408f76c7ed | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
4e9f01df-0229-5d17-8027-a26f40cd8992 | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
98a53fa3-9d41-5ac1-a286-8f424f485326 | note | ○ Concrete pre-pour inspection complete.
a2843d51-8582-5617-b8d9-5e1531e2bf07 | note | HOLD POINT
f007e801-350b-55ed-ad3e-612093ef56bb | note | Before Placing Concrete
0e1560e6-b3cb-5669-b9c9-726c7dc40b56 | button | Acceptance | Yes,No,N/A
6f56205f-e21d-5724-af3c-e636c834ceb1 | note | Key - H
95c22c11-68e9-5de5-b79a-1f3565d74571 | note | UGL Key - H
041ce3ea-e8e9-53af-b508-4b72681a73eb | note | SHL Key - H
62ec69e1-db28-5c62-8dc3-651228116d7c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b33fedaa-2846-55aa-b453-dfb7c77856b8 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Pit & Pipe Connections
a6c2c8f7-d9fc-5c9c-97a5-c7fd7db85828 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
9733dc89-7f22-516d-9e1f-55dc15eecec6 | note | Acceptance Criteria - Inlet and outlet pipes to be integrally cast into pit walls and the joint waterproofed as per design requirements.
d65295d9-5e4b-5fab-8e8c-f4d1ce92a097 | button | Acceptance | Yes,No,N/A
0c9012e0-e222-5e79-b5e9-8ba5955a5739 | note | Key - S
cbb8639e-cf49-545f-8224-629385f37e7f | note | UGL Key - S
d41749da-d81a-5bb8-b920-c915058bab12 | note | SHL Key - S
| checkpoint | 3.6 - Concrete supply and placement
20b97170-c23b-5bff-be64-99eaca04daa5 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11], Drawings
3d7e3bd6-e2e7-58ad-8b61-3f271c9c14d7 | note | Acceptance Criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
23dccb60-9e71-5f85-a444-70c5406e4eff | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
0a09fcb8-90f9-5acf-8eb6-e5226d10c8a5 | note | – – – – – – – – – – – – – – – –
f5c7fbda-f46a-57a9-98e1-c436c63f8c81 | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
3b0b15fa-91df-5e31-8c60-bb35b824defc | note | – – – – – – – – – – – – – – – –
0e497f29-f9e0-561e-967e-3d4b6f11e22b | note | 10 - 24 ¦¦ 2.00
8af4b7de-547e-5f2b-8ebc-1fa59118e1c8 | note | 24 - 27 ¦¦ 1.50
42946e4b-1c8e-551f-ae1a-27e433228dc3 | note | 27 - 30 ¦¦ 1.00
a9d498cf-512f-5917-988f-b56b45eb5c56 | note | 30 - 32 ¦¦ 0.75
89251d67-0168-5bc6-991a-bf5dda58e771 | note | – – – – – – – – – – – – – – – –
95ec4718-644e-5bbb-85c0-0367ac0f9b86 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
10677aef-c1e0-5be8-bbb1-61570b00d6bb | note | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
f15d3336-0b29-5d60-a4f3-5f0149e9bb8c | button | Acceptance | Yes,No,N/A
9cec0849-aa4d-577f-9fbb-4b7a0ce5db55 | note | Key - S
e43bc7b1-2ab4-531a-8f44-ed6e14b1d5d7 | note | UGL Key - S
ced24efc-8061-5003-adc1-9c9d464777bc | note | SHL Key - S
96aa044a-dfb0-5446-b050-746c82694f29 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d3c84e2e-a0b6-5cbf-9c5a-0c8bb9c308a0 | tickbox | Delivery dockets
| checkpoint | 3.7 - Concrete sampling
5542c73c-0673-5f3f-bab6-d1d9130c4bfc | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
174c2bde-5e8c-507b-95c6-a720c9149093 | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
4ce67011-ab45-56fc-897f-d9affcb244bc | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
70047186-d673-5951-8b38-46c7a8470f91 | note | (b) Slump: One per batch of concrete
71b82711-57ff-5cb7-9093-a17b5ed0b75e | button | Acceptance | Yes,No,N/A
9c381db3-94f7-5afa-9df6-c5aacbeb21c3 | note | Key - S
8a3e7d52-4d6c-5f2e-9139-14a156273807 | note | UGL Key - S
9abfe893-e5dc-571c-8b11-26082a5ef0c1 | note | SHL Key - S
e823a7ce-7e51-5c67-a863-44c57c9a189b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4fc00cb8-d144-5031-892d-c8d3eee7f23a | tickbox | Concrete pour record
| checkpoint | 3.8 - Concrete testing
9f92fc6e-8557-5445-8a63-b45978907ada | note | Ref docs - Drawings
c3c75e51-6d4a-59ef-b140-802e1043ce1e | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
556a7ad4-e4ac-59ed-9474-01da93ad631a | note | ○ Slump within tolerances specified in AS 1379
d52aa0ba-bb9e-528a-b6d2-66f40c0ef22c | note | – – – – – – – – – – – – – – – –
c75e816b-a45d-5cc3-8308-201c56ce4a37 | note | Table 5.1 Permissible Tolerance on Slump
fee8faea-4d56-5dd4-8f08-1833dccd96b9 | note | – – – – – – – – – – – – – – – –
ed24ec92-cbfb-5a96-ac47-92273d4173d6 | note | Specified slump, mm ¦¦ Tolerance, mm
995038dd-1e27-5c6f-aa3e-14415e611384 | note | – – – – – – – – – – – – – – – –
c2627da9-7bdb-56b9-a010-2c7f4e504b84 | note | <60 ¦¦ ±10
d6a45446-9278-52c9-8d1a-12b156273694 | note | ≥60 ≤80 ¦¦ ±15
469a25c6-e38a-59ed-8b3b-364055f31d8e | note | >80 ≤110 ¦¦ ±20
f21cac15-9c4e-5a0a-97a0-fa03e80fa3bc | note | >110 ≤150 ¦¦ ±30
3e303904-dc47-52d3-952e-15fa1fcdd340 | note | >150 ¦¦ ±40
0a6ae6cb-af28-5424-bb46-2cf03cf96d2f | note | – – – – – – – – – – – – – – – –
5f6333fa-6bca-5584-8fc6-08075abb7ade | note | Testing to be in a NATA accredited test facility
85406c4d-5c2e-5f8c-a061-d9a51bce02c4 | button | Acceptance | Yes,No,N/A
50e43d65-3dc0-52f3-b146-d0e0cec540d1 | note | Key - S
4eb768d0-e345-5045-ac36-bc791b7323b7 | note | UGL Key - S
824d560e-b8eb-591c-bdb4-1436544711c8 | note | SHL Key - S
1d1e4a96-5aaf-5f5c-b94d-69aea1805488 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ab262bb9-077d-5f19-97ba-5f477c83ed00 | tickbox | Test reports
| checkpoint | 3.9 - Curing
5d9662ea-2557-5ad3-9516-2bffabb7be7d | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
264e1d72-aafc-5258-a148-d68fb25dc5ae | note | Acceptance Criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention until 15MPa is achieved unless directed otherwise by the superintendent
5aea7650-c74b-5977-8d64-90514908d8f1 | button | Acceptance | Yes,No,N/A
823a2eaf-e6ed-5509-95a8-a21491a16af1 | note | Key - S
c1ada7b0-11ac-5892-9ba2-6ca4cbfcc96a | note | UGL Key - S
8ba04dd6-6e78-5806-a327-815f5a1df95f | note | SHL Key - S
| section | 4.0 Finishing Works and Backfilling
| checkpoint | 4.1 - Access Covers & Grates
95107d71-1af9-5771-9628-75bda02f346d | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
43e7f39f-4d73-5dd8-a439-04a0aa5d5fc7 | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
edc53d99-f050-5b07-a0db-136055f74cc0 | button | Acceptance | Yes,No,N/A
de041491-a40e-5407-b2a4-576a31f7194c | note | Key - S
c1f9dd1f-9ed2-5264-94f4-a8f19e6a45be | note | UGL Key - S
29746b71-6afa-546c-8e80-de74539456ff | note | SHL Key - S
| checkpoint | 4.2 - Step Irons
bad9168f-d24c-5c30-8a62-d16213bab03a | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
0dd72312-1b86-5dfc-bf50-6da3e37f3ac9 | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
203f4056-ea64-5169-8704-35c8c5dccfcf | button | Acceptance | Yes,No,N/A
44b0bbb9-ab8d-55e3-ba51-6780ef1012ab | note | Key - S
1436d06d-f4bc-5471-95ff-cacccb58d607 | note | UGL Key - S
a3f0e69c-4a3e-50a6-b958-6c274f4fb0f4 | note | SHL Key - S
| checkpoint | 4.3 - Pit Jointing
24cda578-c261-5e56-8524-7fcb53a24f54 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
fef0333d-01cc-52c7-bca5-ca497aefaa38 | note | Acceptance Criteria - Provide a 10mm isolation joint in between precast pits and any abutting concrete pavement, kerb and gutter or concrete structure
5cb40e18-9a6b-57cd-b722-25d0c5188a33 | button | Acceptance | Yes,No,N/A
d64da8ee-d627-5601-a5b5-205b86f757b3 | note | Key - S
b1ad3c7c-3839-5a63-a50e-78bf9edf8dac | note | UGL Key - S
bb6c829d-bfc5-571e-9713-31c1846f00b9 | note | SHL Key - S
| checkpoint | 4.4 - Structure Backfill
3a6e3816-4287-551d-b34b-6d174f0d6be6 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.7], Spec. 1112 Earthworks [Cl 4.10]
7f380d8b-05d6-5e12-86e4-64f6e681d59b | note | Acceptance Criteria - Backfill shall not commence until the compressive strength of concrete has reached at least 15MPa unless otherwise approved by the superintendent. (Wingwalls shall have no backfill placed until 21 days after casting)
aa1556af-84de-5400-ac98-0e9f68eb8778 | note | ○ Drainage Structures to be backfilled in 150mm thick layers for a horizontal distance of one third of the height of the structure.
e40f3368-61e8-5657-9f99-8d601ea44f27 | note | ○ Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
f8e12239-6fe9-5b32-9d41-cf7a503acbbe | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
bfa3490d-e06c-591b-b59c-328dd558dce9 | note | HOLD POINT
1c34ef61-cd78-5398-a878-f9673e39581a | button | Acceptance | Yes,No,N/A
94c75314-0573-57ee-a5b3-290bf398365f | note | Key - H
2c7e0805-1580-5a3f-8ee6-cda2f878f85b | note | UGL Key - W
4d2a3294-4f90-5873-a117-2c32cdc61c74 | note | SHL Key - W
31b49d18-57dc-5a4e-ae19-01bf648423e5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd6d79ad-f40b-5bf2-8955-b503b10a092e | tickbox | Material Test Report
| checkpoint | 4.5 - Compaction - Backfill
de322539-cabd-557e-9fd8-6af02f8d422e | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
746b90f4-6909-52f3-a4af-ed4c559f39a2 | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against pits to be:
495e6f81-18a3-5412-88e1-6c6826025917 | note | – 92% for general fill
b9710709-0ca6-5ea8-9563-b379738a8c8d | note | – 97% for select fill
251530df-31be-52a5-ae8b-f38c2b02a005 | button | Acceptance | Yes,No,N/A
93ba04db-2825-535b-83f3-c324be664c48 | note | Key - S
5c84ab42-265c-5826-9c5c-cda2bf84066d | note | UGL Key - S
62062831-be4b-543c-a522-9fa77b045271 | note | SHL Key - S
7d692315-73e2-5abf-b5e7-8edaacbc100d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
746d608c-fedb-5b2e-93cb-165424a7dcad | tickbox | Test reports
| checkpoint | 4.6 - Moisture Content
e1e24c70-6d47-5ccc-8c0a-b9e61fdee3d1 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
319b3ca8-2a43-562a-9942-7ad3a0416283 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
72d7cbdd-a995-507c-bab2-66e6321dd81b | button | Acceptance | Yes,No,N/A
11795a05-a4a9-5ebd-bfe7-c02db0e9501c | note | Key - S
3992fc76-e1b1-569a-809d-bba5e5e59a43 | note | UGL Key - S
570e010a-ba66-5857-a5e4-e6e56796c8c2 | note | SHL Key - S
27de1742-9905-515d-bf54-90ce934e3a92 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3ef99f4f-07ba-55e7-9551-6062e595752c | tickbox | Test reports
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey Report
b0b462e6-7c91-5cc6-9910-7ad02d837183 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
7a2cf670-e172-522e-bc95-82da5f236f2f | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
f94305a3-651c-5db7-9270-6e26e18ccd3f | note | Plan: +/- 200mm
cd6d3568-0c7a-52c7-bbfe-4c6e1c056914 | note | Level: +/- 20mm
bfe84377-67aa-5c5e-89dd-691815f4ab40 | note | HOLD POINT
17c0f20f-8894-5a8b-a4aa-f862fde4a8d3 | button | Acceptance | Yes,No,N/A
b85bcd9e-5e68-50fa-89ee-b564b9c3caca | note | Key - H
9742ac72-7e3d-5b8b-b4b2-a89b3082674c | note | UGL Key - W
4671c790-2dc8-5085-801c-2b4692611e02 | note | SHL Key - W
444bec38-97aa-570d-ae06-538e56227a62 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0f7fe90d-cd86-57bd-ba2d-8c56e7396e39 | tickbox | Survey report
| checkpoint | 5.2 - Acceptance and closure of non-conforming items
c65f1a4f-4561-5997-8a70-64b4be41718d | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
65f8bc45-f375-553d-ae9c-f64ef7a57f25 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
99b27de5-e7c3-58b1-b5b9-5458392645aa | note | HOLD POINT
b3e091ac-d9c7-5a68-8663-54fd29cbdb95 | button | Acceptance | Yes,No,N/A
30a86b2d-3e8e-5d9b-aafe-2dc6b3f09d03 | note | Key - H
2f1ceb4f-2931-5b74-8e1c-b839683278f3 | note | UGL Key - H
509b911a-7a2e-5c93-ae97-d5eab0c9c43d | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-012 Concrete Pavement Construction & Checklist - Rev.3 | itp | INF-HSEQ CC0375-ITP-012 Concrete Pavement Construction & Checklist - Rev.3 |  | b730bbeb-eff1-4268-b1b7-ad40b5d2301c
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Determine lot size
307c811a-5fbc-59af-8596-503fb6787a80 | note | Ref docs - Spec. 0161 Quality [Cl 7.15]
46d8d18e-9dc3-5051-a757-a5fdf1602d96 | note | Acceptance criteria - Lots to be broken up accordingly and outlined on a lot map
0b378aef-dc6f-5bcb-b385-5f4098868a7e | button | Acceptance | Yes,No,N/A
93d2d1d9-37bf-5e03-854d-2aa5c5752ec3 | note | Key - S |  |  | 0
78f91c22-2864-5a71-878b-e2ddf3f87a8c | note | HPP CON Key - S
e1bc950d-ec2e-563a-a0c0-4de746b69e8e | note | HPP QA Key - S
3a3e34f0-4e12-5047-bbce-e33ad24b5484 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1449469e-5859-5334-a34c-1fed99e64981 | tickbox | Lot map
| checkpoint | 1.2 - Material classification and source
fc895bda-3759-5d6b-9906-c72956c61ac5 | note | Ref docs - Drawings
e545fb53-7ee5-559a-8e9e-82ff7d50f73f | note | Acceptance criteria - Mix design to be approved prior to placement.
8af191aa-9956-58f6-b037-a7b54aa33b0f | note | ○ Material properties meet project specification.
a6d1013b-c3bf-55c4-8fd9-c53f728305a3 | note | – Minimum Concrete strength 32 MPa or as specified in Drawings
067fee68-3e3e-5f9e-af5f-fe40aa2bda89 | note | – Lean-mix concrete subbase (5MPa)
297e6c80-f6bc-5732-b29c-c49337a0fac2 | button | Acceptance | Yes,No,N/A
effef993-94f8-5430-a479-6a64f68e3f7c | note | Key - S
a79836bd-e8d3-5d9c-a73b-7d260d963332 | note | HPP CON Key - S
6403503d-5a72-5e84-ad74-19d317513946 | note | HPP QA Key - S
d40ed724-b966-5c96-873d-8be1a16f3ff6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
88da6589-7a64-5867-947f-39a35e5845ff | tickbox | Mix design
| section | 2.0 Concrete placement
| checkpoint | 2.1 - Set out
c6be84d6-944d-536d-80ce-a30d9643dab8 | note | Ref docs - Drawings
c0a92d4a-4a13-5b0a-b9df-052be752658c | note | Acceptance criteria - Extents and levels correct to relevant drawings
404020a6-1e58-5b79-b3c0-4e08d5c6880e | button | Acceptance | Yes,No,N/A
37662a81-77bc-5b8b-a699-8ef09fe1e41d | note | Key - S
c52533a2-0703-5b48-b49b-6b2373a7dcec | note | HPP CON Key - S
1d03c7b6-2045-5994-b606-ea560b6f2e30 | note | HPP QA Key - S
ce64ff36-b78f-5656-8b51-bcbbd1972ec2 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
dc524f5f-0cec-5ed3-8b9b-9cb4d591c979 | tickbox | Survey report
| checkpoint | 2.2 - Bedding preparation
9c6c4bd8-155f-599b-b10f-ee79157cb37a | note | Ref docs - Drawings
b8a7a89b-50d1-5027-8044-4156de361850 | note | Acceptance criteria - Loose material to be removed from the surface prior to pouring.
cab48b06-db2c-5da3-aca4-db2bf195bcae | note | ○ Waterproof membrane installed on subgrade prior to placement of lean-mix concrete.
8b1290ef-dafb-5f16-bf7c-d4efdc85640b | note | ○ Notice: 1 working day prior to covering
f8f6114c-08dd-5368-baa5-7393f116e71b | button | Acceptance | Yes,No,N/A
998bc4e8-8c45-543d-be06-aa3c5cc489c2 | note | Key - S
360ef244-80b8-5212-8b16-d6ac1cf91646 | note | HPP CON Key - S
2ac34b85-4350-5070-a889-5884298b1476 | note | HPP QA Key - S
| checkpoint | 2.3 - Conduit installation
6c36447d-17e7-5ab7-98bc-930d58ec8925 | note | Ref docs - Drawings
6f121488-00f5-592f-b21e-948f769e4699 | note | Acceptance criteria - Correct size electrical conduit as per drawings, to be installed before blinding layer
f71bdd77-adf3-5f4c-a6ef-e1f9c19a93d9 | button | Acceptance | Yes,No,N/A
01155124-5fa1-5cbd-98ac-d0b49aac7b80 | note | Key - S
1938b3b8-1180-55c7-b141-f4818f1a0768 | note | HPP CON Key - S
fe743349-162f-5077-8a1f-796dd75d4b0b | note | HPP QA Key - S
| checkpoint | 2.4 - Formwork set out and positioning correct
4fa3485c-bd2b-59ab-9bd8-b864e107221c | note | Ref docs - Drawings
3d1d75fd-cc5c-56e9-85ce-4c1dbdeb276c | note | Acceptance criteria - Ensure drawings have been checked and the set out is correct
5966685d-f319-5885-a828-87ed17a31579 | note | ○ Notice: 1 working day prior to covering
b759a564-73e5-520d-8f48-c8ca27415231 | button | Acceptance | Yes,No,N/A
98238e2e-b9f9-5429-8e58-ec3f2d3b18d6 | note | Key - S
a844b81c-0d13-59eb-9336-0f95fed84693 | note | HPP CON Key - S
475114e6-2f5d-5074-94d5-672bf8de97a1 | note | HPP QA Key - S
| checkpoint | 2.5 - Steel reinforcement
a4319f1f-2bf6-5fda-808a-5ec8db7aecd8 | note | Ref docs - Drawings
9389ee5a-ac9b-5e6d-aebb-e1b51597759b | note | Acceptance criteria - Steel reinforcement to be placed as per design drawings with the correct amount of cover.
7a429395-5188-522f-af50-1c1a5eac0f9d | note | ○ Concrete pre-pour inspection complete.
525a4c6f-0017-5393-baf8-540169301270 | note | ○ Notice: 2 working days prior to covering
fc56fbfa-9804-5613-8b2e-ac110053c780 | button | Acceptance | Yes,No,N/A
15da37a5-a20f-5a9c-a1b2-57c5bea77609 | note | Key - H
a1cce569-53c3-5f4e-a22e-ec2077acc19d | note | HPP CON Key - H
2eb77f63-21d7-504e-9810-6bb91ee8458f | note | HPP QA Key - W
1a9baafa-696e-52dc-b67e-24f1ca8d6258 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d5cd0ea6-5ebb-599d-bb1e-7b43da634015 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.6 - Concrete placement
b1b620f2-2d01-51bd-8ce3-b39f16cb36a1 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
e7498e14-0058-5693-a399-4e889dcce4d5 | note | Acceptance criteria - As per drawings concrete strength of cast in-situ units shall be min. Grade N32 or otherwise stated on drawings.
e02be3d8-c4e2-5cc8-85b5-fb181d0abe7b | note | ○ Placing of concrete ambient shade temperatures:
e63894cc-e921-56f6-8e28-2f576636077c | note | – Cold: < 10°C
78581616-a698-5a77-b471-5600fc7162a6 | note | – Hot: > 32°C
6146f3e3-dd19-5fdc-ae2b-39f15ba9d6b0 | note | ○ Cold weather: Placing
3c2dda82-ca3a-502a-80a3-bd986a0caa63 | note | – Concrete: Maintain the temperature of the freshly mixed concrete at ≥ 5°C
e1079d2d-d591-5eb8-9eb4-a5a48cd91664 | note | – Formwork and reinforcements: Before and during placing maintain temperature at ≥ 5°C
e3bae864-08c3-5a8d-9b9a-711d0c0e010f | note | ○ Hot weather placing table:
b3ac163d-3e27-5c91-935d-781eb0d96a90 | note | – – – – – – – – – – – – – – – –
99f59c16-c8b0-560c-b2c4-4363830a3235 | note | Concrete element ¦¦ Temperature limit
2ee589dc-fbda-57e5-9f89-dc57e034dc17 | note | – – – – – – – – – – – – – – – –
81974c67-8c58-56e9-afb1-d1f12af21554 | note | Normal concrete in footings, beams, columns, walls and slabs ¦¦ 35°C
ab62181c-1319-5c6d-b609-ab17e4da427a | note | Concrete in sections ≥ 1 m in all dimensions except for concrete of strength 40 MPa or greater, in sections exceeding 600 mm in thickness ¦¦ 27°C
5fc9febb-48a1-58d4-89d3-d6cbab54507c | note | – – – – – – – – – – – – – – – –
48af5a0d-4d98-5f0d-96a0-d4a3ae9af139 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
111c1ebf-092b-5844-b2de-e044df7dd32d | note | ○ Slump shall not exceed 75mm unless shown otherwise on the drawings.
8c9fa890-fd40-5b23-acf9-6718fb91080e | button | Acceptance | Yes,No,N/A
39ae2de9-9441-5d78-8c60-d8b1417eb117 | note | Key - S
f4ea824d-ec3e-5c36-af24-7b5ce732bc5f | note | HPP CON Key - S
7dff252a-4973-58b3-9e0d-c0c021e62494 | note | HPP QA Key - S
2cdb8b0a-de79-5db5-b9be-57a819699a34 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ee86e715-cee7-5d51-b7a7-f9fee6fcdee4 | tickbox | Delivery dockets
| checkpoint | 2.7 - Surface finish
4fb2ed57-05d9-5331-9c2c-62ddedd97248 | note | Ref docs - As per drawings
a10a79a6-eefb-5e77-8474-17fb8f90ab28 | note | Acceptance criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
6b11700d-9e65-5da5-8c28-71f075d47508 | button | Acceptance | Yes,No,N/A
a74fe2b6-f594-5249-bf35-fdd800d2be08 | note | Key - S
f6b32817-3171-56fd-87ec-b18a8b9b4a7d | note | HPP CON Key - S
6756df40-a981-5100-9b35-0af610028f72 | note | HPP QA Key - S
| checkpoint | 2.8 - Joints
9b7528d2-bdc8-5fa8-8076-f52c8bc85eeb | note | Ref docs - As per drawings
af5fcbda-5ba3-5cdd-bafe-ee1abd751ef7 | note | Acceptance criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
3cf7c10a-cde1-552b-8b39-52cc2cbf263a | button | Acceptance | Yes,No,N/A
a2b17388-6c2e-5bc2-9655-837d048a7f53 | note | Key - S
01a3ab4b-9ddf-531e-a6af-36f20f55d71a | note | HPP CON Key - S
3fea8ab3-7fb7-5aa8-81dc-bae4523196ce | note | HPP QA Key - S
| checkpoint | 2.9 - Curing
afc69dcf-06e6-5de7-a9df-1f49ebd70590 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
7229cd64-2f34-5b01-8f37-c589e462f112 | note | Acceptance criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
6c410520-8d3f-52c1-a751-703fe25a699d | button | Acceptance | Yes,No,N/A
56e1ea38-099c-5988-8e47-8b44b4eab20a | note | Key - S
9be23a07-cbae-5a23-8eb0-957805345d2f | note | HPP CON Key - S
82c3efd9-20f8-5fc3-8c2f-b90d045707c8 | note | HPP QA Key - S
| checkpoint | 2.10 - Compressive strength
61f42819-aa08-53ae-b7fe-bc2fe83969f7 | note | Ref docs - Drawings
fc83fab1-05a2-5c24-89df-119a3d40432c | note | Acceptance criteria - Average strength of all samples must exceed required value.
55dcbe8c-b8f2-5d54-ab04-68eb0b61d937 | note | ○ Strength of any one sample must be 0.85 the required value.
dfdd3534-0e30-5ee0-b023-5b926a06d35b | button | Acceptance | Yes,No,N/A
133a5e42-099f-5425-ac1e-6533a133a63c | note | Key - S
bc7ddc7e-244e-5b34-a079-b0aae6ad176e | note | HPP CON Key - S
1f8798b8-13de-5948-b0dc-a6f83c6a1c9b | note | HPP QA Key - S
2287cb6c-85fe-50df-8479-76dc57310dd4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
be387f20-c16e-50bf-b319-ad168b296896 | tickbox | Test reports
| section | 3.0 Conformance check
| checkpoint | 3.1 - Survey pick-up
eeae9b20-16d4-5672-a8ed-d251d93e605c | note | Ref docs - Spec. 0161 Quality (Construction) [Cl 3.13]
4e456479-2f00-520f-9670-28bba060c10e | note | Acceptance criteria - An as-built survey completed to ensure all structures are within construction tolerances.
c7c57c1c-ed48-5b98-9c96-03f71cc34167 | note | ○ Plan: +/- 30mm
687dbc2b-ca2a-57ef-9395-1579ebf0a3f3 | note | ○ Level: +/ 10mm
ebbb9410-72d0-5a67-977e-26402ddb84c2 | button | Acceptance | Yes,No,N/A
f5b3264d-d027-5de9-962a-95951017effd | note | Key - S
8212ec24-e2cd-5fbb-ae05-8d7da07eace2 | note | HPP CON Key - S
47f66b3a-1d94-56c7-9604-7944190585a5 | note | HPP QA Key - S
f11c48b8-639f-5de8-aefc-57248e639e9f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0e9fcbc7-935b-5589-a507-fde595412ae0 | textbox | Surveyor:
c115a393-0e55-574c-862f-908f86b14e2b | date | Date picked up:
| checklist | INF-HSEQ CC0375-ITP-014 Piles with Checklist Rev.4 | itp | INF-HSEQ CC0375-ITP-014 Piles with Checklist Rev.4 |  | e835eae4-11df-4f84-995e-d3c83fe1c76c
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
759b92e2-a8ff-53fe-ba97-47d6973469c6 | note | Ref docs - Issued drawings / Site copy drawings
1f7f5fa7-20e1-5a9e-8c7a-67d412790b6d | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
8652baa2-1298-54b0-a0c1-fcb64381cab8 | button | Acceptance | Yes,No,N/A
0ea19db8-dfed-582f-8373-345b2167d068 | note | Key - S
5b398d33-fa34-573f-98ea-73229df0d6c1 | note | UGL Key - S
| checkpoint | 1.2 - Determine lot size
e8549d01-b700-50c3-94d9-374c55f118b4 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
8a54e627-6cbd-5701-a90c-0323547a9129 | button | Acceptance | Yes,No,N/A
d9957f74-7b7a-580e-abb0-794fbae31ad1 | note | Key - S
7545c04b-c0b6-5f5f-93e8-d23c47a466d2 | note | UGL Key - S
7879e1be-7e52-5b7a-8d0c-1dd85adb2fce | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
b5acba0e-acea-51a4-b6c3-e7657d6d2d78 | tickbox | Lot map
| checkpoint | 1.3 - Geotechnical Engineer
255174e1-1d02-594e-80e6-690028c95c95 | note | Ref docs - Spec. 0003 Piling [Cl 2.7.1]
2e876a51-5eab-5e68-8fba-31bc794f0d43 | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience.
41afc3fe-a1c2-5ea1-8c60-d552ce181a95 | note | ○ 5+ Years Geotechnical Experience including CFA Pile installation
c385589a-c0cf-5e90-ac05-01004f45d2aa | button | Acceptance | Yes,No,N/A
c718ac41-01cf-5921-b41f-28067bb1e659 | note | Key - S
9ae287a0-d883-50c2-a6a5-8fa7679404b7 | note | UGL Key - S
| section | 2.0 Materials & Equipment
| checkpoint | 2.1 - Boring machine
3c3d4ae2-7a02-5266-b782-06b540b265b7 | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
7bb57bb4-1cd4-569d-abc8-7628b951bfa6 | note | Acceptance Criteria - Details of the boring machine and any other tools that may be required shall be provided for approval by the Superintendent
1035676e-b2ac-53f5-b4b3-f554ad82989f | note | HOLD POINT
d368a72e-a4b8-50ef-9f09-5c5d71d4f148 | button | Acceptance | Yes,No,N/A
d84d1500-5d93-5b85-8c92-b92fb59c1505 | note | Key - H
04780f44-4839-5ee6-96c8-30c6f2c200a0 | note | UGL Key - H
f7eadc60-3e4f-52a6-b9f3-fc82277e75f8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
aa2dd959-6332-5943-8ad0-d3f6475694ab | tickbox | Plant documents
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Approval of Concrete Mix Design
2815f80e-1f13-533e-8097-8305ab438143 | note | Ref docs - Spec. 0003 Piling [Cl 3.1.2]
fe982c8e-05ee-5033-a318-fd6f1863977b | note | Acceptance Criteria - Concrete Mix Code: S40/10/220 – Special Mix
0d7708ad-2dda-5069-9fd1-b19fa5499b41 | note | ○ Strength: 40MPa
ef768259-732b-5aeb-b851-5808ed42e97d | note | ○ Agg Size: not greater than 18mm
ea094abb-7a66-57e8-8bc8-37a0dcd21a03 | note | ○ Slump: not greater than 220mm
2b1bfefe-2532-59a3-8b90-998a0dc2f713 | note | ○ Required to achieve 25MPa @ 7 Days
4c82c5f8-d6e8-5380-98bb-a856ba12313b | note | HOLD POINT
92bcdf33-ba6f-5aa1-81a8-1dfb26b45541 | button | Acceptance | Yes,No,N/A
7f11d634-2d48-520e-a47e-694beaecd5e5 | note | Key - H
5578e3af-4b85-5b3d-92e4-8efc63a3e651 | note | UGL Key - H
b08aa235-c0e0-518d-a7ca-b0f8df25fef2 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0c7fa7a0-c309-5dcc-b8c1-ab5274cdcbba | tickbox | Mix design
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Pile Cage & Spacers
b5ce277b-5dab-5731-ad69-b7072b42174b | note | Ref docs - Drawings
6396ff64-6fcd-58b5-8813-404f9e493365 | note | Acceptance Criteria - Certificate of Compliance for Pile Cage
825dca7f-95a1-5c2f-aa3d-f8e1f909104b | note | ○ Cage Manufactured as per approved IFC Drawings and welding to approved weld procedure LOR-CJAUTO-12/20-250/500-1
653b80d3-7f24-5bca-a0d5-b8b34ba504eb | note | ○ Site splice weld as required IAW approved weld procedure WPS-CSS-014
1315d59d-9ad2-5b16-8449-fc1d750f9848 | note | HOLD POINT
2116fbd1-bd8c-5cde-b5d9-3aeb96f2c965 | button | Acceptance | Yes,No,N/A
7b8fd4c2-220a-5bf6-9fc6-59c7f4b54d84 | note | Key - H
21e95615-8b70-5d35-bbfa-5620cd2045a6 | note | UGL Key - H
44e7f603-80ac-5fc0-85f7-74ac6b5b66b7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
50cc7e84-f15b-5fbb-b1fc-4878b6a585cb | tickbox | Material certificates and COC
0a5bedf2-7df9-5c63-b8d8-df2187964c53 | tickbox | Site Daily Weld Repot
| signoff | AUTHORITY HOLDPOINT
| section | 3.0 Piling
| checkpoint | 3.1 - Survey Setout
f49f86d8-66f2-5328-8089-224ba3ca6841 | note | Ref docs - Spec. 0003 Piling [3.10], Drawings
184f0ef8-6374-54b0-83b3-657b331db588 | note | Acceptance Criteria - A registered surveyor shall be used to accurately located all pile locations as shown on the drawings and specifications.
d6e532e1-9f22-57a9-984d-74a56128c230 | button | Acceptance | Yes,No,N/A
94d2fcf1-e947-51c4-ab2e-4984e10ce0bd | note | Key - S
a96bba7e-6fff-5e7e-bc67-5430c8b135b9 | note | UGL Key - S
e82faa99-55a4-572b-926d-7152972baee3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bf21aa2c-8cea-5637-ba63-7037032ae326 | tickbox | Survey Report
| checkpoint | 3.2 - Concrete lines primed and in good order
5c2ee664-7d61-5325-a0df-3b081d9eae43 | note | Ref docs - Wagstaff WP-MS-09.3.07 [ Cl 6.2.1]
3ece6f12-c6e1-5d92-a55b-759eacd92765 | note | Acceptance Criteria - Inspect concrete liners have no damage and are primed correctly.
527ed809-94d5-5680-99c7-c82463466450 | button | Acceptance | Yes,No,N/A
eed04f08-ed87-5820-afbe-8216f9cec143 | note | Key - S
a7f03a6f-2c97-553e-b8f2-a8eb7f5bcfa7 | note | UGL Key - S
| checkpoint | 3.3 - Excavation of bore hole
6e4ca09d-c0e4-55b2-807a-31c4e74b2ac5 | note | Ref docs - Spec. 0003 Piling [Cl 3.3], Drawings
9fb6edb1-e8ea-523a-9d3b-0f75942467f2 | note | Acceptance Criteria - Verify: (via Pile Rig)
1756b181-36f8-56a4-b76b-b2891396f82d | note | – Inclination. +/- 4%
3eb7d374-e09a-5e77-bf11-5d33754f3f82 | note | – Diameter: 900mm
edcd1da7-c5c1-56e5-9660-0468c747944c | note | – Depth: Refer to drawings for min. depth into socket material
97378cad-d03f-503a-8abd-8ac98d7d4829 | note | – The tolerances on the level of the bottom of the piles shall be +0, -100mm from the RL nominated on the drawings or as directed by the Superintendent
5dc19090-5c22-5efb-b14e-3ccf1a22bca5 | note | – Length of pile/pile liner shall not be less than total length shown on drawings
2ff48166-c930-5a41-88a4-6008d5f43dc5 | button | Acceptance | Yes,No,N/A
4674aefb-353f-5cb6-903a-9b724e70ce06 | note | Key - S
6acd9cd2-23ac-57f2-87cd-100e35e08276 | note | UGL Key - S
695a6b8a-2666-5062-9f46-e91aa2cee700 | note | SHL Key - W
9ce04fc9-8493-5ffa-8c13-7bde62b5437b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9fdf29cc-afbd-5b73-82f0-aa268b715323 | tickbox | Pile Log Sheets
| checkpoint | 3.4 - Excavation conformance
6ede19d9-f918-5bae-9409-f55c40e21551 | note | Ref docs - Drawings
1d7c3333-2b41-5fb2-a892-f4e99bc63ebe | note | Acceptance Criteria - Check dimensions and cover are within tolerance refer to below conformance check section for details. Correct toe level as per plan. Material encountered consistent with design. Softened soil shall be removed from the bottom of the drill holes.
602e6c91-2f9b-5ade-a15e-6ff0e5023ff7 | button | Acceptance | Yes,No,N/A
7948bc18-f14f-50cb-9542-3a4e8d090cf3 | note | Key - S
05b68a63-7c07-5738-8aed-214be7fb8c37 | note | UGL Key - S
6b1d5a26-0211-5da5-b8e9-de65a624dc7c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a67e551b-cc6c-5c4e-80a3-d7aa1ff13692 | tickbox | Pile Log Sheets
| checkpoint | 3.5 - Examination of borehole
751c918c-4634-5478-be4a-665fc8dfbed4 | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
3b759c44-3c11-5896-a459-457913c92e73 | note | Acceptance Criteria - Boreholes excavations shall be inspected as the work proceeds. When the founding level as shown on the drawings or as otherwise directed has been reached, each hole will be subject to a visual examination (or other methods of examination) by a Geotechnical Engineer appointed by the superintendent.
eb394a4c-024c-5da5-90cf-2b9e7c1f3530 | note | ○ The Geotechnical Engineer will advise whether a satisfactory founding level exist or whether further excavation is required.
b5db4c64-d2d0-5d97-970c-6a8eb1f84d26 | note | HOLD POINT
6f5258d5-45cd-5950-bdfb-85bfa25cc8ef | button | Acceptance | Yes,No,N/A
0c13c1e7-8596-51cf-aab0-f061a709ac1d | note | Key - H
e5690cec-037a-58fd-adf1-e489583f7c9a | note | UGL Key - H
c69d6824-200a-551d-ab48-7d449df4330d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bd94c1f2-cd97-5155-8391-bf31588fa384 | tickbox | Geotechnical Engineer Sign Off Sheets
d65ff8b6-65d1-5659-84fa-448ffc592ba0 | tickbox | Pile Log Sheets
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.6 - Concrete supply
8d960b30-136f-599f-af43-6f4081d5cf01 | note | Ref docs - Spec. 0003 Piling [3.9]
524c62ee-c6e1-5d10-b32a-a7cce7f2f260 | note | Acceptance Criteria - Verify:
65940216-dd57-540e-a596-0cb816c5c91e | note | Concrete mix
d3352389-b87f-5279-b765-86e03fd8203b | note | ○ 40 MPa 10mm 220mm TREMMIE [N545526]
86cc3c22-19e0-517a-9329-e110bd35df03 | note | ○ 65 MPa 10mm 220mm TREMMIE [N876626]
54d01b78-410a-514e-b8fd-d03735c87f2a | note | A concrete delivery docket to be supplied with each batch delivered.
52e55c22-8873-5fd0-bd44-02a4e48393e1 | button | Acceptance | Yes,No,N/A
ea03b2d6-db08-522d-90b7-e530d4f6c7f8 | note | Key - S
30e37087-cf6a-560e-9976-20096bf6f98b | note | UGL Key - W
1bd3ca14-25ae-5542-b40c-a7eae138e189 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
31ef9eae-5ec4-5923-968e-45cd33600c08 | tickbox | Material dockets
7e258bc4-74b5-5255-991f-4383603f3f11 | tickbox | Concrete Pour Records
| checkpoint | 3.7 - Concrete Sampling
3a6c65bf-bf0b-5150-ac15-1d599cc16dfe | note | Ref docs - Spec. 0003 Piling [3.9] Spec 0002 Concrete Supply, Construction and Grouting [10.2.3]
5ed471a0-9362-5b90-833d-59c791193a8a | note | Acceptance Criteria - The nominal rate of sampling shall be taken after the concrete has been discharged at site prior to handling:
0649ec6a-c23b-5a5f-a12f-ac4a34a53d47 | note | (a) Compressive strength (1 x 7 day and 2 x 28 day cylinders): One set per pour or as otherwise directed by Superintendent;
de9939d0-d326-54d8-9367-a9b715d6f624 | note | (b) Slump: One per batch of concrete
e45e05f7-e068-5b05-83e4-d6e8528214c4 | note | ○ Acceptance Testing shall be done at a NATA registered laboratory
ab3380f3-938a-5a70-850c-90b901cb08fc | button | Acceptance | Yes,No,N/A
730edf9d-229d-56f9-bd85-f8fce696b1cd | note | Key - S
709f15b7-67b4-5650-bd78-f08ff1a95cc8 | note | UGL Key - W
| checkpoint | 3.8 - Concrete Placement
7f6c3370-c887-5c93-9ef3-5074343958b1 | note | Ref docs - Spec. 0003 Piling [3.9]
2cb62bc9-b65c-564b-99cb-f4ab64b3b7ff | note | Acceptance Criteria - All concrete shall be placed continuously and in the dry so as to ensure the exclusion of all harmful materials and provide a well-formed dense unit of full cross-section without voids or segregation.
18405182-308b-5123-b9a2-1d3abb6db56b | note | ○ All concrete shall be placed by approved methods to limit free fall of concrete to a maximum of 3.0m
e380b84d-3e6a-5d1a-9cdc-7c2d354c5fa6 | note | ○ Top of 3m of concrete shall be well compacted with a high-capacity vibrator with a min. diameter of 50mm
d2ed76a4-0cb5-5572-9fed-fa7ea0dfbdf9 | note | Notice: 1 working day prior to placing concrete for test pile
a340b417-f304-59dd-be30-7bd3dd8a75a1 | note | WITNESS POINT
7e96afac-ef3d-57e5-9136-b1da36cf1eae | button | Acceptance | Yes,No,N/A
54d0552e-b178-5d16-a006-cd66caae3b1f | note | Key - S
e2b98283-70aa-55e2-ad9c-574672673526 | note | UGL Key - W
8f359a13-4eb2-5960-ade0-0bc53664fa94 | note | SHL Key - W
ab5d78e9-3e56-51f3-8c93-4d0a223314b6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6cd0486e-83a9-567a-a88c-c4570828be8e | tickbox | Concrete Pour Records
| checkpoint | 3.9 - Concrete testing
57927eee-6974-54ba-816f-6828c0ee4517 | note | Ref docs - Drawings
c07ad77a-2b4f-5ddd-8bd6-d3e0a4ae2cfc | note | Acceptance Criteria - Concrete test reports achieve design requirements
a36e85ab-f7e2-5e0c-8f1c-cb18583ea555 | button | Acceptance | Yes,No,N/A
bb8685fe-5921-5850-a27c-34c54d132b60 | note | Key - S
f9df19cb-4ef2-565c-9df2-7649738df222 | note | UGL Key - S
c34c5839-2398-5d92-8290-00adb4f03ec6 | note | SHL Key - R
f96e7ea1-71e7-5cff-a912-45630e6f1653 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ef58dab2-e6c7-509f-852a-312cc7b7daf5 | tickbox | Test reports
| checkpoint | 3.10 - Placement of reinforcement cage.
97a3e3e2-0b25-54cf-b055-3c14f36b2636 | note | Ref docs - Spec. 0003 Piling [Cl. 3.2.2, 3.8], Drawings
259c4f37-5a23-51a6-b4a7-b5bfb403a204 | note | Acceptance Criteria - Ensure that cage is clean and straight. Plunge the cage centrally to pile hole and ensure spacers are attached at correct locations.
b876e97f-01e5-547b-a318-b4da38108fff | note | ○ Reinforcement cages and embedment to conform with drawings and specification.
31aba693-03e9-5d78-a989-21dca6022bca | note | Notice: 1 working day prior to installation of each pile
d356712c-1bb2-535e-8f13-f579dd80ef68 | note | WITNESS POINT
fad83241-07bf-5d96-b511-c0b972f1349f | button | Acceptance | Yes,No,N/A
dd4c1ca0-39af-52d4-b589-172c1a6caf48 | note | Key - S
c7418b33-6db4-530b-8615-61913a08607f | note | UGL Key - W
69c8e42d-efe2-521b-8a6d-9e16e3f7fdec | note | SHL Key - W
b3217662-010b-59d4-80d8-9b72543ce764 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d1befda8-bc96-5341-9194-0545b9db96fa | tickbox | Pile Log Sheets
| checkpoint | 3.11 - Concrete RL and depth
23a76afe-644f-5223-9456-bfd83723fece | note | Ref docs - Drawings
d7176361-dcb3-5881-9636-f3e4a5a8f07f | note | Acceptance Criteria - Bored piers depth, size, position and concrete RL as per the Piling Pile Log Sheet and Drawings.
1eda28fb-fc86-5eba-ae4b-43c89ee88694 | button | Acceptance | Yes,No,N/A
5c73f4f2-77d3-5dbc-beef-c69a33d3a8e9 | note | Key - S
c57dad27-ffd5-589b-b920-71c178b84acc | note | UGL Key - S
db059bf5-85d7-593d-bea4-8d0830368268 | note | SHL Key - R
46d330b3-9d65-5b5c-bf78-3cf29ccbb1c3 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
63873dbb-c90a-50df-b291-10786d94aa41 | tickbox | Pile Log Sheets
| section | 4.0 Integrity Testing - Dynamic
| checkpoint | 4.1 - Pile Testing
17b36df7-5610-5c8d-8474-dba61c44c30e | note | Ref docs - AS 2159:2009, Spec. 0003 Piling [Cl 3.13 (5)], WP-MS-09.3.30 Low Strain Dynamic Testing
50f07fcc-8990-501e-83d9-dd1b6574524d | note | Acceptance Criteria - Minimum 5% sample size
ecc3f179-b8e2-51e8-92e1-2e9975dc7e48 | note | ○ Pile Integrity testing (PIT) as per Wagstaff Procedure WP-MS-09.3.30 Low Strain Dynamic Testing.
31412fdc-aa71-5aff-b894-975248c2e54f | note | Notice – 3 working days to commence testing
3fc80601-4580-5be1-bc59-22d42055fd40 | note | HOLD POINT
f756a290-0acd-5437-ae37-6031ae8c7d96 | button | Acceptance | Yes,No,N/A
6fbe58b6-9291-5670-97e7-42c390154690 | note | Key - H
70031fb2-f318-50c4-8ccc-34ed099df570 | note | UGL Key - H
3401ffdb-d564-56c7-a308-3963f7486943 | note | SHL Key - R
81b93211-d254-5a91-a78c-5edfc5cf1cd6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
55014ad5-b45e-5b16-a217-e2053ac23ef9 | tickbox | Integrity Test Reports
| signoff | AUTHORITY HOLDPOINT
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey
0a526f08-650d-57f8-9a2a-789208165ab2 | note | Ref docs - Spec. 0003 Piling [3.10]
3f5592d6-915c-59d4-9d39-d632f4a16b0e | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
e3485e79-7643-5e0b-ae66-27efc5a6fa63 | note | – The centreline at the top of the piles shall be within 50mm of the specified position
48d074cc-eb80-5bbe-a832-e31799f389b6 | note | – The inclination of the pile shaft shall be within ± 4% of the nominated inclination
7a369edd-f348-576b-838a-54ebedeebab9 | note | – The tolerance on the level of the top of the piles shall be ± 10mm
cb7eed98-80d5-5726-ba76-2bd4ef0c8d74 | note | – The tolerances on the level of the bottom of the piles shall be +0, -100mm from the RL nominated on the drawings or as directed by the Superintendent
6e4c9fdf-1fe1-5118-8bef-8b54bed7ab52 | note | – Piles shall be constructed to the minimum diameters specified on the drawings
14f6266f-b0ae-523a-a58f-92bed723b51b | note | – Length of pile/pile liner shall not be less than total length shown on drawings
757bb383-f9f7-5fe8-b285-1fb6768e09f4 | note | – Maximum bow of pile shall be 0.1% of length
c0e96318-b276-5134-9842-34b484892893 | note | – The projection of the pile cage bars above the cut-off shall be ± 25mm from the nominated level
f17710c9-4884-59fe-96e5-c3dfaf73b584 | button | Acceptance | Yes,No,N/A
e9323d57-127d-5bf5-9273-29475bcd6544 | note | Key - H
260d1403-fd50-5945-8f47-71135b145c29 | note | UGL Key - H
099bb331-cc9d-5b7e-a5fc-09bd3734e242 | note | SHL Key - H
8cb75bcf-6eba-569f-b2da-2446062351a5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
728af371-aba2-55f7-b336-8db39bbb1916 | tickbox | As-Built Surveys
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Acceptance and closure of non-conforming items
34f73e26-0963-5964-9b10-276b43ceda2a | note | Ref docs - Spec. 0161 Quality [CL 3.8]
123eb711-9971-5bd4-87a0-c1f64752fd91 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
dbee7849-413c-543a-b2d2-702ff5cf3850 | note | HOLD POINT
0fcbce47-b530-51e1-94f7-0e338370dcbf | button | Acceptance | Yes,No,N/A
909fa3d5-355e-5fb4-99cd-cb2759495fdf | note | Key - H
8158d287-6083-54af-b274-26813c0d1e57 | note | UGL Key - H
423e1fb7-335a-5433-bb08-4c4acdbe6569 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-015 FRP Works (Structures) & Checklist - Rev.7 | itp | INF-HSEQ CC0375-ITP-015 FRP Works (Structures) & Checklist - Rev.7 |  | 12afd405-da64-4e19-98f1-187dc3b12406
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
d02148e4-76bf-527c-ac3e-b0c803b30a54 | note | Ref docs - Issued drawings / Site copy drawings
557e59b6-ca20-55bc-82d7-986d6acc25f0 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
8773b788-06c0-5ad5-af96-35ad65030ea1 | button | Acceptance | Yes,No,N/A
2f81033d-11cc-56c1-b3b4-d455966e450c | note | Key - S
dbe8be94-e2b5-5028-a15c-00b2b1523444 | note | UGL Key - S
8802a477-6ba6-5f82-b922-51de244cc978 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
7b4865af-eef6-5848-b9dd-de5aab1ef48d | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
ac255880-00ba-5d0f-99fa-ed0ab9b4f051 | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
0605cc47-c5ea-5cbf-a758-1deb8b2d2747 | button | Acceptance | Yes,No,N/A
8a32006d-62d1-542d-b8d5-266768fa2a3c | note | Key - S
ac7720ec-fc0e-5370-9159-b6e2a98b7eeb | note | UGL Key - S
e1488b99-6b9e-5871-b975-93fc06c19187 | note | SHL Key - S
| checkpoint | 1.3 - Set out
b52110b2-d380-59d4-a150-f8d9d8488d74 | note | Ref docs - Drawings
bb0cae5f-9a30-51d4-a1e8-f375511d2608 | note | Acceptance Criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
7433ae24-947c-5dc7-83ec-38f82cb08d89 | button | Acceptance | Yes,No,N/A
f4788699-ff0c-5e80-92c2-e65ea7d4341a | note | Key - S
5057e893-01ee-5cac-be3e-f7351e810c13 | note | UGL Key - S
187ac2f2-a18f-5ead-8967-fb472ef3e4c7 | note | SHL Key - S
| checkpoint | 1.4 - Underlying Lot Conformance
2d0b2d4f-e693-5b1d-9e99-041e8c8b68a6 | note | Ref docs - Underlying Lot ITP
3e957f67-0178-5684-98d8-c9aec23b4ca8 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
cf265676-efe0-54c7-8bfe-83e71de2633a | button | Acceptance | Yes,No,N/A
0774cec0-27e0-5bbd-a9a9-296b3115fbc3 | note | Key - S
6dacb4b0-c0b5-5ed6-8987-c44af29d3312 | note | UGL Key - S
7fea661d-c1a7-5676-99e7-a563696b605b | note | SHL Key - S
| section | 2.0 Excavation and bedding
| checkpoint | 2.1 - Excavation
bc9df847-688f-5105-9043-2e2fb51cca0d | note | Acceptance Criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
0ac153f5-9818-5e32-a531-a642693947ab | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
0a9b3b2e-87fc-59f1-a4cd-9c0ec361e2c9 | button | Acceptance | Yes,No,N/A
a4f6d45d-a099-578f-b8d0-0a8565876879 | note | Key - S
57791f77-6584-572e-8c99-c8d2460c2c5a | note | UGL Key - S
eef4c5d7-6313-5150-a6d0-8ca1e71d676c | note | SHL Key - S
| checkpoint | 2.2 - Unsuitable Material
6b996e20-4adf-5a5c-ab76-92d7ca93b945 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.6]
6381c62e-8117-54a8-b5dd-71aeb5bbb993 | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
1ab47ce7-1a5a-56da-b181-b7d1b78e6515 | note | HOLD POINT
fce682c3-4686-54ce-858d-6faafd08b15d | button | Acceptance | Yes,No,N/A
3d0791f3-7f61-565d-bde5-59cb52526c5c | note | Key - H
223e17a9-e2ea-597b-b2b8-93878eb9b7a3 | note | UGL Key - H
cbbe94df-1de7-504e-9a71-73f09bc762e2 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Compaction - Foundation
466ff5f6-9c92-5262-92e1-3b0bd1e8e91b | note | Ref docs - Spec. 1112 Earthworks [Cl 4.7, 4.13] Spec 0161 [CL 7.2]
06892e50-060a-5fcb-8e08-8a6a571f545e | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 97% modified to a depth of 200mm below foundation level
fb5d1a06-22fb-5822-a2a9-985ea09f6246 | note | ○ Test Frequency = 1 per 500m2
44b7a3f1-0085-5a99-93e6-f30398d4d997 | button | Acceptance | Yes,No,N/A
f0646193-5d5c-53bd-ac2d-8853f9d3d225 | note | Key - S
0242ae6e-af61-5d37-91c0-2741caedc82f | note | UGL Key - S
dc7a336c-0e52-52e6-a3cb-92683c4b264b | note | SHL Key - S
e7441847-477f-5945-b52c-fe184d4331af | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9eee0f75-427e-580e-b07d-4e7580121098 | tickbox | Test reports
| checkpoint | 2.4 - Foundation Inspection
e8e5549d-e9a6-5f66-a0f7-26a6f0bbde28 | note | Ref docs - Spec. 1112 Earthworks [4.7]
63b17777-52bc-51f4-a493-ab849e72b68d | note | Acceptance Criteria - Foundation to be inspected by the Superintendent prior to placing blinding
21a1a2d0-73dd-544b-8888-ac84a02692f2 | note | HOLD POINT
38d7b776-b505-5dfe-a476-692c26235ae0 | button | Acceptance | Yes,No,N/A
1cca8e88-7668-5cff-bab2-fac9ec0a6547 | note | Key - H
72d0065c-5484-5646-9d1f-37018c55411a | note | UGL Key - H
b2c2cf30-87e6-543a-8971-48bb450b3661 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Blinding
a2545660-86a3-5870-8c56-60aa31408e27 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
eb67bdc5-3e3a-5404-8029-33ff7e386452 | note | Acceptance Criteria - Blinding (N15) for Reinforced Concrete Bases to be a 100mm thick mass concrete layer or as otherwise shown on the drawings.
b259dfa7-2578-52b6-b320-627b569f77d8 | note | ○ Unreinforced bases can be poured directly on the earth
bc1b58f1-8ee2-5c26-bca3-bd99dc561323 | button | Acceptance | Yes,No,N/A
61863c85-7028-559a-afa5-dad3525e8e86 | note | Key - S
33741f61-f74e-5a05-8c87-6e197c31a884 | note | UGL Key - S
8fb77736-479a-536a-ab36-91f8bd0077dd | note | SHL Key - S
| checkpoint | 2.6 - Mating Concrete Surface Preparation
014058b8-3e66-55c2-9597-5067fa59f166 | note | Ref docs - Spec. 0002 [CL 3.9]
2a77f820-1903-5f77-91b7-488d521cad59 | note | Acceptance Criteria - Construction joints prepared and free of loose material
7c941c0f-6b32-52cf-bbf1-13e585b4a7c6 | note | ○ Dowelled joints prepared and bond breaker applied for expansion joints if applicable
72301dc7-57e5-57aa-be41-d97525f7ee1f | button | Acceptance | Yes,No,N/A
a9761d1d-14b5-5ba7-bb2e-c643aba70195 | note | Key - S
c00696cb-776f-513c-b779-7ac7afe55b1b | note | UGL Key - S
2d21b50c-390d-5ef5-baae-ff524f35d29e | note | SHL Key - S
| section | 3.0 Installation of cast in-situ structures
| checkpoint | 3.1 - Formwork
f086adf7-8ab0-5271-a5ef-de700ce460fd | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.0], Drawings
52ec8c9f-e0ff-50c3-9f87-742ebe8d5fe2 | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
40abe801-9e32-504d-922d-ab8f04434b50 | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
c375ad68-987e-5164-b9e5-2e201741f678 | note | ○ Formwork engineers inspection certificate complete and received
e69e14a8-06ba-5f80-8e7d-cbdc0ee333bf | note | HOLD POINT
6e9507e6-081e-5606-a8f1-3e80dc4ce462 | note | Before Placing Concrete
c3fe19d9-d56a-5209-b968-e1a4f140d80a | button | Acceptance | Yes,No,N/A
b209f27e-058f-5660-a5e5-a86da15949f6 | note | Key - H
38cd80c2-2b5a-5b1e-a77f-a075e5ebc2be | note | UGL Key - H
58a48d50-2083-54e8-8a25-ba50814b480f | note | SHL Key - H
c9a31f98-4818-5c00-b417-ae1ae4dfb698 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e2803bd6-387e-5f4e-a6eb-7e5a02b329fe | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Steel reinforcement
d6a26407-b061-5e28-b84b-695610478a6d | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.0], Drawings
ef688f89-60eb-5051-b589-1720c3116fed | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars. Inspection per layer installed.
133ad2ae-472c-52db-a880-d21af6e01b09 | note | ○ Concrete pre-pour inspection complete.
70152781-dc5e-5cf8-ab7c-cf53661567f5 | note | HOLD POINT
bdc10d8a-944c-5c6e-b189-3e03db1157a1 | note | Before Placing Concrete
02dc72e3-0e31-52ce-9b09-a7c4ac8dd1d0 | button | Acceptance | Yes,No,N/A
804d7420-e748-5f31-ab01-c776a559c174 | note | Key - H
22aa627c-5dc4-5dd4-b301-4a863783fe8f | note | UGL Key - H
3abdc47d-1fb9-5cd3-8f3b-57633280e20b | note | SHL Key - H
bdb43c0c-6a5f-5ab9-a87d-8d15f7e4d249 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
cb32b5c9-5f36-5fba-9e40-b7333c1268a4 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Reinforcement Splice Lengths
b8fe3a01-ab67-5d00-bd6c-a750eff2af5a | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.7]
f03494b6-0322-5506-9e96-95a92a07cc12 | note | Acceptance Criteria - Where splicing of reinforcement is not shown on drawings min. lap lengths shown below shall be adopted. (SPT-0002 Table 6)
571fc8bb-6809-53d9-966e-3e5d52c6af69 | note | – – – – – – – – – – – – – – – –
b36559f9-7f94-5da6-adea-29924c42d1f5 | note | Table 6 Reinforcement Splice Lengths
b15e6c17-1efe-5013-8dd3-213b11170fab | note | – – – – – – – – – – – – – – – –
e85b4f4d-3f21-51e6-81b0-38730a053e8a | note | Reinforcement Size ¦¦ Lap Length (mm)
5f4dbc3e-3c4b-5946-9967-d614190c1dcc | note | – – – – – – – – – – – – – – – –
2e927fd1-aa8a-5270-bf4a-670cdf8b824e | note | N12 deformed bar ¦¦ 500
d648ef04-9503-59e2-8f68-158aa6ca8959 | note | N16 deformed bar ¦¦ 800
7480f6b6-15cb-5178-9551-af7088d9aa30 | note | N20 deformed bar ¦¦ 1150
0b441248-65ee-5dd8-96e0-10d1cf226497 | note | N24 deformed bar ¦¦ 1350
75275349-1859-5211-8bea-6653b224e088 | note | N28 deformed bar ¦¦ 1600
3fc862a8-8bec-570e-a610-ada750de53fa | note | Welded wire fabric ¦¦ 225*Minimum 2 cross wires
2d55374c-00b0-5603-8ce1-9696187fc8fd | note | Trench mesh ¦¦ 500
180f2506-2961-5bce-bb82-a57b9190cef4 | note | – – – – – – – – – – – – – – – –
e8d833b7-a9b4-5463-9298-1e77381dccf6 | button | Acceptance | Yes,No,N/A
20abee87-862a-57da-9ab3-5f89c03712fe | note | Key - S
8a59565d-2aa8-53fc-9565-73ca9dafeca7 | note | UGL Key - S
0e92a123-b418-5c4e-b340-a275587bb960 | note | SHL Key - S
| checkpoint | 3.4 - Pit & Pipe Connections
025c9242-660b-53f9-a66d-2d9616b2c546 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3], Spec. 0002 Concrete supply, construction, and grouting [Cl 2.6], Drawings
085c6f7e-12c5-5b31-ad24-e4b3bc5659fc | note | Acceptance Criteria - Inlet and outlet pipes to be integrally cast into foundation/pit walls and the joint waterproofed as per design requirements.
dee824c3-66c3-5881-ac1f-fae1ea7ac607 | note | ○ Embedded pipes to be adequately restrained against flotation
d57243c4-118b-5086-a594-60a6cc1b3e9c | note | HOLD POINT
7042a272-61ba-5111-bc84-d4ddf642803b | button | Acceptance | Yes,No,N/A
3700a480-7f3c-5b9a-94c5-5192d0d2244f | note | Key - H
8475ae73-584b-505e-bdd8-f666346f151f | note | UGL Key - H
bb841c4d-1dc6-5276-8c4a-690e14fef873 | note | SHL Key - W
0928c6b9-0ea3-5e7a-9533-b96b1848efe0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - ITP for associated pit/pipe reviewed for conformance
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Installation of Core Holes, Voids, HD Bolts and Embedments
769730c5-a288-51a7-a842-e52c8d91bd61 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
61da65a2-86a1-5ccb-ac01-0f0efdb5394a | note | Acceptance Criteria - Firmly Fixed in position in all directions
86747513-6a4f-52d5-9794-889cd2ea988b | note | ○ Reinforcement displaced where necessary, bars requiring cutting approved by superintendent
6020f86a-2866-5a5a-ab84-9bce9daed9bd | note | ○ Integrity of surface treatments maintained (galvanising, painting etc)
dc553281-de25-5a25-b0ad-60164e5d7831 | note | ○ Threads covered
879d19d4-cc94-58b0-80bb-da901d607c32 | button | Acceptance | Yes,No,N/A
39c137f0-7279-59a3-8aff-d43295cb024a | note | Key - S
3eb653bd-62b0-53b8-a636-8f36da4a46dc | note | UGL Key - S
980cf9e9-5c78-5cb9-b628-56b519d57845 | note | SHL Key - S
| checkpoint | 3.6 - Tolerances of Core Holes, HD Bolts and Embedments
1ef40727-7501-57eb-aef7-27b11cd19172 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
fd512a4b-4f73-5721-81a8-c34b2bbfa591 | note | Acceptance Criteria - HD bolts positioned using a template. Tolerance for HD bolts as per CL 7.2 (see below table)
f00d3552-0d20-5d06-bd8e-4418a096dc7e | note | – – – – – – – – – – – – – – – –
85b17883-c18d-5a82-911e-5d054da719c5 | note | Condition ¦¦ Tolerance
7a74d9c6-703c-55a5-9363-e36da081e8c5 | note | – – – – – – – – – – – – – – – –
04d744b7-c580-56f2-9848-64f68f4bf9e2 | note | Any 2 bolts within a group ¦¦ ± 3mm Centre to Centre
b5db0a53-7cf7-57b0-b29c-5b9428886253 | note | Adjacent HD bolt groups ¦¦ ± 6mm Centre to Centre
c5d345c7-6426-5ff3-ab96-dca3386f50c0 | note | Bolt Projections - From concrete level ¦¦ + 5mm, -0mm
4ad20b3b-d9be-513b-bf27-4d7d920ca64b | note | Embedded steel finishing flush with surface ¦¦ ± 3mm from surface
2a78d256-801e-5241-a0d1-3f1550ca18a0 | note | Bolt reduced level ¦¦ + 5mm, -0mm
11af52cc-74b4-535b-9149-620541687309 | note | Verticality of any bolt ¦¦ 1:300
1404fa69-7b48-570d-a1a4-b746d7392ebd | note | Maximum accumulation of 6 mm per 30,000mm along an established column line of multiple HD bolt groups, but not exceed a total of 25 mm.
d03869c4-bd35-5987-96a2-9831a4769348 | note | 6 mm from the centre of any HD bolt group to the established column line through that group.
3054a8df-8a2a-5aa2-9397-077d43f05786 | note | – – – – – – – – – – – – – – – –
f5468fa6-5d8e-5294-816c-edb5a164ea3a | note | *Before poruing concrete of the GT & GEN foundation, MPW TA will check the setting condition of GT & GEN anchor bolt. Witness Point as per MHI ITP.
1a909a8d-af74-5d86-9f65-1693b3b6c28b | note | ○ Tolerances for other embedded fabricated items in line with AS 3990 or AS4100 as applicable.
b49cd147-29c0-5da6-89c4-06f65ad629a2 | note | ○ Pre-pour survey performed and recorded to verify location
7dca92ae-980a-589d-8907-b5a6fcea628a | note | HOLD POINT
925de734-2d0e-547e-a831-62278c98929e | button | Acceptance | Yes,No,N/A
a0d40960-3d1f-5d19-b22c-1a81e75fe0ce | note | Key - H
5370fc6f-c4a7-5396-9732-0a78c4ff398e | note | UGL Key - H
5426f039-4709-55f3-9950-97796f08be97 | note | SHL Key - W
f059ee1b-591b-5575-be78-0320427d1b4b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f669cfe0-2bf9-5a58-a925-4dfdddb084b5 | tickbox | Pre-pour inspection and Survey Records Inc MHI Check Sheet for GT & GTG Anchor Bolt Setting CG-64294
| checkpoint | 3.7 - Earthing for Concrete Structures
38195817-04ed-563f-b2d8-09d597ded1a2 | note | Ref docs - Drawings Spec. 0002 Concrete supply, construction, and grouting [CL 2.6]
ba360a78-c507-5952-8728-bd4ff3063c11 | note | Acceptance Criteria - Earthing installed for concrete structures as per provided Drawings
2507d19f-1ee4-5eba-8b4b-759447d122ce | note | HOLD POINT
bff0a028-1e76-5099-a3f4-1d0acd1e7582 | button | Acceptance | Yes,No,N/A
5a6a04b9-98ed-5113-bb9e-60b1b0e4fc46 | note | Key - H
85ed65f8-73f0-5f10-9a0b-498a1f13130d | note | UGL Key - H
1311df57-d509-5448-92b9-dbf2a2a2b942 | note | SHL Key - W
fb5a6268-8c7a-5c10-beb7-783b5a71c57e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1ac0c9c0-6938-57be-a82c-f48dfb4a35cc | tickbox | UGL Earthing FIC
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.8 - Concrete Mix and properties
aacd227d-7c65-5019-a4be-f585dced14d3 | note | Acceptance Criteria -
381b0ac8-4a54-578d-89f6-1e737893ebe6 | textbox | Concrete compressive strength required (28 days) = |  |  | MPA
208925a9-41c2-516a-812c-4b1026624daf | textbox | Approved Concrete mix ID =
164d6bd3-8eeb-5c11-80af-1a49b28a0299 | textbox | Slump = |  |  | mm
0a18a453-c2b8-584d-927d-21b31ad95383 | button | Acceptance | Yes,No,N/A
ee3d4a2f-146f-55a0-842a-e57001b74a3a | note | Key - S
76ec3611-aad9-5255-a869-2457b09fb028 | note | UGL Key - S
5040019b-3f65-558c-b04d-cb96564b5da2 | note | SHL Key - S
321b8f62-9b49-554d-9e37-8a0218d383c8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
65acb076-f826-5b2f-a851-31d10aec19bb | tickbox | Material dockets
ebe85780-452a-5934-9bdc-45e9d3cb333f | tickbox | Concrete pour records
| checkpoint | 3.9a - Concrete Supply Temperature - GT Foundation Only
e0cc7b6c-e35f-5eb5-a3e7-801da7b8491e | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2], Thermal Analysis Report
158ce6c2-468a-5f38-b956-c65a5aa9ba7a | note | Acceptance Criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 25°C.
50207366-8364-5d5b-8f2d-a747c7cbad81 | note | ○ Ambient air temperature at the time of placement must be between 5oC and 30oC.
2ac10273-3215-57c5-8d55-b0610434d1c5 | note | Key - S
a8489b26-25f7-5f21-85b9-e7df8fa81b57 | note | UGL Key - S
f3ba78da-cfe4-5a90-911f-285650b596b8 | note | SHL Key - S
8ff7ccd7-8bb5-551f-b886-5d443cb72af4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3a2e4428-ebfd-5cee-88f7-d9225971bdc1 | tickbox | Material dockets
67254708-6bc0-52cd-b189-2df6ec5e3e13 | tickbox | Concrete pour records
| checkpoint | 3.9b - Concrete Supply Temperature – Other foundations
58071e07-fd4f-5c74-8074-aae2c311c9c1 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
dfeb4a86-bd8e-53f5-b09d-05424501ad0a | note | Acceptance Criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
e9cdb38c-df00-5349-b43a-9c648c44a8bd | note | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
b9404258-580d-5e0e-b918-4f197c29e387 | note | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
4bf1dee2-d95c-522f-84d1-5f8247708293 | note | Key - S
d829ebba-d699-5033-95b1-502bd11cf681 | note | UGL Key - S
031ce80d-6ad4-5531-8116-ed82ed23663f | note | SHL Key - S
c4a09a8f-efb7-5947-b3c1-4554fa03e743 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ab427342-380f-5e6e-96fe-aadc3f95408c | tickbox | Material dockets
44f91894-360f-5709-bae5-ae36dd7f5d25 | tickbox | Concrete pour records
| checkpoint | 3.10 - Concrete Placement
8ed7b180-0c03-5e54-b167-bc4670c11aad | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
d454f90e-4bda-56fd-a9e1-07b86bd330b0 | note | Acceptance Criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
bf01e9a4-c49f-5f85-92f2-ef69cb81777c | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
71e87cc9-deef-5d32-abf8-d33b7ee96398 | note | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
4b0bf674-3d48-5b57-86df-b1dc27e009c8 | note | Key - S
4a6582ba-190a-52c6-9fed-b5243f6e950c | note | UGL Key - S
1188fc2e-adcf-5369-9758-805de15054fc | note | SHL Key - S
fa3c94d0-a619-5521-9f91-9aef93edb37f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3f5b91ab-4d70-5bdd-bdd8-b7b55891e1bf | tickbox | Material dockets
c16ceb32-bac3-51fa-b354-b4ee1b2f1409 | tickbox | Concrete pour records
| checkpoint | 3.11 - Concrete Slump Testing
9ce2909f-f917-5316-9078-41d91585ff5d | note | Acceptance Criteria - Slump Test - One per batch of concrete
7e4f0726-4fed-58e3-a8ee-d1572a1cba50 | note | Slump within tolerances specified in AS 1379
3c301884-ffc8-5ad2-be3c-dde89022b5a9 | note | – – – – – – – – – – – – – – – –
44a38783-905a-55bc-a6d1-798c477ffb05 | note | Table 5.1 Permissible Tolerance on Slump
2d51011b-0fd6-5090-9051-abe945606034 | note | – – – – – – – – – – – – – – – –
fd9fae1f-d86e-5cad-8804-e33583354b17 | note | Specified slump, mm ¦¦ Tolerance, mm
d3357081-531e-5607-8f5b-8ab8d76733e1 | note | – – – – – – – – – – – – – – – –
b7efae44-e910-54f6-b733-fdc4a68dab26 | note | <60 ¦¦ ±10
b0cfcd69-fb75-51ca-8026-ef6144364c13 | note | ≥60 ≤80 ¦¦ ±15
4cd7b149-7973-56e5-9d86-1444d00e99fd | note | >80 ≤110 ¦¦ ±20
5d75f8cd-bcaf-5a28-afac-1db5babe9886 | note | >110 ≤150 ¦¦ ±30
77bc07a9-b219-5201-88e2-8e126b995b41 | note | >150 ¦¦ ±40
7c9f6a88-265e-5071-b9ae-5391fdb9e666 | note | – – – – – – – – – – – – – – – –
ef45e67f-3ada-54ad-a72b-5aacecb788bf | note | Testing to be executed by a NATA accredited test facility
70b56dc6-7ca0-5eda-8a3f-6f9cee7e1f7e | button | Acceptance | Yes,No,N/A
307b2597-4800-59f5-ad24-bbfd6e6fca05 | note | Key - S
89c9b346-ce8a-566a-b572-d6c16bc25525 | note | UGL Key - S
89d984d8-115d-5c13-8aa9-7bb041d0e6f2 | note | SHL Key - S
d55ddef9-1f3f-52aa-9dc4-cb9fbfd151c4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
779bfbf4-5591-5a13-9cdc-6f87fb5382ae | tickbox | Concrete pour record
| checkpoint | 3.12 - Concrete Compressive Strength Testing
6452946e-1e84-571a-be7d-12da3d2595fc | note | Ref docs - Drawings
62f55345-7611-5632-8368-a112ea565d6f | note | Acceptance Criteria - Compressive Strength Testing - 2 x 7day and 2 x 28day per 50m3
1f25029b-0c10-56d2-9208-485454ff140c | note | ○ Testing to be executed by a NATA accredited test facility
8409b014-5383-5528-9265-59d4461acf03 | button | Acceptance | Yes,No,N/A
ce0d0145-33de-565c-be7d-bd3e2270c6a2 | note | Key - S
910902ce-16f1-5dfd-880f-e2660e8b9f91 | note | UGL Key - S
8e4dd4d6-2ee6-5ab3-b941-87c1f768ecfa | note | SHL Key - S
1ca9e828-9b05-5544-a340-9e6b875755af | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9e0e160a-f91a-5f46-8d70-9a6157869593 | tickbox | Concrete pour record
| checkpoint | 3.13 - Surface finish
2a53b644-67f3-5046-948f-c2d4e84ac587 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2], Drawings
0281595a-1409-5a66-833a-e2e458b468f1 | note | Acceptance Criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
5c1c3eb7-5833-5ef2-b5f6-7450681a4dd6 | note | ○ Formed surfaces conform with surface finish requirements of AS3610 for the surface class nominated.
8adb6e57-9d39-584b-89fa-0b9341979e8d | note | WITNESS POINT
e3e2d541-7489-552a-b316-8cfb7e257e92 | note | 1 day prior
bb9e37ca-b3ed-565f-a009-58ebe14111b3 | button | Acceptance | Yes,No,N/A
66c01ff3-9c68-5674-a882-817629bcbd21 | note | Key - W
b4705925-3384-5843-81c2-60eb07c53d58 | note | UGL Key - W
cf8ace51-ec66-5163-8388-96bd60059c1f | note | SHL Key - W
| checkpoint | 3.14 - Surface Treatments
a0aacf3c-8b50-5fb0-9430-03f8408b56bd | note | Acceptance Criteria - Any surface treatments to be applied are approved for use and appropriate dose rates have been determined
e08db6b7-26ed-5efa-830d-92ae484bdbc4 | button | Acceptance | Yes,No,N/A
ebfed0b4-1cd9-57db-a747-aa1caf399a24 | note | Key - S
2b570d66-abec-5f0b-95e2-1386ec3d7061 | note | UGL Key - S
99c32a7c-7531-58be-b9d3-0bed3210d88a | note | SHL Key - S
| checkpoint | 3.15 - Joints
0b1dda2b-4ad5-5240-926e-a46677c4815f | note | Ref docs - As per drawings
78a01543-ebb8-5103-8ff4-7c1487730b0c | note | Acceptance Criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
51b28d05-4c2f-5224-9c98-41bf25900622 | button | Acceptance | Yes,No,N/A
8220a9bb-37c3-5782-996a-a18c6ae194c7 | note | Key - S
e72590c7-4518-5add-b75b-847289fbc31a | note | UGL Key - S
ee10abef-7c80-5edd-a230-83de9d49ff9b | note | SHL Key - S
| checkpoint | 3.16 - Curing
47caa657-3e83-5a40-a925-1c5ea09bb132 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
890e91c7-1d17-5c05-bdd8-6fd2755c9a3d | note | Acceptance Criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
5238d57d-793d-5c88-a958-fd90a650fe8b | note | a. Ordinary Portland cement concrete – 7 days
6f6fd0bc-f56a-5fd7-af93-c8853aab3c8c | note | b. High early strength concrete – 3 days
1cb9e399-a139-5a27-9a73-34ac1eedbd04 | note | c. Concrete with cement or pozzolan materials – 10 days
91abb0ec-634c-55cf-bd00-096c1ef66db8 | button | Acceptance | Yes,No,N/A
2a7e839e-9fdb-510d-9a6c-eeb8b9348df8 | note | Key - S
e1fbe8c2-d8be-5333-a0b3-8e07f15879ca | note | UGL Key - S
e432882f-0040-53ba-a00a-2310a5499586 | note | SHL Key - S
| checkpoint | 3.17 - Stripping of formwork
b78ad0ee-ce75-5bf8-a4e7-71063b9dbe23 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.4.5]
43ba6bc3-da12-545d-ae36-ab403fa8c67b | note | Acceptance Criteria -
6cd64397-2edb-53a7-ae79-2d11976e9db3 | note | – – – – – – – – – – – – – – – –
3634817d-c0e6-5a92-ab62-bedba13f351e | note | Member Type ¦¦ Member ¦¦ *Effective Span mm ¦¦ Minimum Stripping Time (days) for Average Air Temperature during period prior to Stripping
6ae43905-bc65-5364-a233-518ef2a97749 | note | – – – – – – – – – – – – – – – –
d0a1f88e-ded6-5ddf-8344-87ba9552b91c | note | - ¦¦ - ¦¦ - ¦¦ 20°C and over ¦¦ 10°C to 20°C ¦¦ 4°C to 10°C ¦¦ Under 4°C
5ca78118-9e46-5b2e-b6ce-aaaf2274ca09 | note | Vertical Unloaded ¦¦ Wall, column, beam side, slab side ¦¦ 0 ¦¦ 2 ¦¦ 3 ¦¦ 5 ¦¦ 7
65b48f7f-ef57-5d4b-82f7-26b43f9ddc6f | note | Vertical Loadbearing ¦¦ Wall, column Or loadbearing Structure ¦¦ 0 ¦¦ 5 ¦¦ 6 ¦¦ 7 ¦¦ 9
bca83872-b9a2-50aa-98fb-0c23386bcb8c | note | Horizontal ¦¦ Slab ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 7, 10, 14 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28
4f5bde31-c5cd-5c06-8feb-82774a89ba5e | note | Horizontal ¦¦ Beam ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 10, 14, 21, ¦¦ 14, 21, 28 ¦¦ 21, 28, 28 ¦¦ 28, 28, 28
065d99fe-bbe1-5b83-ae8b-5895ce34a338 | note | – – – – – – – – – – – – – – – –
f7c8d477-0fe6-5a00-b53d-cbebdf4f5286 | note | * Effective span is the maximum distance between supports (either temporary or permanent)
52909241-9928-5bfd-912c-7aec80d6e0c9 | button | Acceptance | Yes,No,N/A
33084da0-58fc-5765-8b3e-04545d2b9972 | note | Key - S
055b44d1-6ec5-59c7-9be9-9e7657566d62 | note | UGL Key - S
ab25919c-95c8-5f75-be1a-9156a2730489 | note | SHL Key - S
| checkpoint | 3.18 - Concrete Repair (If required)
422b1db6-8ec5-540b-a562-8831aae43bf6 | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.7]
f29df1da-c740-5f81-a77a-b31b44edd96d | note | Acceptance Criteria - Defective concrete shall be repaired or replaced. The materials and techniques of repair shall be examined and approved by the Superintendent prior to the commencement of repairs.
9ce212d9-c67a-50cb-9e80-0f1ae42780e8 | button | Acceptance | Yes,No,N/A
413697bf-441a-549c-8661-dde6cf9123cc | note | Key - H
f82b7ce5-ec07-521b-a851-fee8287e2f8c | note | UGL Key - H
82546829-f039-53b9-8405-7f66d36a84f3 | note | SHL Key - H
f24d9f47-633d-545a-9410-cfcbf23481d0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
abf68c34-e05a-56e8-8fcd-3283632938c6 | tickbox | Grout Placement Checklist
0b7460e2-b639-5fdd-bc19-3d3d4961d3eb | tickbox | Approved Aconex Corro for Repair Methodology
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Backfill and Compaction
| checkpoint | 4.1 - Structure Backfill
46372a5b-b455-5680-b945-6bc194633a68 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.10]
4919311d-aa7d-584d-853b-83c6ef5908f1 | note | Acceptance Criteria - Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
95e76a2a-b343-5391-a948-c9423cc2dace | note | ○ Placed in layers of maximum compacted thickness of 150mm
844e9fee-4e43-5080-9104-2da0335ed8d4 | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
4489bf16-a6fd-5afc-aeed-50f4360c2914 | button | Acceptance | Yes,No,N/A
fc4d975e-c814-5945-9db8-9c067a9e074f | note | Key - S
27e011ac-cae9-5a40-b10f-2356186d0855 | note | UGL Key - S
0f15a42e-23c2-5a38-a1d7-973f9bef8774 | note | SHL Key - S
1c3b04ae-705b-53fc-a14c-2a8ae1b54d65 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
20050dd1-eef8-52c9-a4eb-0d8e34d7a56d | tickbox | Material Test Report
| checkpoint | 4.2 - Compaction - Backfill
3e35a1e5-f954-59bd-affa-825c4f7f6683 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
697c6ab0-40af-5bfd-8634-596ca012b392 | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against structures to be:
ab21886a-fc8b-5f79-bc24-bcc7cf87d2e9 | note | 92% for general fill
054b33e8-b239-5d6b-8049-8873e4738dd0 | note | 97% for select fill
e6f29b1a-5cfe-5280-ad3a-c2dd53b532ab | note | ○ Test Frequency = 1 per layer
5d27d9ad-e736-5bb7-86b5-3b8e8ee91516 | button | Acceptance | Yes,No,N/A
3bbd0efb-0650-56b0-b429-908716b62c66 | note | Key - S
80346087-7909-5291-8281-16cb3b24497a | note | UGL Key - S
80bbb21a-e761-5601-934e-0e131475e428 | note | SHL Key - S
931105e4-e245-5af2-afa4-daa9a92676b0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2670363d-66c9-5200-ab2d-0952e40854ad | tickbox | Test reports
| checkpoint | 4.3 - Moisture Content
7a7053b7-8672-5cea-8d8e-18b71cdabd79 | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13 & 7.1]
f36b8884-6692-58d9-ad9b-64ec46493d04 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 90% OMC unless otherwise approved by Superintendent
33d32df2-62f4-5231-b170-1db13f7fe150 | button | Acceptance | Yes,No,N/A
f435f174-31cc-5d44-8480-72c8e81d5d04 | note | Key - S
7b8ab75d-d015-53d7-8331-7c29220d3cdf | note | UGL Key - S
20e1e576-1127-5e06-9a06-a2af3862882c | note | SHL Key - S
83d8935a-1259-5606-a73c-39304f6c780f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7be1012a-98a5-5a48-a854-704a19a64d23 | tickbox | Test reports
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey Report
708daad9-9978-57fc-ae0a-fb854b5f173f | note | Ref docs - Spec. 0161 Quality [Cl 3.13], AS3610
600d7a82-f9c0-57df-85d3-cfc5b647cd3d | note | Acceptance Criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
0b0b11f6-41b5-5ee0-a370-abe900895212 | note | ○ Absolute position in plan shall be within 10 mm.
587a2059-aeec-5ae8-b28c-49834c827fa5 | note | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
b3f23b54-583d-5fdb-874e-2b2cec7422e0 | note | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
88eb668d-054f-5526-b33a-6344059ca5bf | button | Acceptance | Yes,No,N/A
d611b2c3-ba33-554c-94b1-8a32adc57c22 | note | Key - H
e0ec5a52-2975-5feb-8338-f0773f002605 | note | UGL Key - H
e7164dcd-4052-5a5f-aa38-67000b284a2a | note | SHL Key - W
72c059d5-9f6a-513f-b010-b671947720d5 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f608f85d-9724-5558-a608-d52415ef07ac | tickbox | Survey report
| checkpoint | 5.2 - Concrete Test Results
8f8d6469-9cf5-5b4c-a8c3-6b2d2e08efea | note | Ref docs - Spec. 0002 [Cl 8.2]
e0f9ace5-c1e4-5d9e-8908-a684837fc3c0 | note | Acceptance Criteria - Certificates received, reviewed and conforming to requirements for each pour.
4eb426c9-04e2-55d0-abf4-fe181d72f51e | button | Acceptance | Yes,No,N/A
20061a7a-5f8c-51c5-9351-d432e534dba5 | note | Key - S
a766aa19-7ea8-5fbd-a66c-02024c6500a6 | note | UGL Key - S
8c6d4835-5123-5219-91f4-0dbc945d2ce5 | note | SHL Key - S
c5087528-47a2-52f8-84e4-a7f217c61482 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2e5bd544-d118-5cb3-a268-9597d0e12e63 | tickbox | Test reports
| checkpoint | 5.3 - Acceptance and closure of non-conforming items
3166a3ea-35ec-52fa-a7b4-e8afe287b1b5 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
a97e207a-dc87-56eb-8f94-be71c9f6ed03 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
fb0f58f4-8506-5e79-9967-b9bd22f29960 | note | HOLD POINT
a1050b07-a080-5db0-ae9c-9af6c043f2d6 | button | Acceptance | Yes,No,N/A
18d782fb-0300-5222-a6ac-1c741db11a64 | note | Key - H
a7a6af0c-0d7b-5d15-87e3-cb755c116a0a | note | UGL Key - H
bb7531ae-cf89-5a87-9f04-0dd3a978962e | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2 | itp | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2 |  | 948b8c0a-21e7-4bad-b3f7-f9244f4a8714
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
d94fabb2-4c63-5dc1-9756-9a4c4ef18f37 | note | Ref docs - Issued drawings / Site copy drawings
8d8ef602-28be-5b9f-a99d-9afe5d150deb | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
eeedd88b-fb82-56b6-8671-63e12f6f8eb5 | button | Acceptance | Yes,No,N/A
3fae3d80-69c2-5fb9-9cae-65ebf7fc7a06 | note | Key - S
0a5f6fd1-a9aa-52f8-a817-ec295473f341 | note | UGL Key - S
25396972-0970-5e8e-bea6-bc2363939bd8 | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
f4088ac4-1aa2-59fa-b2da-a09ea4340ff0 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
56e7ad99-9f15-5342-a100-7d82cac9cf3b | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
a93d5c68-58be-5685-bc2c-f207760f4f65 | button | Acceptance | Yes,No,N/A
cb1a23db-91e8-5b49-96d2-ff55f2406cf0 | note | Key - S
8c16765a-b2c9-59eb-b783-1e2e00ca2c51 | note | UGL Key - S
6773634b-960a-58dc-9f76-980e8474980a | note | SHL Key - S
fc37cd2a-d112-54bf-836d-bc615887198d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5af32261-ccc0-5725-ae07-74596f175fb3 | tickbox | Lot map
| checkpoint | 1.3 - Underlying Lot Conformance
3e620195-dee3-560b-8d28-2902ed740290 | note | Ref docs - Underlying Lot ITP
f1a47fe9-a1aa-536d-96bf-269ab6eb6dac | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
52d977eb-0612-5dc0-90d3-b783e5d52922 | button | Acceptance | Yes,No,N/A
| checkpoint | 1.4 - Set out
0521baa2-d9f9-5574-b602-d912c13e187f | note | Ref docs - Drawings
db0859f5-1358-5240-84b8-2ff8342391ee | note | Acceptance Criteria - Setout pits to the location and levels on the drawings
46ed1b8a-7158-52f0-a0fe-32302555e094 | button | Acceptance | Yes,No,N/A
677cc112-a137-59a0-a20c-1ce2bea4f5d3 | note | Key - S
487069ad-efa3-5eb1-a282-7198153727d9 | note | UGL Key - S
d7be1716-bfbf-544f-9ec2-3c393253a501 | note | SHL Key - S
| section | 2.0 Excavation and Bedding
| checkpoint | 3.102.1 - Excavation
9d57023a-8986-53a7-ac6e-57faf12f2db0 | note | Ref docs - Spec. 0002 General Electrical [Cl 6.6]
4ef34b1a-cbe3-5a9f-ae48-8d9351339f68 | note | Acceptance Criteria - Excavate to the depths and widths of the design drawings
63c24624-673b-5443-b703-76a8815f3a51 | button | Acceptance | Yes,No,N/A
c6ece6c2-76ec-5f04-8aec-20d96645b74d | note | Key - S
413cbf32-4295-5dcc-a060-5f68b24b114d | note | UGL Key - S
733f74f7-d065-5516-8348-0ce755dacd86 | note | SHL Key - S
| checkpoint | 2.2 - Place Bedding
a7c89144-1003-5f02-95f0-a643a62f59d2 | note | Ref docs - Spec. 0002 General Electrical [Cl 6.11] Drawings
470900b9-a868-52d0-81e9-3383f64d304d | note | Acceptance Criteria - Pits to be installed on a 100mm thick compacted sand base.
7e3af4e9-85c4-588b-a486-76c91577c7af | note | ○ Alternatively, a 150mm thick 20mm crushed rock layer can be used if the pit floor is below the water table.'
b6619676-0e3e-52b4-b1ce-8949ca03d0d4 | button | Acceptance | Yes,No,N/A
8a09bd64-b62b-5908-99a0-4b34cd82d079 | note | Key - S
6cba7b9e-c75c-546d-ad89-44410a6b13ec | note | UGL Key - S
a815db8e-42db-5754-b242-dd82ad2c92c1 | note | SHL Key - S
0632b814-9272-5751-919d-c2d5c191f5c8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
14f349af-37ff-577d-b76d-7c04dfd52b6f | tickbox | Material Dockets
| checkpoint | 2.3 - Blinding
47b3bc8c-b9d6-5caa-b90c-66b5ed472bbc | note | Ref docs - Drawings
7b736405-20d9-5bd4-9f2a-5e37d0be05ff | note | Acceptance Criteria - Blinding (15MPa) for Pit Bases to be a 50mm thick mass concrete layer.
b426333b-5104-51da-a51b-2b171dcd28f9 | button | Acceptance | Yes,No,N/A
ecf8c69c-5d0f-5c70-8734-b9dea46963cd | note | Key - S
1590100b-e369-5200-8228-a81426b9173d | note | UGL Key - S
340b8ebd-9bb5-5713-af5d-408d8c538fce | note | SHL Key - S
| section | 3.0 Cast in-situ structures
| checkpoint | 3.1 - Formwork (Base)
44a5da7b-56fb-5eff-92fe-9c872bff2507 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
0d9dec8e-2b1a-5a26-8f1c-1652378b7261 | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
61ff1710-74ad-5bce-957c-ff5cd10107a7 | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
dccb2817-f867-50e0-ab09-9cbdb2a7085a | note | HOLD POINT
940fd6b0-67f8-54ae-8181-62452d2df4e9 | note | Before Placing Concrete
40590182-6461-5b84-9fe9-71bd02f9eb1e | button | Acceptance | Yes,No,N/A
4d6a3e4a-41dc-5c02-b9ed-f8789d6ae619 | note | Key - H
cdee1992-e1e5-5914-be8c-99214ef5aa54 | note | UGL Key - H
730b970e-4b1a-56bd-8aaa-1fa5923ec513 | note | SHL Key - H
151db578-6653-591b-8232-8581e6d28788 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
57835752-4319-58c7-b7ae-374d8c3180f4 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Steel reinforcement (Base)
50fa6676-48d6-542b-849e-44f405c7d03a | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
46ac5531-6dcb-5a3e-b84b-bdd9ee0ea893 | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
9335e728-2aec-51bc-9c55-d71fd95748a7 | note | ○ Concrete pre-pour inspection complete.
396f4e81-a5c6-58a0-bc19-70c338a11d42 | note | HOLD POINT
d598caa8-22a5-53b7-a981-3ece7c9e3e21 | note | Before Placing Concrete
304f5d13-5942-5da6-b7e6-d17ffc7643c1 | button | Acceptance | Yes,No,N/A
bdcf67ea-bcfa-54b0-9a63-aabf3efc277f | note | Key - H
034eb040-4b71-509e-a502-dc70658bc1a9 | note | UGL Key - H
7c09f218-e49e-587d-b22e-de0ddad6daa4 | note | SHL Key - H
2f663674-2b92-519f-a680-6be3ed709e15 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
37f2e658-f957-5be0-8b31-911a48e97ea3 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Formwork (Walls)
9ffe4a18-584a-559e-b601-67ce27ac2194 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
69384eba-edd2-523a-8b1c-49e15625a660 | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
f2d11411-e075-5a5c-90dd-9db5ae974857 | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
7d96f31b-fd8d-597b-8223-b3db4528fcf6 | note | HOLD POINT
a17fca45-a238-57e7-a110-20594a879140 | note | Before Placing Concrete
9a2cb1d0-ccc5-572a-b424-805de5115143 | button | Acceptance | Yes,No,N/A
79b50740-0aad-5968-b8b2-62b38aeecee1 | note | Key - H
2c02e33e-7284-5b26-93ca-f5a002b0b5d4 | note | UGL Key - H
349d222a-da19-5d7b-9472-8c06f126b6e1 | note | SHL Key - H
860cdcd5-035f-5b96-8e26-1cd752cba69a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ab3d6a7c-7be5-5936-994c-f0c44424f558 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Steel reinforcement (Walls)
b43c08b3-98da-570f-88bf-a9f05fe22df8 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
ac2851bb-78dd-5a39-8709-820194cf71a2 | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
edd705ab-e98f-5922-8673-fa15a7952bce | note | ○ Concrete pre-pour inspection complete.
38c97513-7119-5238-8fc5-616938ea4e75 | note | HOLD POINT
b82dcc14-dcd0-5786-934b-3f6cc35041af | note | Before Placing Concrete
0373189c-48f4-5e24-9117-118790011af8 | button | Acceptance | Yes,No,N/A
a3eca659-ee19-554e-8600-a994ad669372 | note | Key - H
82727c24-d1f3-5b4f-911b-5dec7f62066f | note | UGL Key - H
381037ff-ab3a-54b2-b2c5-430667d28b54 | note | SHL Key - H
24d5219c-0b8e-5162-bf65-752116f6000a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8ed255b2-47e8-549e-9166-95dbfdb50068 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - Bell-mouths
902aad4c-e6e8-58b0-8199-5894279e9d8b | note | Ref docs - Spec. 0002 General Electrical [Cl 6.11]
51ecdaee-d064-542e-b2db-d18ab7bd14ee | note | Acceptance Criteria - All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall as per manufacturer specifications
d83c7939-261e-59ba-83a6-d03bf4a08aec | button | Acceptance | Yes,No,N/A
d5e915ea-3cd9-57c7-90fd-1dcd32dbc86b | note | Key - S
737c614b-357c-5f49-90ab-d244f6803600 | note | UGL Key - S
fcbfea45-c8a4-5c6e-93b0-3d332856482b | note | SHL Key - S
| checkpoint | 3.73.6 - Concrete supply and placement
92f885c5-8d59-53ac-9179-d4e6cbc4028a | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11], Drawings
e6d0f79e-e045-50fa-97cb-6ca502d56ca4 | note | Acceptance Criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
21737322-578a-5e39-a6f7-ab4dd44f3dd6 | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
5506dd69-acae-50cb-9195-bfcd74ce6da8 | note | – – – – – – – – – – – – – – – –
046c587b-d233-5245-813c-5ae39082d32c | note | Concrete temp at discharge (°C) ¦¦ Max elapsed time (hours)
57ca3ff4-0fbe-500e-bef6-5258eacc4f4e | note | 10-24 ¦¦ 2.00
61d4e9ff-1740-597a-9e84-da68f88736ab | note | 24-27 ¦¦ 1.50
ad93ca03-34d7-5dc3-abef-cd3b4c136931 | note | 27-30 ¦¦ 1.00
696cf7bd-2af7-52db-a748-363f468772a3 | note | 30-32 ¦¦ 0.75
f911c453-6407-578d-926a-0ac0690172f5 | note | – – – – – – – – – – – – – – – –
8611d3e5-8c36-5899-b904-686bbb6996a9 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
076f6ad3-7bc4-597b-80c7-c8b026ece200 | button | Acceptance | Yes,No,N/A
2b134cf6-0800-55ad-9a9c-bfd4a17c1f5c | note | Key - S
a092a379-0157-5586-a9f2-a74a2ba70139 | note | UGL Key - S
01c9e696-8c5a-5215-ad15-0f88742ae22d | note | SHL Key - S
f25b4ac2-dfe0-55fc-8776-4a81eb25479b | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
72564d24-566e-5675-b558-1ed48eae62db | tickbox | Delivery dockets
| checkpoint | 3.7 - Concrete sampling
10202c0c-8c69-5f65-b65d-8eb53e4dd210 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
5ab7f1d9-0d79-5f67-98de-15ab947e21d0 | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
690fcd52-4db7-58b7-8a98-f2236cd4a978 | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
36e2162c-ab29-52aa-8855-f671a0707914 | note | (b) Slump: One per batch of concrete
6ca33135-2747-5751-a956-e9d282cb2202 | button | Acceptance | Yes,No,N/A
cc27d0b6-2a6b-5463-b941-3a6438a9e589 | note | Key - S
db470424-fcec-593d-a6aa-9a73c5db8bfa | note | UGL Key - S
f9a63336-b513-5a54-9d12-c79260390e7e | note | SHL Key - S
1a397a1c-751e-5e3d-be95-cb34a4214d60 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4f819a2b-bf9d-52b2-8834-d918ab38718d | tickbox | Concrete pour record
| checkpoint | 3.8 - Concrete testing
50a1e29b-7501-5713-8808-d64e36cfdb79 | note | Ref docs - Drawings
4beb37b8-51b4-53ad-80f5-bb56a58b4ab8 | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements. Slump within tolerances specified in AS 1379
d17f611f-313a-5e94-801a-a4f98dd0f46a | note | – – – – – – – – – – – – – – – –
573a6566-0cf1-5ed3-aa55-ad132cdf2f00 | note | Table 5.1 PERMISSIBLE TOLERANCE ON SLUMP
c4a30649-8513-59c9-892b-1d510a102ccc | note | – – – – – – – – – – – – – – – –
023a60f4-8e28-5707-a5ce-8d0fe55cdb38 | note | Specified Slump (mm) ¦¦ Tolerance (mm)
399617e6-4f34-5c25-830b-b7f0e5810380 | note | – – – – – – – – – – – – – – – –
120aa10c-2940-5773-b806-dbe523e44304 | note | <60 ¦¦ ± 10
aa88cf8f-9faf-5b60-8e82-f2bb050e85ba | note | ≥60 ≤80 ¦¦ ± 15
1af050d3-9e45-5b66-9ee3-643aa3d14e34 | note | >80 ≤110 ¦¦ ± 20
089472c1-7679-553c-a175-76335bdb2d3c | note | >110 ≤150 ¦¦ ± 30
7e997f8a-4918-55fa-b461-cbf6b2b0206c | note | >150 ¦¦ ± 40
c177be6a-69bb-52a4-90f3-a7f59cca3aff | note | – – – – – – – – – – – – – – – –
1705e6fc-58b6-57c0-b062-b6d90818748e | note | Testing to be in a NATA accredited test facility
411fb446-af35-527a-afe5-fe5bd7c703bd | button | Acceptance | Yes,No,N/A
8bc506cf-17d4-597b-a12f-397abab21c64 | note | Key - S
af12d071-fb57-5ee1-9763-e4d3f57d93f8 | note | UGL Key - S
a12eaff2-239b-594a-920a-c8be597a2b9a | note | SHL Key - S
a1284c01-c52f-5827-b310-5019cf581c57 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0cf96643-3fd8-5bb9-8e91-085ab9e18daa | tickbox | Test reports
| checkpoint | 3.9 - Curing
ab43d534-ae88-5630-8ff7-ba0e3e6271b2 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
d12c167f-6bd1-5f1e-8d30-d25657e26977 | note | Acceptance Criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention for a min period of 7 days or as directed by the Superintendent.
9173e4e0-49eb-573f-b9d2-7aeee2079300 | button | Acceptance | Yes,No,N/A
8c9a57d3-f846-5d87-b039-87be6f9cdf06 | note | Key - S
7daf9624-6860-5fe6-8f82-3edf47efaa7f | note | UGL Key - S
e076b065-0822-5342-822f-ff29d4ba0587 | note | SHL Key - S
| section | 4.0 Finishing Works and Backfilling
| checkpoint | 4.1 - Pit Backfill
fa1febc7-9a2f-5509-95a9-14cec49c175a | note | Ref docs - Spec. 1354 Earthworks [Cl 3.7]
fa1b7ebd-05ed-5e68-ae21-2cae5f6b584a | note | Acceptance Criteria - Pits to be backfilled in 150mm thick layers for a horizontal distance of 300mm as per RFI-069
61ac2f8f-a4c7-51f9-994e-b81c5c34915b | note | ○ Backfill to be with a thermally rated compacted sand as per the design drawings up until the top of the conduit bank. The remaining backfill above the conduits to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
01771d15-3efe-50e0-a656-abd6b2f592f0 | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
c48e43e1-d79d-5be9-92d7-f030a841c8d8 | note | ○ Backfill shall not commence until concrete compressive strength reaches 15MPa unless approved otherwise by superintendent
a84110a4-565c-5217-b6eb-2867e49af437 | note | HOLD POINT
b9337800-fad9-526f-b06a-49b10d3dbe1c | button | Acceptance | Yes,No,N/A
ba4aaf2e-bf73-5b2c-875c-f96ba3bc990c | note | Key - H
58564afc-0936-5fd6-a078-6f758ad98ca2 | note | UGL Key - W
dc563456-4e58-5abb-b673-b7310810781a | note | SHL Key - W
780c23f1-94f1-5740-a483-8b5e1d6a9f9f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2fd1d111-5e4f-5ea0-9168-f91513498c62 | tickbox | Material Test Report
| checkpoint | 4.2 - Compaction - Backfill
3512927a-4e77-5397-a926-9ab6fb4dc244 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks [Cl 4.13]
06c50918-5ce7-571d-b8eb-f4ed6228cdf0 | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
d832aa35-1ad5-5948-9fb1-3a1200e12f6c | note | 95% for pit bedding and conduit embedment
dcb2149a-af43-52af-aef8-24c71299f905 | note | 97% for select fill areas
94d9ccb6-0f00-5caa-b917-a025953119c0 | note | 92% for general fill areas
a0b9a39d-1d31-5a24-bc6b-2ebc48a3557a | button | Acceptance | Yes,No,N/A
63fdab33-885c-57ba-83e7-9fe81360b9c0 | note | Key - S
3dd66666-c478-5f2a-9772-e7b707bf5389 | note | UGL Key - S
276d4a47-065c-52da-b405-7b4f5c3e8540 | note | SHL Key - S
7391ae49-8916-545e-9a79-5bb11b91bfd7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6f81194b-bc3f-5d12-86ad-f9fc40cfa891 | tickbox | Test reports
| checkpoint | 4.3 - Access Covers & Grates
783783d9-776d-55ac-b43b-1b36a2b5dab7 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
a629818f-13b1-5c36-a9d4-0cd17e59ddcd | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
ab5067da-461f-55b0-826f-c3e55e060290 | button | Acceptance | Yes,No,N/A
6de30edc-81e2-552b-abaa-4fa66c3ab92b | note | Key - S
5e769ff3-2ea2-5f32-9d19-ca0004a7fdb4 | note | UGL Key - S
1d7d118e-8c7d-5d7a-a2b6-019e810d0ade | note | SHL Key - S
| checkpoint | 4.4 - Step Irons
9fd07298-875c-50b6-86ff-a460018c4c75 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
8b9ea3e7-4cff-5415-b746-59760bdecee0 | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
d8d56b7b-d820-5ddb-83f0-7a309ff15788 | button | Acceptance | Yes,No,N/A
03e5ca79-78b9-5f9d-b9fb-58566b024adc | note | Key - S
6c682768-1737-532d-a9de-f937da8fd25a | note | UGL Key - S
6bcf8eb1-91c9-5346-9e1b-3313804dbdc6 | note | SHL Key - S
| checkpoint | 4.5 - Brass Marker Plates
668b4488-81fa-509f-a751-dc87a28b22b8 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
3f279001-fa76-5719-9d8f-682bc4f0559a | note | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
429f24d9-dae4-5dfb-8058-264ad855853a | button | Acceptance | Yes,No,N/A
f2ea165a-260f-521d-8dae-7cda2e062d34 | note | Key - S
e58b4623-46b8-51dd-a7f6-a742e08066e6 | note | UGL Key - S
8ab3ff55-e733-5bbc-92e9-f6768c7e898c | note | SHL Key - S
| section | 5.0 Conformance check
| checkpoint | 5.1 - Survey Report
3147cfdb-d122-56cc-b7bb-e610ab9a6fe1 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
4c1650bb-82c4-53af-969b-8e0c8bc5a98f | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
36fbe3a8-e5b9-5323-8cce-7695c4d795f4 | note | Plan: +/- 200mm
0c1d05e5-646c-56dd-bd1e-b23190091340 | note | Level: +/- 20mm
a89dca7b-10f6-57a8-8e38-a65d5236f9b6 | note | HOLD POINT
ad8f20e4-3531-502d-a906-f1329f51dde0 | button | Acceptance | Yes,No,N/A
d9fdb5fe-9298-5ffb-a5b7-9e8fe794481f | note | Key - H
fa3c2b2e-f5e5-5dc6-8982-1ddc92122c4f | note | UGL Key - W
9af37690-ea71-5f84-9da8-e553071c6ae4 | note | SHL Key - W
41ddebdf-dac6-57c8-92ef-e1e5d911a993 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
5a64189f-2675-5ebf-a733-a5c51b1e8db4 | tickbox | Survey report
| checkpoint | 5.2 - Acceptance and closure of non-conforming items
67ef945c-95a3-5ec9-96d6-8e7fc42171cf | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
3f4829a6-6b10-5c67-bb1d-33c16b29a6d0 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
ea803b06-cf4b-5f2c-a221-20356cb49492 | note | HOLD POINT
4026c9f6-3d80-5834-b3d1-8d0d363e57e6 | button | Acceptance | Yes,No,N/A
ad737eb9-523f-5e20-996f-182e76d095e9 | note | Key - H
96b62041-3720-5841-870e-fcae89569f0c | note | UGL Key - H
7feda0e6-9061-5112-b456-d749600766c5 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2 | itp | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2 |  | 6feef3ec-0967-4646-a752-ab56a2049173
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
5f9bc9b5-d5db-5ef0-b595-037afe8eff14 | note | Ref docs - Issued drawings / Site copy drawings
c1e7cc8f-35c6-5d27-8a94-1e3662a05fba | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
b5e632d1-814b-50fd-a07c-d8efcd277a73 | button | Acceptance | Yes,No,N/A
06195079-55e5-5fa9-9b97-650ca108be2d | note | Key - S
aade9b51-61b8-5167-b53e-eff747da2f95 | note | UGL Key - S
2b0951b1-348e-5cd8-9e82-89fadf14265f | note | SHL Key - S
| checkpoint | 1.2 - Lot Traceability
145223af-4c44-54ec-a9d0-f28523d5df3a | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
e758bfc9-d774-5504-a230-c67da6a488b7 | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
07b8484a-2503-58b1-a01e-34f72ea7246a | button | Acceptance | Yes,No,N/A
65282d10-cca2-52af-8c75-cd67fcb54c85 | note | Key - S
ae068240-1674-5411-b79f-b745910c7eed | note | UGL Key - S
7f36be76-9a82-53a3-b280-3626bc946ec6 | note | SHL Key - S
c6b28620-28f5-5d7a-bd4c-9ddf201dca99 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
abb3d71b-43f8-53bc-8931-1e9c60ab8286 | tickbox | Lot map
| checkpoint | 1.3 - Pipe Material
b12442f9-6921-5be3-bf94-7b7ac1423f49 | note | Ref docs - Drawings
f2c85ee1-27ff-570e-bee0-cb54eedb6b0e | note | Acceptance Criteria - Has the correct class & type of drainage pipe been supplied. Has the pipe been inspected to be clean and free of defects?
60341232-cfd0-5562-b171-b9cf2adb7eb6 | button | Acceptance | Yes,No,N/A
56e30506-1668-5d6b-8ccb-9785876915be | note | Key - S
e9982474-c855-5575-9768-e296f975736d | note | UGL Key - S
61ce001c-df7a-54b8-bdf8-fd789a68fd31 | note | SHL Key - S
62181d57-1fd6-5ad4-b7c4-d32eef2cf3ec | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4a127dcc-5d88-5607-a608-6fc96fbe1735 | tickbox | Material conformance certificate
| checkpoint | 1.4 - Embedment material
00caa399-3309-5a0c-a1a9-79c0dc8fa9a8 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
c0851e04-caa5-558c-ae80-4ce5a0fdbbe9 | note | Acceptance Criteria - Embedment Material to be a cohesionless material with a plasticity index less than 6.
c7f46c78-06c8-5a1c-85d0-737cbd4ab0a4 | note | – – – – – – – – – – – – – – – –
0306a507-2503-5ed5-a4df-8f03befa9827 | note | Table 5.1 Embedment material grading
ce1aa27c-1db7-5505-a5d9-2d2616841e48 | note | – – – – – – – – – – – – – – – –
95671961-9362-5582-a44d-add7797f2af1 | note | Sieve size (mm) ¦¦ Weight passing (%)
938ba9f8-9b0a-5ccb-b25e-8b6e32bed171 | note | – – – – – – – – – – – – – – – –
5b28306d-e17a-5b39-87e2-dcf280a4919c | note | 19.0 ¦¦ 100
feff010d-5f45-5263-8401-f8a332abeb92 | note | 2.36 ¦¦ 50-100
22e3e629-fbee-5908-a7ba-0a2a31c32871 | note | 0.6 ¦¦ 20-90
278423dc-7046-5c20-a80b-687c8c857f19 | note | 0.3 ¦¦ 10-60
151a365a-479b-5715-9bbc-cf05e181bc9e | note | 0.15 ¦¦ 0-25
22d741f3-159e-543f-9c51-fdc1ade6e6ce | note | 0.075 ¦¦ 0-10
006f0267-7c64-5725-9770-27f97c6218b0 | note | (Table taken from AS/NZS 2566.2, Table 5.5)
95916354-9686-52d9-9313-ddb1b364d8e2 | note | – – – – – – – – – – – – – – – –
86dbc983-6ed0-5967-9e0e-e892ef74dd0f | note | Alternatively, embedment material may be a drainage aggregate (10,14 or 20mm) as specified in AS/NZS 2566.2
ceb16d52-a9a0-59cc-8901-0f7c786bc1da | button | Acceptance | Yes,No,N/A
383c2aeb-db5d-5dac-bcc9-34b153d80658 | note | Key - S
a30e5025-88a7-57d6-ba94-f7613367f6df | note | UGL Key - S
2db87cfd-47ae-5267-b48b-c2eef986c911 | note | SHL Key - S
2801482e-2630-5c92-87dd-2277cd9d814a | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c82cd359-0cff-52a7-ae30-f9a89f8a3ad0 | tickbox | Delivery dockets
addb1478-3089-5d27-bca5-2a9883f2e471 | tickbox | Test reports
| checkpoint | 1.5 - Welder Qualifications
bc329a6e-2ce9-5fdd-8120-0b094cff3f27 | note | Ref docs - PIPA TP003
f41d3ad6-3f60-5d73-8b18-d2b0ca610856 | note | Acceptance Criteria - Have the workers involved in welding of HDPE pipes been trained by a Registered Training Organisation?
4e33fa17-46c4-5d80-a002-d9a37168195c | button | Acceptance | Yes,No,N/A
f1dcca82-c6b9-5d43-b0f3-8e3fb8ed039c | note | Key - S
0e250ecc-9ad6-5dff-b5bc-b034a5e3ce44 | note | UGL Key - S
870f7508-3b47-5ce5-9f28-24b3a8488fcb | note | SHL Key - S
e0bd5b88-1552-5b3f-9363-31ed84a8205d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c564d570-fbfc-50ba-81fb-3b421dc3853b | tickbox | Welders Qualifications
| checkpoint | 1.6 - Underlying Lot Conformance
87fe5c03-9c60-5636-bb3b-d92de4c53818 | note | Ref docs - Underlying Lot ITP
e54f2921-e1dd-5e95-a6e3-b85dee0c3c87 | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
53454913-17a3-5e8f-a215-57c00c20261a | button | Acceptance | Yes,No,N/A
72de314a-0fa8-5a02-bd60-9c0b3d264efc | note | Key - S
b9853345-6af3-5957-b032-dd637b1ad8a3 | note | UGL Key - S
ed00f5ac-a4fb-5f71-9909-5fe2993db940 | note | SHL Key - S
| checkpoint | 1.7 - Set out
3b5a40c3-8834-5503-94e6-c75c24d9114a | note | Ref docs - Drawings
54a5780b-ac6e-5a6a-b70f-e3b007112c1a | note | Acceptance Criteria - Setout of water line alignment and level. This shall be presented for inspection by the superintendent, if requested.
378ab40f-b37a-53bb-9a93-6517a8962a99 | button | Acceptance | Yes,No,N/A
b450fbca-6d39-5e68-acfe-2aeb4182708c | note | Key - S
9ce642c8-aca7-5b6a-ac26-284240a07bf7 | note | UGL Key - S
eb6ec6ef-6bf0-584f-be4f-5a41b9dc71ba | note | SHL Key - S
| section | 2.0 Excavation & Backfill
| checkpoint | 2.1 - Excavation
1eab5661-7c76-509c-bc70-c675da9fc9e4 | note | Ref docs - Spec. 1352. Pipe Drainage [Cl 5.1], Drawings
f7ad6795-293e-5649-8ab0-ea317a0ce132 | note | Acceptance Criteria - Has the Trench been excavated to the correct width and depth to allow for the pipe size being installed?
fa5775be-fb50-537b-bb8f-51dcfb024642 | note | PE Pipes:
37229b60-0da3-5f70-bb45-35c2b79aa506 | note | – – – – – – – – – – – – – – – –
25888670-1fef-52cd-a220-28e17d9d21ca | note | Table 5.2 Trench and embedment dimensions
72f9f5c4-ef4c-527e-8c60-2a242b748dec | note | – – – – – – – – – – – – – – – –
202193bf-5c81-5fae-b81e-f53a398d1389 | note | Extreme external ¦¦ Minimum dimensions (mm)
d448357a-40d2-5c20-8442-00fa538366be | note | Dia (De)mm ¦¦ x : s : o : y
9fe82829-02f2-539b-9eca-b9e2c3027c74 | note | – – – – – – – – – – – – – – – –
903d002b-829f-5800-9595-3b6a3c876a93 | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
7c9d83a4-7c78-5b49-a6ca-fa0c74c6b4c6 | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
76d558a3-1a6e-51b9-a68c-280bc66ba9df | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
57eae33f-96ce-52c1-a677-d6e127549c4e | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
1cbd7d16-7678-5dd6-9a88-2e774859aa1c | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
48b9057d-eed6-56ba-8a6f-9aea163dfde6 | note | – – – – – – – – – – – – – – – –
954bb56d-c52f-5c46-85a2-3c2967d6ac93 | button | Acceptance | Yes,No,N/A
ca1f2180-a9a6-504b-84c0-aec6cf2a9c22 | note | Key - S
ac375b45-267e-5287-bb62-ab52ed2aacdc | note | UGL Key - S
1eb7696c-7423-5cef-851d-f6b919d881db | note | SHL Key - S
| checkpoint | 2.2 - Compaction –Bedding
f0886642-d801-5004-8b95-b658b5d914d1 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
a5a55146-8d81-56ae-8fd6-4856f053e69c | note | Acceptance Criteria - Bedding:
1a322db3-8ca6-5c9f-b49c-0e62ab6cd3f4 | note | ○ Has the correct thickness nominal of bedding been placed and adequately compacted below the pipe to achieve 70% Standard Compaction? (Compaction test N/A if drainage aggregate is used as bedding)
56356b91-a9d4-530c-af84-354c4dadc433 | button | Acceptance | Yes,No,N/A
25d1e664-9f07-5521-8384-b11fa29874d7 | note | Key - S
bdb7e4c5-4008-5efb-8693-298e8909c152 | note | UGL Key - S
1973cb46-5308-5afb-9d23-ca421c641fa4 | note | SHL Key - S
5ffc2803-1955-5a81-897e-4e25e3cc33d0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1c19fb82-298a-51a4-ac91-c99bddc36a58 | tickbox | Test reports
| checkpoint | 2.3 - Pipe & Fittings Installation
5150a476-4680-57d7-8ad9-fe4dac814793 | note | Ref docs - Drawings Manufacturer Specifications Spec. 1352 Pipe Drainage
dc8930a0-a533-53d0-a078-c377ff3d74e3 | note | Acceptance Criteria - Have correct pipes (size and type), bends, risers, valves & junctions been welded and installed as per manufacturer specifications? All weld records to be recorded daily on the HDPE butt fusion checklist
18fca3c8-7fd9-5f6d-b9b1-20bb7a024390 | note | HOLD POINT
2024f886-79cf-5025-a40f-2c7b0b3c05ff | button | Acceptance | Yes,No,N/A
f2ff35e0-28d9-5026-9545-bfaf773fa14e | note | Key - H
1d48796c-c6a8-575e-a44c-0ae6c816bf51 | note | UGL Key - W
73b8b6f6-98cd-5be4-a690-f04aacab53c8 | note | SHL Key - W
971fa8a3-c58b-5c2f-b8e7-f38727c8bde9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7abaff21-2289-5c93-9da9-402982ff8c01 | tickbox | HDPE Butt Welding Checklist
| checkpoint | 2.4 - Destructive Testing
bfddd6b0-96fc-5af6-8406-926df39c74d7 | note | Ref docs - PIPA TP003, PIPA POP014
f9693f6b-3f19-59f7-8b86-35a2485168cf | note | Acceptance Criteria - Destructive Testing to be carried out as per PIPA guidelines using the Tensile Test Method at a NATA accredited laboratory. Frequency of testing will be one test every 100 welds. If a test fails the frequency to be dropped to one test every 10 welds until at least 5 consecutive conforming tests are received.
0134f1c7-f7c0-5a7a-83d6-631dd02e3cc1 | note | WITNESS POINT
bac096e0-58fc-5c3b-b7e6-d0bfd901a434 | button | Acceptance | Yes,No,N/A
916d7fc6-87b7-55df-81c1-92c69a4930b9 | note | Key - W
4469eeb0-ef75-5e26-a898-40b57cbef9e1 | note | UGL Key - W
0167fbfd-9cff-5ef8-adae-d9ba87253691 | note | SHL Key - W
25903c26-b7b3-5453-bdfe-771fe560a73c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
1dfe9285-3444-59cc-a339-9a1c8165d96d | tickbox | Test reports
| checkpoint | 2.5 - Flanged Joint Installation
281ff1de-701e-54e9-a3b0-5d7f102a999d | note | Ref docs - AS/NZS 2033 Cl 4.5
f39c93b8-1eb5-5208-b01e-d6e5fcbe406f | note | Acceptance Criteria - Flanged joints to be installed as per the drawings and manufacturer specifications. All flange joints to have a gasket or backing ring as nominated in the drawings.
7bb240ed-6d44-5524-8a52-8338ee546252 | button | Acceptance | Yes,No,N/A
efade449-8cf9-56e3-9ac2-973805d38aee | note | Key - S
10f65459-87b0-501c-b869-aee311b99333 | note | UGL Key - S
88cdaa07-b9e7-540d-9783-fd8abb6c1d8f | note | SHL Key - S
| checkpoint | 2.6 - Backfill
a7425dab-5c78-5d01-bb69-2877015f1d26 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
3a359970-c275-5ab6-b2f7-fbc0306260e4 | note | Acceptance Criteria - The pipe must be backfilled with the correct material and nominal thickness as per the project drawings and specifications
6b8281e4-c82c-54e7-a7ae-e2894f2ffb2e | button | Acceptance | Yes,No,N/A
a12b872c-2688-5d05-bfc7-dd5213d7de36 | note | Key - S
5e24ff7d-8e44-50f1-9be3-8b1b8721f06f | note | UGL Key - S
950297f3-c848-5951-b27b-8332449c0e84 | note | SHL Key - S
| checkpoint | 2.7 - Compaction – Embedment material
7357cf0d-9afe-513d-ba86-46c1cd2615c6 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
204df642-2600-58c5-b56d-df23e311c129 | note | Acceptance Criteria - PE Pipe:
fd151d90-e88f-5be6-8c04-cd6e915cce32 | note | ○ Side and Overlay: Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
d584643e-ffb2-5942-ba35-b114af8b4e4b | note | ○ Layers not to exceed 150mm compacted thickness.
87763ebb-403b-59f6-9496-b10d7b4dedd4 | button | Acceptance | Yes,No,N/A
d55874de-7ea3-546a-b33c-576b1f75eb88 | note | Key - S
f5adde79-4660-5745-901f-9ba00463f4e7 | note | UGL Key - S
31175873-73d6-54c4-b918-3174d3f4efd1 | note | SHL Key - S
0a72f2ea-57af-5667-a4a6-06307ba777c7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6e3d2729-e48b-5b2a-9794-4ea1acb92dd0 | tickbox | Test reports
| checkpoint | 2.8 - Compaction – General Fill
bb884270-feaf-59be-a600-5abec26bcd56 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
05d12917-fbc1-5758-8677-6ec9dcee6006 | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
bc5d9241-7517-592b-85fe-ff58f4c13fdf | note | ○ Minimum relative compaction to be 92%
83c40a5f-54f8-5c63-a42b-8c14a456cf2a | button | Acceptance | Yes,No,N/A
73f31aad-58c7-5d92-a349-b59e0dc854dd | note | Key - S
adf492b2-6aad-5d2e-83a4-4322dc9b2125 | note | UGL Key - S
cae9f35a-bf6e-561f-af4b-04a455754847 | note | SHL Key - S
9bb4978a-6ec1-5909-b652-893289272857 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9239e268-0440-5d33-9b4d-8dcfe8eebb75 | tickbox | Test reports
| checkpoint | 2.9 - Compaction – Select Fill
99d875bb-fe85-58e5-96f3-ea4e1823933a | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
10801a2f-3707-59f4-9581-861f619b3d28 | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
612ab17d-8a28-55b5-b69d-c3473b39a27d | note | ○ Minimum relative compaction to be 97%
cb43e6d3-2048-53f8-bb62-c9b26fa9e14e | note | ○ Layers not to exceed 150mm compacted thickness.
3cf32d62-c834-5e43-9773-be84621efc4a | button | Acceptance | Yes,No,N/A
9da1c436-0bad-5fe0-bf14-c28271914954 | note | Key - S
e7e83739-6d73-5494-8537-eb8a7b3bebcd | note | UGL Key - S
40826797-56b4-5756-b52e-20a838c3cc70 | note | SHL Key - S
9b59522e-62b2-50ef-a4b4-1ee7985d0b7c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f1957a72-ff7e-5466-9285-e9ee6875fdd9 | tickbox | Test reports
| checkpoint | 2.10 - Moisture Content
19761f25-2593-5ae0-b042-aed249a07cd9 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
e10142cb-b80d-560b-abaf-0ec1e117b201 | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
610fb572-a673-5707-807c-d34bf335d7fa | button | Acceptance | Yes,No,N/A
21e94893-7b23-5c13-95ed-8193222e1450 | note | Key - S
13e3d2be-203f-581e-8d38-363c240a2050 | note | UGL Key - S
e775a438-3407-52ba-b2d9-1c94bc8dc289 | note | SHL Key - S
cc13a7f5-e89b-5bc8-81f5-43d482b771af | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d0ddeeec-b716-5cca-9dac-0026760a953e | tickbox | Test reports
| checkpoint | 2.11 - Marker Tape
0a0a3811-7cdf-5719-b859-35aecd60c6fb | note | Ref docs - Design Drawings
5ec0eb52-2bc2-5167-a2e5-764c57f5b747 | note | Acceptance Criteria - Detectable Marker Tape to be installed a minimum of 300mm above the pipe. Tape to be red and labelled “Danger – Buried Fire Main Below”
78ef5e3b-28d0-5db8-b485-fa2d17bd5868 | note | Key - S
8fe73eb2-66bb-5cfd-9b72-c09dca9975a7 | note | UGL Key - S
610d5196-4b0e-5c31-aca8-892e9fab57e1 | note | SHL Key - S
| section | 3.0 Testing, Commissioning and Conformance
| checkpoint | 3.1 - Preliminary Pressure Test
658b9809-c9b3-542a-9562-6d64543e4863 | note | Ref docs - AS/NZS 3500 Cl 17.3.1.
baac80e3-2bfd-5e97-bba2-8ce5033c7596 | note | Acceptance Criteria - Subjecting the pipe to 1500kPa for 30 minutes and checking for any leak.
af568c36-f89e-510c-96f3-3eb0601db28a | button | Acceptance | Yes,No,N/A
7a357b65-c0ad-5a26-a3ac-f9b62fa41c5f | note | Key - H
051871ec-a337-596d-ae55-7eb7dc152002 | note | UGL Key - W
dd429d1b-dda5-5b7e-8fc2-a8de293c5121 | note | SHL Key - W
| checkpoint | 3.2 - Hydrostatic Pressure Test
a43c674a-b701-5dff-9f9e-625f35117764 | note | Ref docs - AS/NZS 2033 Cl 7.2
ee4f8f9a-8aca-57a0-8d01-382bc4a59f92 | note | Acceptance Criteria - Has the line undertaken a hydrostatic pressure test in accordance with AS/NZS 2033 Clause 7.2 achieving at least 1.25 times the maximum working pressure of the pipeline?
bf75e12f-dc23-52b2-ac86-20e75b5d7fb5 | note | HOLD POINT
4f8780cd-5d08-565f-9fe2-c641d6dfe377 | button | Acceptance | Yes,No,N/A
5023016b-c7ee-59a5-9fd1-36011a2d9d47 | note | Key - H
89a39c94-e020-5d93-bf52-331fc126da37 | note | UGL Key - H
4164db28-02fd-5780-bcde-5f94fedf6948 | note | SHL Key - H
62475eef-04b7-506e-921d-3dd8fa329740 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
fd0044ea-de91-5f54-9c36-a20c3fe6dd34 | tickbox | Test reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Survey Report
c0da7a8e-15a3-512f-8e4a-c79dd30a644c | note | Ref docs - Spec. 0161 Quality [Cl 3.13] RFI-026
9ca798c0-1f5c-57bc-85b1-785d3177d4ef | note | Acceptance Criteria - Has an as-built survey of the system been completed to ensure all pipes are within construction tolerances.
9931fa96-d006-5538-9618-b74b8ebdc08a | note | Plan: +/- 200mm
176d5af6-3eeb-5360-a6d6-059104312b63 | note | Level: +/- 50mm
55f715b8-faf0-54b9-861c-69d197ac5e71 | note | HOLD POINT
4eadd377-06e1-5e0b-8b15-13c84751d660 | button | Acceptance | Yes,No,N/A
33dbfa69-1d12-5866-9521-711b40ae2231 | note | Key - H
fe8c77ab-873a-5291-bc5c-edaad46c712d | note | UGL Key - H
b8cb4c01-e831-524a-9c30-6a08e5161a36 | note | SHL Key - H
53db7897-62c1-52d2-8cc6-0c554b8b48e7 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
9e5726f8-b6ff-5862-b8f7-77bfcf521cc5 | tickbox | Survey report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.4 - Acceptance and closure of non-conforming items
1d89d995-969b-51e5-ab26-1d1428e2fc8f | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
e8427969-ec9d-5077-a62c-7c05a0329ab4 | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
5278f50b-546e-5c08-ab53-2e42bc1ae23b | note | HOLD POINT
5c90771e-7cbf-5afa-9d81-4e4a491d4127 | button | Acceptance | Yes,No,N/A
1e0dc990-5aee-569c-b3af-18d1ff5160b9 | note | Key - H
01820eff-1ba4-5b97-8bdf-63aa4d1f87ac | note | UGL Key - H
9da76c7d-ae47-582e-a0b4-12b76cd09c87 | note | SHL Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4. | itp | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4. |  | ee2eca22-9a52-4656-a5da-5f71c8719ae1
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
0f23dc21-f8da-599a-8422-b42f00eaaa31 | note | Ref docs - Issued drawings / Site copy drawings
637573b9-9ea9-5a10-adcb-c33690a4f665 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
2972d9ab-7417-5928-8093-f201977a26af | button | Acceptance | Yes,No,N/A
12af8d57-272d-58be-8d37-f26a8c157dd2 | note | Key - S
a51e8c43-245d-5694-a5c6-c4af6d8b43fb | note | UGL Key - R
| checkpoint | 1.2 - Determine lot size
1a5ab8da-ef6b-5461-9251-c9153f63bd58 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
e89ab71f-7c3d-5c5a-b3ac-b06460d63189 | button | Acceptance | Yes,No,N/A
fac066b3-8062-5ce5-88fb-3b5281ed8df9 | note | Key - S
9e1fafc7-3bdc-5d46-aa07-03bc889bef6d | note | UGL Key - R
c0a8081b-e0ac-55f4-944a-17ef22648db2 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
25918b83-dd71-5a66-9cc8-92271ee3f0c5 | tickbox | Lot map
| checkpoint | 1.3 - Material Certification
6a3ad37b-d497-5b73-98eb-8efddc99c91c | note | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
a4e3625c-264b-57d5-8d79-d895c00421c0 | button | Acceptance | Yes,No,N/A
07c5afc5-3ffb-5460-939f-3c333a950e1c | note | Key - S
89d759d1-ab13-5261-9df1-085508063e44 | note | UGL Key - R
41aba242-7ca0-553f-b66a-c82abf2624fb | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
dad1b2a0-dd5e-5efc-bd3f-d2c2ac86b92b | tickbox | Material Certification
| checkpoint | 1.4 - Geotechnical Engineer
99f9fa54-ef65-592a-bc46-68ce1c86ff0f | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
50878205-ff9f-56f2-ab5b-697f346c3dcf | button | Acceptance | Yes,No,N/A
4e93d879-f352-51ec-a9b6-05bc127419ea | note | Key - S
0e062795-453b-57ee-84f1-65b9add5811a | note | UGL Key - R
37bf88e6-368f-50f9-b129-29a09e2ea176 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
c4cd47cf-0a1f-5ae4-bf28-21c56a7a95ff | tickbox | Bore Hole Log
| section | 2.0 Materials & Equipment
| checkpoint | 2.1 - Screw Piles Shop Drawing
0e8d809a-181f-5707-9921-f3f68195fcc5 | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
b23b2ed2-7aa0-5bc7-a089-df6beb2b1d4a | note | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
1023f0ff-5bf6-5fc0-a64b-97cab1e3a1a1 | note | Shop Drawings to include.
2ce57a3b-152f-50eb-bddb-490dfc92db76 | note | ○ Dimensional Requirement including tolerances if applicable.
d509b1a6-a0bc-5cfd-baf5-23708aee72a7 | note | ○ Sections designation and material grade
f855b6de-552c-5159-8034-ab1b30b2cfea | note | ○ All Welds and weld procedure
84ef875a-f03c-5783-8032-f690cae2947b | note | ○ Corrosion protection requirements
e8dc42bf-6929-52e9-af5e-5052af7e1052 | button | Acceptance | Yes,No,N/A
fca86555-7e4f-5b31-a2cb-cac26da80193 | note | Key - H
547ea1a5-63e9-5a53-8d38-8f433fd4c594 | note | UGL Key - H
f8ded7ac-9bcc-596b-8393-d965dffee6a1 | note | SHL Key - H
6e4829bc-bcbf-5752-8301-2485a43f9d94 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
c199bdef-8722-5583-8492-02721fdb9b87 | tickbox | Bore Hole Log
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Manufacturing of Steel Screw.
0769f6e5-8a5b-55cc-9ab9-98fb67d62e89 | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
755a21c3-4e0c-5bfb-b069-d156534a5a02 | note | Acceptance Criteria - Fabrications
6f7884a2-8f53-5cf8-bc38-6a68971f89da | note | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
88d6aaf5-1deb-524a-a1e5-aaa669135379 | note | Welding
7860925c-bedb-5c1f-af58-257db3d75816 | note | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
4bd8155d-7d08-5843-9dcb-faafb900a3ee | note | Helices.
27c89773-78ab-5bf6-bcbc-9ddc75a19e32 | note | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
a786d9e9-1785-5bbb-8fc2-a7a70fd52d27 | button | Acceptance | Yes,No,N/A
181b3852-00fc-535f-96b6-50161182a2e9 | note | Key - H
0f1a9574-e689-5e75-aaab-8e0086db0f6e | note | UGL Key - H
69e9b346-e8ec-5a89-b83a-b4e16042dbf1 | note | SHL Key - H
190cd590-e959-5e44-95b2-86210cd7d6f9 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
f07d08df-5a95-59dc-8042-89aae99a3adc | tickbox | Material Certification
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Piling Machine
57fecc29-1d2a-5fe8-9e12-22699c62b4f1 | note | Ref docs - Drawings
62491929-985d-5598-9f6f-812447246527 | note | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
6e8673b0-bde4-5982-a563-3b43bae40e45 | note | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
755f8af6-b6d7-55e2-9fab-8c054396390a | button | Acceptance | Yes,No,N/A
7f24bd46-7399-53e2-b0ae-358a91a65e9f | note | Key - R
93e4290f-c0cf-5eca-8d1f-94aebaca3bcd | note | UGL Key - H
b1095940-bfe1-5152-b031-85b0c291d0bd | note | SHL Key - W
fc6e0c75-16bd-591b-b115-1917b89fa22f | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
5e75acb1-d07e-538b-b4e8-d6942b7c7592 | tickbox | Calibration Records
| section | 3.0 Piling
| checkpoint | 3.1 - Survey Setout
e7822654-2447-5538-b4f9-712e48170bb1 | note | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications – 3 test/ centre piles to be located as per the markup.
c5277891-3dcc-51c1-8e82-abc28a870246 | note | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
9986b806-d60f-572d-9f37-c31cca826991 | note | ○ Static Load Test Compression: 4 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
4922342e-2923-501e-b1cc-6f9c3a86d16f | note | ○ Static Load Test Tension: 2 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
c4dabcea-2b0a-5749-b369-0b1feea19ff3 | button | Acceptance | Yes,No,N/A
cbd21f48-848e-575e-8a75-f39802883653 | note | Key - H
5cd0f293-9e90-5a05-8025-77b5309d802d | note | UGL Key - H
b07b8e8e-5c82-5961-9735-6120bccc335a | note | SHL Key - H
6c5897fd-a5dc-5ed5-8bbb-216b359fcf76 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
df9d01d0-71db-5e77-b346-da3fc42d07a8 | tickbox | Survey Report
835e2e43-5d58-5844-a717-bb258e610b89 | tickbox | Test Setout Plan
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Screw Pile Installation
871f0674-1399-5479-b3ef-684923c08f8a | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
b4f15205-0e2f-5405-aca4-002a6f4b1d42 | note | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
22f17010-d81f-50e0-9bc8-52a21097e6f9 | note | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
a766e73f-0c31-5228-8b5c-4d4f643dc00c | note | ○ Screw piles installed as per design and with min driving torque of 48,000NM
d796d75f-bf4c-50ca-869b-f8d2ee27951b | note | ○ Rate of penetration and torque vs depth to be recorded.
df7c3995-c01e-588d-8e39-a04490a0f2d4 | note | ○ Each piles finish height is to be checked.
1d8c0082-241e-5531-9907-9b6157111b56 | note | ○ Testing piles to be 300 mm off the ground level, Reactive Piles to be made to suit ground level.
945d2386-7ffb-547a-8f45-9b8bd8f2fedd | note | Notice: 2 working days prior to excavation of test pile
482451d0-2b8c-53ba-8fb8-3234d1d16275 | button | Acceptance | Yes,No,N/A
accf6cdd-ac56-5527-aa76-8e0c47325d46 | note | Key - H
bd3816e9-95fa-5a71-b2e4-844a5a70e9a6 | note | UGL Key - H
6e6ece65-00b3-54d0-a9a0-c3ede8b0bc41 | note | SHL Key - H
9f0ab7de-57e5-5a09-a9d5-c2eb796a933d | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
9528dfe3-bfd9-551f-b7d5-3d4a9bf6f928 | tickbox | Geotechnical Engineer Sign Off Sheet
a05eb34b-3930-55a6-ba8d-93f2b8eb1dd1 | tickbox | Pile Log Sheet
| signoff | AUTHORITY HOLDPOINT
| section | 4.0 Static Load Testing
| checkpoint | 4.1 - Static Load Testing Set up
a9afe9a3-94dd-5af9-9d7d-9060fb39b5f0 | note | Acceptance Criteria - Australian piling Experts Static Load test Method Statement for set up of both Compression test & Tension test configuration.
3097da13-d671-57d4-b9b9-8e01051c2fcb | note | ○ Place I Beam on the Test/ Reactive piles. Pile Stubs to be facing the same direction as the inner beam.
7b8e86f2-8e07-5147-b21d-ef46aa6dc5a5 | note | ○ Place Hydraulic Jack and the Dial Gauge, allowing the dial gauges to slightly touch the reference beam and securing it into place.
15044069-81d9-5018-bcbd-ba7cf65b7b92 | note | ○ Circular black casing to be turned until the reading is zero at 12’0 position.
c10894d4-969d-5f61-9c21-2b3e4e9f201e | button | Acceptance | Yes,No,N/A
74536ce2-947e-5328-8c8c-3d5a1462898b | note | Key - W
6f91848b-aa60-590a-b477-7026a5e34b24 | note | UGL Key - W
2050903d-306d-5ec9-bc9d-5c9bdfd6fc58 | note | SHL Key - S
9f540a42-6681-5863-8d08-e17ff29df943 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
45a1bb89-205c-595b-b0ac-796ea8f0e1bb | tickbox | Photos
| checkpoint | 4.2 - Static Load Test Acceptance Criteria
fd1c4d40-1181-5666-9b58-32549a6c4b75 | note | Ref docs - Spec. 0003 Piling [Cl 3.13]
e76f2075-a7da-5efb-a53f-70055ee125f1 | note | Acceptance Criteria - Test piles 1 & 2
f7c6f861-b0b7-5e88-8d8f-93b622f8d41f | note | Test results to conform to the following:
51ee2831-03a9-5066-9bc9-3d16e364c017 | note | – – – – – – – – – – – – – – – –
07993c19-2f5e-537b-b1bc-1ddb699d36a0 | note | Test Type ¦¦ Load: Description ¦¦ Magnitude (kN) ¦¦ Maximum Deflection (mm) ¦¦ Symbol
856ce198-eb8a-51c1-a38c-bf1956be42fe | note | – – – – – – – – – – – – – – – –
fbaf8f7a-fa21-5448-a21d-faea14b0e851 | note | Compression ¦¦ Serviceability (Proof) ¦¦ 120.0 ¦¦ 5.0 ¦¦ Ps
d17d0e55-0691-5620-a0f8-1fda2b413324 | note | Compression ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 180.0 ¦¦ 10.0 ¦¦ Pg
f8875a03-5c97-5abc-9bc0-12e56c6492e3 | note | Compression ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 450.0 ¦¦ N/A ¦¦ Pu
86799897-0c9a-5dbe-a14e-b7594a4c0c83 | note | Tension (Uplift) ¦¦ Serviceability (Proof) ¦¦ 80.0 ¦¦ 5.0 ¦¦ Ps
86435cd2-e861-52d1-a6bc-50bce3671e5f | note | Tension (Uplift) ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 100.0 ¦¦ 10.0 ¦¦ Pg
7775ede4-8dda-5cfa-be61-fa358ce18c80 | note | Tension (Uplift) ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 250.0 ¦¦ N/A ¦¦ Pu
2df981e6-8085-51cc-985a-0df173210a61 | note | – – – – – – – – – – – – – – – –
fdcf019e-64f8-53d9-9b36-639557ec1ad1 | button | Acceptance | Yes,No,N/A
1c35cd27-5f1b-534d-aeb6-4d4e0af43607 | note | Key - H
46b9adf1-c000-5f3c-86a2-18737a0e90ea | note | UGL Key - H
733a355f-082f-5a79-9ee1-d92ccf514bf2 | note | SHL Key - W
5b718393-456b-57d7-bdf0-a4540111d14d | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
be7550fd-44de-5329-9a87-5037718ee7e0 | tickbox | Static Load Test Reports
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.3 - Static Load Conformance
ef8a74bd-5c29-5cf0-aeff-2fb9be0832ee | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
c032b46d-3957-5df8-8458-0a3a9a25fb2d | note | Acceptance Criteria - The testing piles to conform with the following.
7ba459be-ffd5-56e7-b485-749ccd989e60 | note | – The loading system shall have a capacity of at least 500kN.
74214283-8dee-5119-925b-a2513275ae3b | note | – The overall loading and measuring system shall be capable of accommodating a pile movement of at least 25mm.
c8bb052e-34cb-5c48-a293-45ce5ab4dfd0 | note | – Movements shall be measured with a system capable of delivery an accuracy of 0.1mm
c9b045c7-4df3-5269-b90a-b7a6ee75d706 | note | – Test piles to have a min spacing of 2.5m
366cf292-3195-563d-a8c6-eb19fda6dcd0 | note | – Test piles top be min 5.0m from location of permanent piles.
fa1bd7ba-13c1-5ed2-ab9b-0a15dd21f18f | note | – After UGL review of the Test report, the test piles to be removed and kept on site to facilitate inspection by UGL to determine their suitability for reuse.
0e297c71-8c01-5477-95fc-850f0f1ab8b6 | button | Acceptance | Yes,No,N/A
4a9314fd-b9c0-541d-b02f-015ac557b3cb | note | Key - H
9ab9dcad-efe9-577e-8a5c-7cc79dea98c6 | note | UGL Key - H
52a18888-0df8-5be5-900f-aeb3f014f8c6 | note | SHL Key - W
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.4 - Test Method & Loading Sequence - Compression
bbcbf6b8-c127-5a36-81e0-1ad18bc01c25 | note | Ref docs - AS2159-2009 8.4
4a8f2ec2-4aa0-587f-be4d-851de3392555 | note | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
27615bba-b5a5-5e52-8d0e-94c8be49d10b | note | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
d699aca1-9ea9-5519-80be-8e29257b87ef | button | Acceptance | Yes,No,N/A
aa383a15-ca68-5ac1-81fc-c5b228c49772 | note | Key - S
c0056064-6cd0-5e14-baf7-24394c8a3ff3 | note | UGL Key - S
fe1a6dcd-dd66-56fb-af69-35cc6ccce3ae | note | SHL Key - S
fc29fee5-ae64-569a-95de-88ebb5133eb4 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
cdcad820-d475-579e-a7a8-d6aabe113987 | tickbox | Load vs Displacement Records
| checkpoint | Test Method & Loading Sequence - Tension
edb9a01c-5b7a-5c9e-8f23-d321be0e9aa9 | note | Ref docs - AS2159-2009 8.4
09a7b088-061a-5cb8-9ef7-87f195060195 | note | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
cf451820-db2b-5987-a0eb-89f0bd06ea77 | note | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
0ff6f6c6-04ae-58e3-b104-40a6d47420c7 | button | Acceptance | Yes,No,N/A
0425bd57-5833-5a1e-9ccc-477a79a10b12 | note | Key - S
2a2b0316-7641-58af-881a-f0a017ba0321 | note | UGL Key - S
4c18bb70-7ab1-53b0-9cfc-9bb6f3a5aa35 | note | SHL Key - S
7da07abf-4a24-53a9-9703-2109f457e35b | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
e7c50564-30dd-501f-8dc2-1177f713c5c0 | tickbox | Load vs Displacement Records
| checkpoint | 4.5 - Reporting
1f3ad748-517e-5df8-9e35-bd6ab7233c84 | note | Acceptance Criteria - Test reports forwarded to UGL/Snowy for Review/Acceptance in accordance with AS2159 A4
1f61aded-8cbd-58bf-bc8b-af1624347f15 | button | Acceptance | Yes,No,N/A
1a2c2294-7e5d-51c9-91a8-5dbc657ae434 | note | Key - H
f318a3b6-634b-53af-85d2-515be59d5564 | note | UGL Key - H
f7102a2c-6a99-5437-8404-2bd3aa321d04 | note | SHL Key - H
827039bb-ceda-5e71-9b2f-a23be8427ac5 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
248efcc5-ad32-59b6-badf-4b4b9ee6300b | tickbox | Test Reports
| signoff | AUTHORITY HOLDPOINT
| section | 5.0 Conformance
| checkpoint | 5.1 - Survey
036e2442-c56f-5e8d-b172-3a4589264906 | note | Ref docs - Spec. 0003 Piling [Cl 3.10]
dc17a448-3ff7-5aba-b8cb-aed3f80b9f58 | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
691adba0-761e-579e-b053-88a0c09780d1 | note | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
585dca69-1282-53a0-947c-1eced45fa42a | note | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
80213c23-218c-56b3-9950-0b9e2760818c | note | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
bf4f2fab-617b-595a-8d35-afa5d9df953e | button | Acceptance | Yes,No,N/A
a3da262d-ca15-50e3-891d-784bbe0f9c23 | note | Key - H
57fe4a33-cabb-59c3-ba3b-e39799aa7e8d | note | UGL Key - H
8de5f79b-b047-54b7-8c43-078019b76692 | note | SHL Key - H
d35d3c33-9fa8-5d18-9e36-56b11c2420fc | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
63b5fdfd-e682-5829-806c-6eeed78a092e | tickbox | As-Built Survey Conformance
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2 | itp | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2 |  | 4fa6e1a6-3a25-45d3-9b9f-d8a7fc96d3eb
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
ad18b816-4ed8-5979-8bb9-24711442b6d6 | note | Ref docs - Issued drawings / Site copy drawings
d6bafaf7-b31b-5e72-a04b-a66a9cb55304 | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
9c420586-452b-5520-868d-ef34b217598b | button | Acceptance | Yes,No,N/A
a0694a4c-9271-53e5-bcf3-0538ef0a963b | note | Key - S
| checkpoint | 1.2 - Determine lot size
6b233749-75ac-51cc-839d-ee418bf30fb3 | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
133e9b54-c6bc-5d32-8973-551e047d9417 | button | Acceptance | Yes,No,N/A
aab8e36f-a3dd-5f10-bbb0-7aad69cbedfb | note | Key - S
5b1e8239-54df-5772-9409-6225241dfbe2 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
9038ae4f-be08-575b-88ca-b7855b419575 | tickbox | Lot map
54df3821-85e3-5429-a407-e6487891fe3d | tickbox | Piling Schedule
| checkpoint | 1.3 - Material Certification
445f84c4-769c-5470-8f6c-a3319d8a2304 | note | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
a17fbd5e-c194-51e2-803b-dbc3e80e1e83 | button | Acceptance | Yes,No,N/A
12e99b27-4f7d-5c76-a447-616f79328c52 | note | Key - S
ac2702ea-3e17-52f3-8e90-53493a3e2806 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
b0f28937-02dd-5cf5-bbbe-7ff8361aa7f9 | tickbox | Material Certification
| checkpoint | 1.4 - Geotechnical Engineer
0fb93aaa-ec61-5140-9aad-e2147918f63b | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
2d80147e-8a06-5f31-adee-a3e136933c42 | button | Acceptance | Yes,No,N/A
a25d93aa-c5a3-51db-b843-6ba7bbe1dbd9 | note | Key - S
5d5098f3-3d9a-5bbc-96f2-6b08420e2aa6 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
c867717e-4202-5c1d-a227-13c2686c251f | tickbox | Bore Hole Log
| section | 2.0 Materials & Equipment
| checkpoint | 2.1 - Screw Piles Shop Drawing
adec23e4-0d8f-5119-a54a-f8b11d85db7b | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
72325818-6399-5d47-8962-b4f6b9eb632b | note | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
fc6ae8be-2068-5f38-b21f-8f3a4dc7f217 | note | Shop Drawings to include.
a38e1b46-2f95-5898-a632-437533b33484 | note | – Dimensional Requirement including tolerances if applicable.
b5f53bb7-48b0-5552-aca3-3b76b2e38144 | note | – Sections designation and material grade
ab21d4f9-81bc-557d-8f34-a484187db8ca | note | – All Welds and weld procedure
ccea1a5c-9e19-5dc0-8d64-744ef961c164 | note | – Corrosion protection requirements
3518e232-58ee-5479-bd55-f41715f3a7c1 | button | Acceptance | Yes,No,N/A
05dbef10-0922-528f-940a-b4538e723368 | note | Key - H
ebe2575f-a6e5-5cf3-978d-cf8b39a34b52 | note | UGL Key - H
c50be11e-146e-5719-a6fc-f635014901fe | note | SHL Key - H
7eeac7e1-56fc-5a17-8e33-0b952c226da6 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
033d1ef7-aea5-5b16-b3fb-b67e71274ca7 | tickbox | Shop Drawings
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Manufacturing of Steel Screw.
65bda2f6-ba83-506e-8413-e1aa43658871 | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
5e4e9c13-cace-50a1-8636-afdbd3278042 | note | Acceptance Criteria - Fabrications
b16fd25e-fd0b-5d0f-8523-960b7d8a7361 | note | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
e36b9b90-dbc5-5e09-9de3-89382581fe35 | note | Welding
0c2d7994-33e7-5213-b92c-28723951fc76 | note | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
d220f89d-5841-5ffd-a3b1-95c65a4bc555 | note | Helices.
5fb04e66-33a4-58bc-8ebf-abb0d84b651e | note | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
7165bf54-0f3c-5c45-a272-ce86cb5c1acf | button | Acceptance | Yes,No,N/A
dfd05cce-0cad-5619-b9dc-f7f46e261d93 | note | Key - H
a455d09f-27ff-515a-b60d-d1377d122f9f | note | UGL Key - H
15ad9620-939d-52db-9dd0-34b710353537 | note | SHL Key - H
d56dd816-fef6-5574-9d4a-c1899df8c254 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
69e46334-1c27-5945-88ee-ac11480320de | tickbox | Material Certification
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Piling Machine
84ebdd4f-439a-5371-a9a7-104369f595ab | note | Ref docs - Drawings
8ecb3f3c-a670-5810-a345-792459614b7d | note | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
0819ee95-2b3e-5bac-ad57-5c0d356b8c21 | note | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
1db5c4b1-1dd7-57c9-acbd-06dcb31a9e6c | button | Acceptance | Yes,No,N/A
f0674c92-2694-587d-b1ca-02614db5b94d | note | Key - R
8cdd7263-bbdf-51d5-910d-549eda653bda | note | UGL Key - S
369b7e8a-c56a-5bcf-b64b-6439fbbaa81a | note | SHL Key - W
bce8124a-f6b4-5572-99b5-f88f1a68d66a | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
324b72dd-7885-5de0-8c2b-0bc223a24ac5 | tickbox | Calibration records
| section | 3.0 Piling
| checkpoint | 3.1 - Survey Setout
7eb6d4f0-2b35-5a96-af43-dd1a395de55a | note | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications
b665ea15-b6d1-5e59-bbd7-17becb634a75 | note | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
3b6f3e53-5594-5ac6-b1b8-c2e2ffa595ba | button | Acceptance | Yes,No,N/A
0b0d946c-4713-5b0e-9c40-a4338db4c1ec | note | Key - H
e7b50fc5-76e8-52d1-94ac-2d8545ed92a1 | note | UGL Key - H
ae185911-4d69-51bf-8087-091320a15d00 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
e5eaf2e1-8dcc-5d73-b142-d45b900a9ec4 | tickbox | Survey Report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Screw Pile Installation
d2794989-02d0-5c09-9bf7-28e303858b2a | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
af0ec9b2-280b-591a-a94f-d9a315090d83 | note | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
0dc523f8-03e1-51b3-82b0-03d59ac5663d | note | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
006593b3-9d87-58b1-bd9e-5fb52bc00e51 | note | ○ Screw piles installed as per design and required machine torque.
074e4d47-642c-5d0e-8af1-f575788d6f3b | note | ○ Rate of penetration and torque vs depth to be recorded.
230e35bd-2faa-5717-a793-25fa5395a5e8 | note | ○ Each piles finish height is to be checked.
ca7d3dd2-01b2-5c2f-9a72-8c65054c7420 | note | Notice: 3 working days prior to excavation of test pile
7068b210-2450-57be-b41b-57ed5c8837b4 | button | Acceptance | Yes,No,N/A
b798d336-e5b5-5607-9377-e759aa8bcd50 | note | Key - H
f64ba602-30c5-5ce2-bf61-9fba424107a0 | note | UGL Key - H
722f8f4e-9f81-5bef-bf16-f769ce7a62ca | note | SHL Key - H
3d9ff63e-124e-5e30-9a16-3e94cb5cb30a | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bdffd828-faff-5cba-b432-2cf981c9d7a4 | tickbox | Geotechnical Engineer Sign Off Sheet
396a305e-c8f2-52e2-bbb4-32f1da643a1a | tickbox | Pile Log Sheet
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Concrete supply
2b0e7585-7f66-51d8-a9f7-1f103a3b59f2 | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
197e49c0-792f-507c-aa73-bca08e0163d3 | note | Acceptance Criteria - Verify:
921ba7c2-27d5-5656-b474-f668c768247d | note | – Concrete mix
f5e68cb8-cd24-5568-b97c-316e3d5a84a7 | note | ○ A concrete delivery docket to be supplied with each batch delivered.
5db562e5-6365-504a-af69-1bb6cc0e5e4a | note | ○ Concrete work shall be in accordance with the technical specification for concrete supply, construction and grouting and any other notes on drawings.
c519f2a3-7b20-5d55-99b1-25d0add7fc0a | button | Acceptance | Yes,No,N/A
95210026-8586-5115-81ce-3bb3571dbf2f | note | Key - S
50d0d9e4-43ab-5261-a760-eca74aefe467 | note | UGL Key - W
137b186a-418a-5808-afd0-098cf1881407 | note | SHL Key -
b95115dd-0f84-5969-8dee-16636b2cad7d | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
d881d1e1-5040-5171-828b-6ac5095ef505 | tickbox | Material dockets
4d23a1b6-574f-5eb5-bc35-c77997bb0fb8 | tickbox | Concrete Pour Record
9f089f5c-458c-53c6-b21c-64a2a89079bf | tickbox | Pile Log Sheet
| checkpoint | 3.4 - Concrete Placement
8233d1f6-03df-5ec2-9de4-d888ea44c8eb | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
82d3ba68-d203-51ec-bcf9-0d62255d105f | note | Acceptance Criteria - Concrete to be placed as per the construction drawings in accordance with AS3600.
182ee511-9c65-59ed-9a1b-00ed09c22022 | note | ○ Prior to the pour ensure there is no water or debris at the base of the pile shaft.
fe08bf6f-a23c-5ae1-afdc-4aa52d48d145 | note | Notice: 1 working day prior to placing concrete for test pile
6f9c75eb-8b60-5bf3-9f4e-605f8e092d21 | button | Acceptance | Yes,No,N/A
15e9be40-6e3b-55a1-bea1-0f1599bbf3ed | note | Key - S
b11c6700-df90-5b5a-966b-0bd0e06ed7be | note | UGL Key - W
| checkpoint | 3.5 - Pile Cap Installation.
dba40be3-900d-5c4e-9a31-ef9234646436 | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
f124edf3-e756-5dc9-a561-76d977d56130 | note | Acceptance Criteria - Reinforcement for pile cap to conform with drawings and specification. Reinforcement grade to be either 250N or 500N.
a6e48486-728e-58d2-bdbc-d5dc70be0753 | note | ○ Formwork to conform with drawings and specification.
0fc57c87-a6ac-54ef-a13c-0875478b6cdb | note | ○ Concrete to be vibrated adequately during placement to ensure there are no voids or segregation.
f20ff353-8f2f-5e0e-9608-e40d23a2b946 | note | Notice: 1 working day prior to placing concrete for test pile
a10e1135-f247-5e5f-a302-d27b59538000 | button | Acceptance | Yes,No,N/A
9ba8e4b0-cf1f-5ee5-a35a-ebe451c14544 | note | Key - S
b8b90135-6b37-56b7-8f4a-745efca166f4 | note | UGL Key - W
ff1eeebb-c050-52fd-82c8-fbcd918f25f7 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
f01e2917-c486-5c02-bc15-a9b9022e9c92 | tickbox | Concrete Pour Record & Pile Log Sheet
| checkpoint | 3.6 - Concrete sampling
096b6fae-cbb4-5e33-a515-35d29288340f | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
3d163fbe-7fed-53d5-9230-f1dfb82e7946 | note | (a) Compressive strength: One set per pour or as otherwise directed by Superintendent;
0a1b04df-3b16-598c-9bce-25620f84e67f | note | (b) Slump: One per batch of concrete (xxx mm)
cf421fdc-50df-5c9d-b568-17212bcdbd57 | note | Acceptance Testing shall be done at a NATA registered laboratory
2a26c838-0f9a-5aba-aff7-c837685f5df2 | button | Acceptance | Yes,No,N/A
64681501-0e55-50fb-a0ae-b8df81dcf376 | note | Key - S
579ac796-bad9-5ef3-b3b9-305d0288928e | note | UGL Key - W
7a396fef-ae75-5c83-ad1d-7b2dd0f9c5a8 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
581021bb-a734-579f-9dd6-788756ee7a4b | tickbox | Test report
| checkpoint | 3.7 - Concrete RL and depth
d8e5e81b-415b-5477-879d-3f4977074cf2 | note | Ref docs - Drawings
5f48697a-82bf-568a-b3e1-06ee7677ce2d | note | Acceptance Criteria - Screw Piles depth, size, position, and concrete RL as per the Piling Pile Log Sheet and Drawings.
44c72ca7-eca8-52fc-88e5-cf9e9ff4465c | button | Acceptance | Yes,No,N/A
ba98f98e-05d5-5fce-9c3e-d6827d558ccc | note | Key - S
40ba2de4-71bf-5974-938c-c0a9481a4c16 | note | UGL Key - S
605d6737-7026-5fcf-a065-98bd591306f4 | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
f0648d8f-ea74-51e2-b241-abe72102a174 | tickbox | Pile Log Sheet
| section | 4.0 Conformance
| checkpoint | 4.1 - Survey
d6421578-4688-5bed-844e-9e3ca2e0ceab | note | Ref docs - Spec. 0003 Piling [Cl 3.10]
5b82d3be-b8db-522e-9453-ecebb53ca3cd | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
25ad7c1d-dbe2-531d-a07f-83cd8f074498 | note | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
f3089c20-003e-5653-8b43-e6f6bf3c97ce | note | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
ab48c377-924d-5e88-ab72-fa66364f3d2e | note | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
44f1fc08-50a4-5142-be4f-0c608234925b | button | Acceptance | Yes,No,N/A
914955db-8d04-5561-8725-be2fd2ca98f4 | note | Key - H
c9219129-f29c-5105-a896-761a670c7d7b | note | UGL Key - H
7c261ade-d19d-5763-9600-4a51497ad7cb | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
33cef580-b118-5b3c-9f4f-345889cb59c4 | tickbox | As-Built Survey Conformance
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-023 Light & Security Pole Foundations - Rev.1 | itp | INF-HSEQ CC0375-ITP-023 Light & Security Pole Foundations - Rev.1 |  | 303a72c7-1083-4aec-aec3-9d3f1592fbb0
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
1d415336-d4c2-5d9a-8db9-c229dffaa13f | note | Ref docs - Drawings
7fa252f5-18f9-5190-82c6-1a525bc2e780 | note | Acceptance criteria - Check the latest site and engineering drawings BEFORE starting each task/set of tasks.
da29d844-6cf2-58ca-96b7-c4e02df3ec9c | button | Acceptance | Yes,No,N/A
5000947b-072e-5dbd-96a3-b7d497d7ff02 | note | Key - S
3b72413a-5bca-5b17-9ecf-106ce52f4ee0 | note | HPP CON Key - S
97e356b6-2483-56c5-97d1-b52f82e78a2f | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
4746c940-0561-5950-b3ff-71a561236e39 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
ea79c6bb-5a6a-54fe-9951-631542b1c538 | note | Acceptance criteria - Prepare a lot map for traceability of the work area
87be46a2-1b85-5859-9c66-5a543bd51a3b | button | Acceptance | Yes,No,N/A
294c8daf-464a-5fdf-bdb6-44b7e6a8ce88 | note | Key - S
1ebec481-9b03-52d6-9b8f-54c83c361827 | note | HPP CON Key - S
d9b0621c-1f2c-528f-8614-4c62a69b30cc | note | HPP QA Key - S
8ec8f48f-849e-50d3-818b-8eb14c0ce2b8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
cbdbd655-a5bf-51da-abaa-9db4f687418d | tickbox | Lot map
| checkpoint | 1.3 - Set out
a71523cc-e43b-5ef1-b6ed-332c3fbd48ae | note | Ref docs - Drawings
8cd22edb-4f30-5bfb-92cd-eb256054f38e | note | Acceptance criteria - Setout to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
cd0daa09-7fa1-5b36-82cf-3b277acaee91 | button | Acceptance | Yes,No,N/A
99e83070-a10d-510b-bed6-ac5f5d95d0f3 | note | Key - S
9574a8f3-45e7-5b88-9d2a-9090d9776e4e | note | HPP CON Key - S
f4eb36f9-7ef8-5c2d-8525-41cb56db78a3 | note | HPP QA Key - S
| checkpoint | 1.4 - DCP Test
0eddb9a4-e744-509d-8bcb-8de3763e905e | note | Ref docs - Drawings Note 8
6e699730-df82-59d7-8a4d-d1020fcd67d6 | note | Acceptance criteria - Conduct DCP test for each pole location.
494c55b8-055a-53b2-82e1-e36c7b52aec7 | note | ○ Allowable minimum bearing capacity =100kPA must be verified by a qualified Geotechnical Engineer.
bf7d3d9a-5763-56e1-b2a9-a14e0a1d4d9e | note | ○ Ground improvement shall be made If existing soil profile is inadequate.
da120a9e-9922-53e4-81cb-9e4de26bbf3e | note | HOLD POINT
b781fc9c-4324-532b-8454-d1c2b2295e48 | button | Acceptance | Yes,No,N/A
b31a2e6f-dc55-5114-b903-7ffdeddf0b58 | note | Key - H
de8aee8b-9c60-5b28-9878-d9d9fa2d8da1 | note | HPP CON Key - H
0b8a0df2-4642-54e6-a47b-d9a5b16ea4ff | note | HPP QA Key - H
da62b3a6-935f-54b2-b578-eb2854c6c0de | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
6cf15ae3-a356-504f-b0bd-b779670a9f50 | tickbox | Geo report
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Base Bore
| checkpoint | 2.1 - Bore Excavation
9bda56a5-2aa3-5a3c-a75c-49af4c90e1e6 | note | Ref docs - Drawings
13ada146-9c4d-5c98-8b20-fe194b351c36 | note | Acceptance criteria - Bore to the correct diameter and depth nominated on the drawings and remove any loose material at the base.
95a06011-7be1-51cb-bc3c-6cca5daa4c03 | note | ○ 450mm – Light Pole & Joint Use Pole
96da773d-96b8-5030-aa21-be2244611acf | note | ○ 600mm – Security Pole
11dfabba-27bc-5692-a987-e401210c2b9c | note | ○ Depth to be verify by qualified Geotechnical Engineer.
0d7d0628-a11b-522d-bc98-d68e77baf189 | note | ○ Base must be clean and dry to be inspected by the Superintendent.
520d6c68-d869-50c7-8046-847a267e4dd4 | note | HOLD POINT
39d6a889-6c8b-58bc-9376-58fa53d2bc36 | button | Acceptance | Yes,No,N/A
7a6786bd-0fa0-5d46-a287-2470230c92d3 | note | Key - H
b9c63d72-fcdb-5eef-9ecb-653cc5e68810 | note | HPP CON Key - H
819071d9-831b-5ec0-a824-1660623d6af9 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Formwork Sleeve
9ae55def-3a13-505f-b668-e637449fccb7 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
9ef03baa-be5d-5b01-af0a-fbe1135c4ab8 | note | Acceptance criteria - Formwork to be set as per drawings and adequately supported and RL checked.
118cbbcd-2e8d-56fd-9752-1dcd5d31f021 | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement.
d81f1c02-0cc0-50a0-a94b-d41d2ebc19ba | note | HOLD POINT
6a8c1df8-f0cb-5c08-878c-84dc945da3cd | button | Acceptance | Yes,No,N/A
a8d71608-ddfd-5db4-a036-9ffc7f91b85a | note | Key - H
8e553e50-9021-50bc-904b-9133c915feb7 | note | HPP CON Key - H
49ee2794-c7bc-57c2-8156-773cda4ff761 | note | HPP QA Key - H
0556def7-1b78-5ca3-a695-58c744cf2f4e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
f7a2d040-4616-56b9-911f-8e2be56705c1 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Placement of reinforcement cage, HD Bolts and Earth Lugs (Supplied by Client)
ff1a1f67-f426-58d1-aa64-ec39a84303bc | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5] Drawings
eec2e430-1c50-5733-8ca0-2a11ae6e5e3b | note | Acceptance criteria - Ensure that cage is clean and straight. Plunge the cage centrally to bore hole and ensure spacers are attached at correct locations.
325c8632-084e-593c-aa1f-9b526780e549 | note | Reinforcement cages and embedment to conform with drawings and specification.
03c884d3-5c54-52de-b22e-d6da0d09f753 | note | ○ 4-M20 HD Bolts grade 8.8/S
bef67c26-6f7f-5a6c-a2a9-0666690243aa | note | ○ 500mm min embedment
01e3bbbd-0fb9-5ed3-8e89-c6015ced20c2 | note | ○ 130mm projection
400601c8-9e62-5df4-8395-a5e7d3f69af9 | note | Or
f3a490fd-f3a2-52b4-a04a-82e825b6a510 | note | ○ 4-M24 Bolts grade 4.6/S
52de79dc-5a0f-5d11-a6ef-81ce8f46501c | note | ○ 600 min embedment
4ae0b679-7e56-5438-82bf-587cf790ec19 | note | ○ 150mm projection
1471b9dc-b16a-5636-8bd7-ab0547c6dd22 | note | HOLD POINT
806bdcc5-a02d-54f4-bf73-639402de726e | button | Acceptance | Yes,No,N/A
b9665c93-66c7-5fe6-86b6-4ace1cce8719 | note | Key - H
6ba9be13-1ae9-5c46-b16e-c933d8c4590c | note | HPP CON Key - H
e2c255e1-6c7a-5f58-9d08-4859acf6f67c | note | HPP QA Key - H
d71c0995-106b-57a9-9c84-6c5a071207ba | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
4966b010-8987-5b87-b6a4-b5744721ba87 | tickbox | Pre-pour inspection
| signoff | AUTHORITY HOLDPOINT
| section | 3.0 Concrete
| checkpoint | 3.1 - Concrete supply and placement
5998fe3e-1d89-5b39-96f7-821e5983f252 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
61ef8983-c674-5021-b9f3-eaa0ceba665b | note | Acceptance criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
fefb6498-79b2-52fe-a0e0-104269bdf33a | note | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
2336ed73-b9a2-53c5-bf7c-f4324a43ff69 | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
5671376d-a708-5948-a42b-43b1a23f6a27 | note | – – – – – – – – – – – – – – – –
be560ed9-2dca-5241-8590-9c50f54058c2 | note | Concrete temp at discharge (°C) ¦¦ Max elapsed time (hours)
89e894c0-bb55-5376-ae7a-b6bc9e62f81f | note | – – – – – – – – – – – – – – – –
6efbc748-7c9a-5b16-8ec9-277d5035eb7b | note | 10-24 ¦¦ 2.00
6023461f-4bf6-53dc-8334-af79147382e7 | note | 24-27 ¦¦ 1.50
3a43a3a3-9970-52a6-b42b-b4aa47af7ac2 | note | 27-30 ¦¦ 1.00
74c91880-db00-5339-aeff-7935226f3ec0 | note | 30-32 ¦¦ 0.75
1ae9314c-21ee-507a-bae7-0ecffa99aabe | note | – – – – – – – – – – – – – – – –
46ad998e-fcbb-5106-a8bc-622f5bf82ab1 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
d5e49e5c-aaff-58c9-99a0-3a67b0cc7fbf | button | Acceptance | Yes,No,N/A
9c985240-1a18-5791-98b9-9b2de85fe2af | note | Key - S
f1585110-1107-52d6-801c-dee7eab9e559 | note | HPP CON Key - S
644dfbf6-a341-5eff-81c2-5958f7615578 | note | HPP QA Key - S
d870eef0-d089-51d5-a7f7-dc4217344aa8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ccb8e5cb-c65c-522b-a685-32deaa6a0715 | tickbox | Material dockets
| checkpoint | 3.2 - Concrete sampling
5b077a56-1d4a-5e3d-ada7-b7330ed3e63a | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
b4ab27ab-e9ae-5f7d-bb45-ae7185d5f4ea | note | Acceptance criteria - The nominal rate of sampling shall be taken:
2bf9c5cc-59ca-50ce-b933-7cc103da2380 | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
dd0ab810-db9d-596e-88e5-9bf5f3796e5e | note | (b) Slump: One per batch of concrete
809b1601-6719-5f21-bd54-408a0abd370a | note | ○ Average compressive strength at 28 days meets minimum design requirements. Slump within tolerances specified in AS 1379
781f7182-7c67-5855-aeb6-01f902c1578b | note | – – – – – – – – – – – – – – – –
ff290c48-15cc-56af-8b18-c271caa1dda5 | note | Specified Slump (mm) ¦¦ Tolerance (mm)
152db6dd-8973-5ba8-8a74-13d6fc702ba4 | note | – – – – – – – – – – – – – – – –
60055e76-7d67-5805-bdfb-15fc758075e2 | note | <60 ¦¦ ± 10
3e80c47a-e6c6-53d5-a0b2-1526fbbbd133 | note | ≥60 ≤80 ¦¦ ± 15
f12de317-4e5f-562c-87eb-cdd74e20b067 | note | >80 ≤110 ¦¦ ± 20
38d244ac-4896-584d-9085-3e02581f4c65 | note | >110 ≤150 ¦¦ ± 30
a4895b91-e502-55ff-9d5f-275288b23877 | note | >150 ¦¦ ± 40
dcd0f942-e87b-52c6-9431-ddb5d596961f | note | – – – – – – – – – – – – – – – –
cc72dc41-ddc7-51ee-b81e-60a85a0685b8 | button | Acceptance | Yes,No,N/A
4c8a0273-23e2-5768-990e-c38ad1de036c | note | Key - S
a5314a3f-f97e-5c62-8210-8479ae0386eb | note | HPP CON Key - S
0e874af5-e38c-54e1-aa06-03175b43148d | note | HPP QA Key - S
a00fb00c-ab00-5f89-81b2-358b42838d76 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
ab32d41e-ec99-59ed-9143-ae7937c43ee1 | tickbox | Material dockets
| section | 4.0 Conformance check
| checkpoint | 4.1 - Survey
5bf021cf-6837-58ef-bb7e-2f60e495f04b | note | Ref docs - Spec. 0003 Piling [3.10]
0e530ee7-b1da-557b-8a59-c36b9c613b33 | note | Acceptance criteria - All piles shall be constructed within the tolerance specified below:
9615617e-80f0-523c-a624-d9dd8029ea46 | note | ○ The centreline at the top of the piles shall be within 50mm of the specified position
c3dd1123-548a-5712-be1a-e5114450b7f7 | note | ○ The tolerance on the level of the top of the piles shall be ± 10mm
111ece0a-f8d3-57dd-9cca-cd7c860f9d73 | note | ○ Piles shall be constructed to the minimum diameters specified on the drawings
c22e7237-3a85-50f2-a7fb-b6ad50724dc8 | note | ○ Length of pile/pile liner shall not be less than total length shown on drawings
89c85987-f7c1-59a0-89c3-79a0be672d69 | note | ○ Review survey as build report.
a34c60d6-34f4-59bb-83d4-48a2bd0c6db2 | button | Acceptance | Yes,No,N/A
4afc44ee-2529-5e3b-89c9-61fe09904e19 | note | Key - S
0e64909c-6e92-53b3-87bb-e55d9752055a | note | HPP CON Key - R
39846905-212d-5584-b130-1cb998813b8c | note | HPP QA Key - R
3c25ca0a-0439-55ae-8023-2456569008e8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c6e76896-5998-5321-b09c-562b4caffc48 | tickbox | As-Built Surveys
| checkpoint | 4.2 - Concrete Test Results
e68dbd3f-38da-52e6-8ba6-5b30162311a5 | note | Ref docs - Spec. 0002 [Cl 8.2]
7390a9f1-479f-5c29-9b73-0104f6ca3056 | note | Acceptance criteria - Certificates received, reviewed and conforming to requirements for each pour.
43d21ece-2e4e-56d6-b559-27b580b38b68 | button | Acceptance | Yes,No,N/A
f70be150-cf06-54e3-ba94-a287eca22eed | note | Key - S
e315478f-6233-5323-9a60-1e2a7f7c5d60 | note | HPP CON Key - R
f21eb127-b727-5bf6-bbf2-fbb42b37baaf | note | HPP QA Key - R
d44f6980-a2c3-5a16-9ee9-55f421f30071 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2f33bc09-4182-5d0c-98be-4a85ba7b70e2 | tickbox | Test reports
| checkpoint | 4.3 - Acceptance and closure of non-conforming items
390b15b5-15f4-5c4d-9fbd-eb566756a1d0 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
c55a4c1e-b747-581f-90ae-cc570b10ab95 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
0502b9e5-e49f-592b-85ad-6eb4eb305e53 | note | HOLD POINT
1c257cef-2997-5ad0-9012-1219104976c4 | button | Acceptance | Yes,No,N/A
27ad7400-b4e6-5a6d-844a-126ef85e7f54 | note | Key - H
2ac740c0-9fa8-5e39-ac6c-ffd3c0ca7e85 | note | HPP CON Key - H
9f13406c-744d-546b-8a5a-1772ca0168dc | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-024 Pit Works Completion - Rev.1 | itp | INF-HSEQ CC0375-ITP-024 Pit Works Completion - Rev.1 |  | 9299f117-aea5-474d-8a01-74ccbaae6af6
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
e61ec239-8510-57e5-8992-dd3048295b6e | note | Ref docs - Issued drawings / Site copy drawings
55181d03-e94c-59bb-96e4-0db291eed78a | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
ed1856d2-cd89-594d-9080-24c142478f97 | button | Acceptance | Yes,No,N/A
9684aed2-1ac6-57ab-97d2-eece8586e134 | note | Key - S
6089f9a4-4f77-5766-b14b-6a52f1cfe4cd | note | HPP CON Key - S
06f3e7fd-0cde-5f77-85d3-7b66a7735d29 | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
45db2d01-0476-5249-9646-0facb254d64f | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
067ddfb4-a961-5660-98f8-dc2c7e5095f2 | note | Acceptance criteria - Prepare a lot map for traceability of the work area
c41f31fa-5bfd-5dc7-b13e-4b2f00ac7403 | button | Acceptance | Yes,No,N/A
d8fefdfd-9b05-596d-8676-febc2620f3be | note | Key - S
98873dd8-0397-5370-9644-843ca8105042 | note | HPP CON Key - S
477b0f5a-0b9f-50c9-9b34-3495df7155e8 | note | HPP QA Key - S
ef45c7d2-2339-509a-8c6d-fac12f1f7301 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a73ce992-ddd0-5dfc-aeeb-829936401382 | tickbox | Lot map
| checkpoint | 1.3 - Set out
8ec6cb18-8acd-5121-b264-771825158194 | note | Ref docs - Drawings
70962006-3e98-54b6-9e35-959b0bd81eba | note | Acceptance criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
112c0b17-54f9-5959-b8d7-2331058960a2 | button | Acceptance | Yes,No,N/A
89a280d8-1362-5386-9059-2fa58949e100 | note | Key - S
17339e9b-484d-5be9-b40d-c51cf2ea252b | note | HPP CON Key - S
cf51b3f5-ae9c-5ff5-85ba-a3d48dbf13b3 | note | HPP QA Key - S
| checkpoint | 1.4 - Pit Handover
f044fd67-833e-54d6-8171-35e24a195947 | note | Acceptance criteria - Each pit shall be visually inspected prior start of the completion works. Any defects recorded must be reported and rectified before receiving back the pit from HPP.
c2dc11e7-3fec-5b40-8fd4-77ca3234ed7b | button | Acceptance | Yes,No,N/A
791d1645-f70a-5e9e-8ed3-3ada10155587 | note | Key - H
a6baa41a-e393-554b-8803-8606c74b4341 | note | HPP CON Key - H
7cd3fe3d-1d1a-5350-953b-6b5e380b9439 | note | HPP QA Key - H
ec9bd782-64c9-56ff-984f-f99af20053ac | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bd8f6d18-792d-55ff-bf85-14b9b7a9a17d | tickbox | Joint inspection with HPP rep
| signoff | AUTHORITY HOLDPOINT
| section | 2.0 Pit Completion Works
| checkpoint | 2.1 - Pit Lid Installation
abd0ef4b-dbb8-5208-9f7c-08e1f091c6fb | note | Ref docs - Drawings
e2032b54-0666-5cae-8e7c-18d706b60317 | note | Acceptance criteria - Pits Lids to be installed as per drawings and manufacturers specifications utilising certified lifting points.
4925e610-26c9-566e-afa8-5f47838b1fa2 | button | Acceptance | Yes,No,N/A
74b4a2b6-fb8c-5e0a-8d6e-d02a4f70e7d5 | note | Key - S
322d5375-b51a-5c2e-85e7-530fe48f9ea9 | note | HPP CON Key - S
704286ee-96be-5b54-9def-1b175c0af115 | note | HPP QA Key - S
| checkpoint | 2.2 - Access Covers & Grates
18e1d97c-3992-5b86-a12e-7fdfc0d436a4 | note | Ref docs - Drawings
21f8b887-65fd-5ded-a2cc-a269d15a08e4 | note | Acceptance criteria - Access covers, grates and frames to be installed as per the drawings AS 3996
528bc8da-86e8-54fc-a712-384026b99043 | button | Acceptance | Yes,No,N/A
09efdcdc-eab1-5483-936c-9c0983c2c780 | note | Key - S
57137039-9949-500a-9529-e1915f9101b0 | note | HPP CON Key - S
358a1700-a7ee-5e98-a1b9-88b9f4bd9a1e | note | HPP QA Key - S
| checkpoint | 2.3 - Step Irons
1fb84644-c189-59ff-b767-ce198566eb13 | note | Ref docs - Drawings
6214f175-073f-51d6-b7c1-f952b3dfd7f6 | note | Acceptance criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
6fc41aca-3238-5c1f-a590-a2ea53277c37 | button | Acceptance | Yes,No,N/A
ce723ef7-c0e3-5810-8b42-c3ae352b01be | note | Key - S
3b2e50f3-6d62-5921-960b-94b394503ff4 | note | HPP CON Key - S
7d7a8dca-d691-53dc-a03e-b59bdbdd98be | note | HPP QA Key - S
| checkpoint | 2.4 - Pit Jointing (if applicable)
283fcc88-7339-558c-96d1-4fc0b18b28a5 | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
1569402b-9d47-5258-b51f-403a615bf110 | note | Acceptance criteria - Internal joints between precast pits and riser units to be waterproofed as per Symal RFI-037 & manufacturer recommendations.
5e9e13a9-b9fb-5005-94ac-59278885253f | note | ○ External Joints between pits and abutting concrete pavement, kerb or structures to be a 10mm isolation joint.
71779113-9d1b-5066-a3ec-e09880d1b1ad | button | Acceptance | Yes,No,N/A
b0347bb7-6504-5add-9b83-0ac413af1f6f | note | Key - S
6cebeb2a-7037-5d2a-a983-9195d9477b7a | note | HPP CON Key - S
22295906-6b26-590b-9d7f-82d4adcae0c9 | note | HPP QA Key - S
| checkpoint | 2.5 - Brass Marker Plates
4c4eba4c-3157-57c5-af1f-3e1b26d67f74 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11] Drawings
1ab208ca-7298-5d1c-8f27-f6bd6954ce16 | note | Acceptance criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
47901522-0fb7-5305-8a76-e0e38106008a | button | Acceptance | Yes,No,N/A
cbf7d792-403a-5ebc-a0ad-ca1c3126c6d9 | note | Key - S
605d7ad5-fd0e-55a8-aae7-e2544e738d9f | note | HPP CON Key - S
df173096-0d8c-50a1-bd0e-7a564afcdf0b | note | HPP QA Key - S
| checkpoint | 2.6 - Cable Markers
5ed0c067-b8e0-59ed-b65f-07b555c473c3 | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.10]
b56769d5-14f2-551a-91cf-dfc24c784cd5 | note | Acceptance criteria - Install Concrete Cable markers on the surface of all underground cable joints, at every change in direction, and on straight runs at least every 30m.
73ac4fc6-ac91-5d3d-a3fe-3ef1a085c1e5 | note | ○ Markers to be a 400mm square and 100mm deep concrete block with a brass label attached. Label to identify conduit type and direction.
843b76ec-9ca5-53c5-9f90-4186e3ef63fb | button | Acceptance | Yes,No,N/A
bbc7edd2-2eef-5f44-b018-f7ab4665430c | note | Key - S
0e952a99-3b81-58d4-9585-c7a4b4d7bfd6 | note | HPP CON Key - S
8662dcf3-86a7-56a7-9bd1-0b72a037b1b2 | note | HPP QA Key - S
| section | 3.0 Conformance Check
| checkpoint | 3.1 - Survey Report
c2a71412-116d-5cf5-bb2c-9286ad436339 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
ec149948-100f-5a7f-9834-8afcd0d5682a | note | Acceptance criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
d660b14e-1587-5757-8112-2e22ac772606 | note | HOLD POINT
a89e3409-ba2f-5c30-bd06-f2008493d924 | button | Acceptance | Yes,No,N/A
2f3a6307-2dbf-5ee4-9f02-33471a9b5f51 | note | Key - H
f103582b-02be-5740-b75a-f9554541a3e3 | note | HPP CON Key - W
bc113066-15df-514b-b3ef-88791cf2b7c7 | note | HPP QA Key - S
800bb9b9-bd30-5113-af0b-1f9da1f3c7a2 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
885cd394-acf0-51f9-a392-0005efa9f5c1 | tickbox | Survey report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Acceptance and closure of non-conforming items
69d49436-69b0-58a0-9e23-ade7f3ab53b9 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
4d0a49af-b892-5b34-b4cf-1a21b3e1612a | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
1c99141d-39fb-5bf6-b79d-c0ac1f4ead9b | note | HOLD POINT
a30d12f0-917e-5081-a74a-ba88334e51bc | button | Acceptance | Yes,No,N/A
e6e76ae8-030a-5e45-9d11-4e56b021e05e | note | Key - H
e5d16bea-9de5-54cb-b1df-93521a518aee | note | HPP CON Key - H
750ebf31-0c0d-5e44-af8f-9b1262ea48ec | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-025 Minor Concrete Structures - Rev.1 | itp | INF-HSEQ CC0375-ITP-025 Minor Concrete Structures - Rev.1 |  | eea01001-2843-4222-bef2-d683c54be20c
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
feb83063-d007-5785-acca-f655b48360f4 | note | Ref docs - Issued drawings / Site copy drawings
22ba6558-8fab-5208-bd70-a886ed5298fe | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
5a089be4-3e04-5d75-bfc5-86fc172f20f7 | button | Acceptance | Yes,No,N/A
fcd248fe-a3aa-5adf-a35f-1fa0866a9f6a | note | Key - S
961b2730-dccf-5bdb-bd05-d1216407f029 | note | HPP CON Key - S
977b93f5-d57f-5ffe-b3fc-872b5ae4ecee | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
e0729e1e-7a25-5014-87cf-62f43d7c95e3 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
0daf60b3-0324-5fbf-8046-5864359202ea | note | Acceptance criteria - Prepare a lot map for traceability of the work area
534629ef-2fb6-51c2-8dfa-8c2775bf5b0c | button | Acceptance | Yes,No,N/A
96dc652c-119c-5c06-8d8c-8bcaa066459c | note | Key - S
43a8bf71-79bf-5be5-a588-a29de83a9712 | note | HPP CON Key - S
922d8903-2725-5069-8e0f-0ae0aacf8e60 | note | HPP QA Key - S
341daf6d-9cfa-56ce-8845-d2f844c37fec | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0d27a667-4e4d-57a4-b337-bd85810c481c | tickbox | Lot map
| checkpoint | 1.3 - Set out
0270cf6a-c5b9-54d9-bcf0-39de782bf147 | note | Ref docs - Drawings
879c9d00-06d4-5339-a623-cc651a265556 | note | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
73d67afa-f3ac-5b67-a906-8afbb2506b7d | button | Acceptance | Yes,No,N/A
5dfe9f5a-0b9d-5734-9650-1cbb57fe6382 | note | Key - S
5caa4bf1-1208-58a0-aa42-71f721243968 | note | HPP CON Key - S
b47bd726-a0c7-529a-a41f-3edadc3f4ea6 | note | HPP QA Key - S
| section | 2.0 Formworks and Rebar Reinforcements
| checkpoint | 2.1 - Blinding (if applicable)
7e94c9fe-a37e-5887-ae60-b0e62d187d56 | note | Ref docs - Drawings
da404add-d538-5067-9246-ab3590f064b0 | note | Acceptance criteria - Blinding (15MPa) for Reinforced Concrete Bases to be a 50mm thick mass concrete layer.
cff9b31e-2cce-53f5-b637-43e423a83929 | note | ○ Unreinforced bases can be poured directly on the earth
06ec8aeb-ad42-57da-8e6c-73807d17d9bd | button | Acceptance | Yes,No,N/A
c9d6da0a-fd9f-5581-b189-fb199f5478b4 | note | Key - S
2bdc7688-77b8-500a-9a77-fdb6bb90e2cb | note | HPP CON Key - S
3b8b3977-942c-56bc-b89e-de52f08e34d4 | note | HPP QA Key - S
| checkpoint | 2.2 - Formwork
d11f63a9-1a56-59b3-a129-96026faf8fce | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
3a2727f1-fe44-5dc2-a265-806d5f5142bf | note | Acceptance criteria - Formwork installed as per drawings and adequately supported.
a8ef8d17-5fc6-508d-93fd-55db484bf4ce | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
d74da0fc-4754-5644-b730-f4df8861032e | note | ○ Before Placing Concrete
f703b3fc-a897-5bed-a11a-aaa20542f5cb | button | Acceptance | Yes,No,N/A
6e8c0dcd-2d6d-5829-9d0b-4c2de3061f50 | note | Key - H
2d9f6f8f-18f6-5cb4-bfb8-121ad9aedd67 | note | HPP CON Key - S
294cad6f-420a-50c4-a22b-e0b9ac75ce39 | note | HPP QA Key - S
71e33aa5-ec01-5b70-b50d-924e9338c2df | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e055b57f-709b-5aad-85af-1470d072aa1e | tickbox | Pre-pour inspection
| checkpoint | 2.3 - Steel reinforcement
89134f9e-c6e9-5e89-9880-2dcfe109cae1 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5] Drawings
d98ca47f-a1eb-5818-9d51-29202df51fc1 | note | Acceptance criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
78b335ea-3586-5281-8aef-c4b7ee7b3c09 | note | ○ Concrete pre-pour inspection complete.
01714e08-76e1-5416-a872-ad40e04c68ca | note | ○ Before Placing Concrete
636558ae-2493-534a-a3a3-cd8c51054468 | button | Acceptance | Yes,No,N/A
d1b65d52-0431-57a6-b980-fe2119c6a7eb | note | Key - H
54812886-9421-5219-a9d5-772711e6c397 | note | HPP CON Key - S
ec2c85ec-8845-520e-8ae8-327ff6ededd9 | note | HPP QA Key - S
6fdfa308-42cb-58ac-97e9-1306a709649e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
2e3c4b2f-0a63-5374-aaeb-540f452abcba | tickbox | Pre-pour inspection
| section | 3.0 Concrete placement
| checkpoint | 3.1 - Concrete supply and placement
cf563543-aee5-5646-a4dd-e1133e0156a7 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
575f6b98-1d99-5230-9cea-c385ac6f9f54 | note | Acceptance criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
6e222c8f-04a5-5944-9874-854d7e7bd992 | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
3e569854-3409-5728-b29e-1451e0d30721 | note | – – – – – – – – – – – – – – – –
fd3a309f-b50c-52f0-9561-e152c96758dd | note | Concrete temperature at time of discharge (°C) ¦¦ Maximum elapsed time (hours)
fee6f33c-a106-5371-a2fb-ebb9a7d317df | note | – – – – – – – – – – – – – – – –
a26147c5-e3a0-5fea-a289-7369977b154a | note | 10 - 24 ¦¦ 2.00
906a09cf-d830-537b-8a39-2999dbddea81 | note | 24 - 27 ¦¦ 1.50
7aea69c7-88ad-5707-a010-5dead765299e | note | 27 - 30 ¦¦ 1.00
be33409e-a04d-5bff-a16a-625089d06878 | note | 30 - 32 ¦¦ 0.75
631d0b8b-2856-593a-be42-ac9d8e9486d8 | note | – – – – – – – – – – – – – – – –
47a3f0ac-7138-579d-b978-8944845697c8 | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
b1b8ec03-783d-5410-b47c-5006dd68ee52 | note | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
1f217e19-d400-5f5a-ba30-663b375aa5b6 | button | Acceptance | Yes,No,N/A
e3f05c74-7af5-5297-b99f-d624b9d2993c | note | Key - S
c8a9d54c-eb74-54a3-9e70-74fcace75755 | note | HPP CON Key - S
fce039e1-9a2b-5b5a-9c9a-0e5f4677723c | note | HPP QA Key - S
da41f85a-a311-5534-b53f-1a5829e85ea1 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
a5bf428f-2f10-5227-a3ef-6edc7cc0efb9 | tickbox | Delivery dockets
| checkpoint | 3.2 - Concrete sampling
4fcbd014-0c5c-5381-aeaa-c8c97db68dbf | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
24014a79-6508-58cf-8073-88b706b4d8a4 | note | Acceptance criteria - The nominal rate of sampling shall be taken:
932657f4-9d5d-56dc-b915-94765938920c | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
eaf879f9-5c4a-5b77-9483-6be5f5b226ba | note | (b) Slump: One per batch of concrete
488674d7-77ad-554d-931b-1c68c2ac2f87 | note | ○ Slump within tolerances specified in AS 1379
ae7f3f9a-285e-54a8-8b3c-8bf316f00bd8 | note | – – – – – – – – – – – – – – – –
a63d9f01-716b-56db-8b6d-9f4bcf4d99c9 | note | Specified Slump (mm) ¦¦ Tolerance (mm)
8a7542a8-72dc-5164-9d67-0f35e82e69ba | note | – – – – – – – – – – – – – – – –
79a50b89-ddf5-5435-8ba0-3d1ea3ec2fe5 | note | <60 ¦¦ ± 10
b6f75484-0df7-58b6-9ae0-2781a0506ef9 | note | ≥60 ≤80 ¦¦ ± 15
ba41a901-706b-575f-a89e-9c664e588509 | note | >80 ≤110 ¦¦ ± 20
2973129a-205a-508a-b17a-a28c438c033e | note | >110 ≤150 ¦¦ ± 30
af00b779-4758-5fa4-b9e1-d14a7d329c45 | note | >150 ¦¦ ± 40
c483c167-27ba-5a5c-97a6-f5f0df11ec56 | note | – – – – – – – – – – – – – – – –
5d882c4c-7512-5b8a-a8e4-da1048e9212e | note | ○ Testing to be in a NATA accredited test facility
28594937-5827-5598-84cf-60b19b578ee5 | button | Acceptance | Yes,No,N/A
36f1f7a9-dd15-5892-a2ea-0a24484a8dac | note | Key - S
d66e6719-402a-5101-bcc6-86cb9234219c | note | HPP CON Key - S
75060b6f-1bf8-570a-b6e2-2084f727ee62 | note | HPP QA Key - S
284bcf1e-9b8e-5081-975f-b4f0532c1839 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
19368854-b99b-5298-9771-13bf72a1d2f5 | tickbox | Concrete pour record
| checkpoint | 3.3 - Curing
54dbdd2c-f74b-562c-9c02-6fca35725f10 | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
091bb599-02b3-5171-b4dc-7179f74e2039 | note | Acceptance criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention until 15MPa is achieved unless directed otherwise by the superintendent
0570f58a-9c30-553c-9ab5-39f7b61aabab | button | Acceptance | Yes,No,N/A
1d307df6-8be3-5d53-a810-a701353a8f28 | note | Key - S
d1bd0d83-0fc4-521b-9f9a-19790a6863d3 | note | HPP CON Key - S
7f64c237-8c1f-5966-8f54-73cbdbb92187 | note | HPP QA Key - S
| checkpoint | 3.4 - Concrete testing
81ac62d3-ca1f-534b-b717-e6ddd2d79470 | note | Ref docs - Spec. 0002 [Cl 8.2]
2f9e5f2e-bcf7-5b71-8062-6518d02879e2 | note | Acceptance criteria - Certificates received, reviewed, and conforming to requirements for each pour. Average compressive strength at 28 days meets minimum design requirements
4810b884-e5c7-5650-8204-582900826d8a | button | Acceptance | Yes,No,N/A
251f0509-406f-5153-960e-ae6cace78775 | note | Key - R
b4d0c9ac-251b-5ad8-b4be-cafecfcdc4b3 | note | HPP CON Key - R
8e9a3435-c605-5301-899e-f8a8c2e8d264 | note | HPP QA Key - R
77013a07-7708-590c-8db4-f28a59d59c66 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
3610d6e0-94ee-5a13-9b5f-5ba660f9c379 | tickbox | Test reports
| section | 4.0 Conformance check
| checkpoint | 4.1 - Survey Report
dbbb4607-0810-5fb8-80a0-c589ef129e58 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
7f50b7e8-2fd7-508b-8f5d-ae818d1f3015 | note | Acceptance criteria - An as-built survey completed to ensure all structures are within construction tolerances.
5a94c1cf-f619-5c3f-aa1f-743353a8d6da | note | ○ Plan: +/- 30mm
eb21a335-21ed-52b4-8eb3-f02e8daae62a | note | ○ Level: +/ 10mm
8564ac19-458a-5b1e-b6f4-b39f07f5de11 | button | Acceptance | Yes,No,N/A
74408db2-7d17-551d-9052-5fd18a9e0092 | note | Key - R
495ffae5-506e-5200-8e03-46a64480cbc9 | note | HPP CON Key - R
1c3172cc-f527-5e68-aba3-a7e6c41113e2 | note | HPP QA Key - R
3773978c-0cf1-5009-9f27-7900d94525b8 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
db165f3f-7ba9-53bc-a1a4-bd86d0d018ff | tickbox | Survey report
| checkpoint | 4.2 - Acceptance and closure of non-conforming items
5a75c909-d3f8-507d-953b-0f5bb5915ebe | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
7b5e9eac-cfa8-5444-93ad-bf897eec30d9 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
e1d8e297-16e6-5015-9aff-b78dde63f1cb | note | HOLD POINT
d833087f-68de-54e7-840a-66a65cecb5d5 | button | Acceptance | Yes,No,N/A
8cc25cfc-8857-52f4-b5e1-d391d49e6d1f | note | Key - H
6cd7c2bc-4d6d-5cdf-bfc1-93923323f77b | note | HPP CON Key - H
406065fb-b936-5ce8-bdac-f26dd9b613d9 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-026 Sewerage System - Rev.2 | itp | INF-HSEQ CC0375-ITP-026 Sewerage System - Rev.2 |  | c91096fc-3d3f-4a60-9f47-6e6b4bf49f6e
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
d318873b-772b-53b7-b468-2f057978044c | note | Ref docs - Issued drawings / Site copy drawings
23b064a2-4a8a-55f1-93fb-80f4f44e63de | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
c8a32927-42a4-527f-9f44-6887ad9fdeee | button | Acceptance | Yes,No,N/A
9ca5e08f-ed1f-51fa-b942-dc2d220113a9 | note | Key - S
eacd6882-2296-5652-8d7d-8f1554fda228 | note | HPP CON Key - S
b1a0b1d3-28c6-5976-b290-16fc1af83d7d | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
fe772ea7-7089-5d83-969f-fbaf8d50277d | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
7d02bcd6-d22f-5255-84b6-9a029b3e8575 | note | Acceptance criteria - Prepare a lot map for traceability of the work area
c962412c-56a0-52ae-be8f-4c1d22098582 | button | Acceptance | Yes,No,N/A
b7fe1fae-718f-5c72-b52a-6f1a420df4b5 | note | Key - S
a097ee82-eaf9-540b-a6e4-47a288dfc36b | note | HPP CON Key - S
5d3cbc8d-56ac-5736-9b2d-a069aa385684 | note | HPP QA Key - S
254dc0e6-33c4-5a0d-aec2-88f6ebf581fa | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8bacdb08-b5d0-50e9-aec1-804bf44f31d4 | tickbox | Lot map
| checkpoint | 1.3 - Pipe Material
318056fd-402b-57c3-97e3-effc4955ee72 | note | Ref docs - Drawings
608f7654-35ad-5676-87fa-b92f86900361 | note | Acceptance criteria - Has the correct class & type of drainage pipe been supplied and free of defects?
05c63df6-3387-53ae-9f2a-25d25143a29a | button | Acceptance | Yes,No,N/A
59a70250-42c4-5522-85de-d4cc1c176d5d | note | Key - S
95acc737-fa75-5815-ab9e-c4b53d360881 | note | HPP CON Key - S
11a203bc-ea2f-5d75-9bf6-12579a7593da | note | HPP QA Key - S
94920af6-c398-54f6-afac-1425bf34f1bc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
dcf6ff3d-3617-5318-a9d4-8cff5318075e | tickbox | Material conformance certificate
| checkpoint | 1.4 - Underlying Lot Conformance
da84b6db-d8d7-55a4-9ba1-dc56bf6c23bb | note | Ref docs - Underlying Lot ITP
a0733bcd-287b-5c49-8fc1-d7c1967e826c | note | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
ad92cb47-2bfc-5120-8b7a-10b4994e1b3f | note | ○ Refer underlying lot ITP(s)
42e16908-3db5-5ae6-9ee8-007ecfb1c61e | button | Acceptance | Yes,No,N/A
8f5cb1a1-540b-5ed7-996b-f87d04c99663 | note | Key - S
38f205b1-4e45-51f4-9d52-e546344b5319 | note | HPP CON Key - S
b605438f-d793-515e-8105-8a717ffbee6c | note | HPP QA Key - S
| checkpoint | 1.5 - Embedment Material
efcdf72b-ff20-5670-aeb5-580f92f9a76f | note | Ref docs - ASNZS_3500.2-2021 Plumbing and drainage Part 2: [cl drainage 5.4.2]
5c4ba682-2652-5784-8678-bb9a9afc5ed1 | note | Acceptance criteria - Filling materials used for bedding of drains shall be one of the following:
1f1c0b47-1a29-55fa-a189-df0598d817f9 | note | (a) Gravel screenings or similar recycled materials of nominal size between 7mm and 10 mm.
0b0801bb-3f0c-5f54-bb41-2e416167531e | button | Acceptance | Yes,No,N/A
84e8f67c-ad98-5efe-b9f3-9823dfa81c97 | note | Key - S
0437771d-edd3-5184-9e1c-97fdf5ca0a94 | note | HPP CON Key - S
b779ed44-13f2-5ae3-af77-2c21425b99b0 | note | HPP QA Key - S
| checkpoint | 1.6 - Set out
efec8ef7-b8d7-514e-b5e7-bb052771c49b | note | Ref docs - Drawings
743fe11d-4ca0-554f-8a94-9a92cdb49044 | note | Acceptance criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
e91d3189-91d3-592e-9d73-af05399bbe43 | button | Acceptance | Yes,No,N/A
53c6b7c4-cb4f-5cbb-a7b0-91d2738c0aa9 | note | Key - S
4303276b-bf36-56e6-9a71-68528a662ab2 | note | HPP CON Key - S
1f1da650-5c6a-54c2-b07b-8be26939c29a | note | HPP QA Key - S
| section | 2.0 Excavation and Pipe Laying
| checkpoint | 2.1 - Excavation
e4c13e21-79a8-56e5-8527-e20a5ffecd3f | note | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 6.21 -GRADES 6.7 -Trenches.
8dbdef32-32cf-5269-b58b-874c60f87663 | note | ○ In Accordance with IFC Drawings
06477a34-f5b9-52d7-bf87-a381498043d8 | note | Acceptance criteria - All trenches shall be excavated as per Drawings otherwise directed by HPP.
5eec187f-e6d2-5d0f-82c5-305e6dbf9e0b | button | Acceptance | Yes,No,N/A
b97f84a9-2563-56f7-8a11-052290d4d4a3 | note | Key - S
84f2e5a8-5bef-515a-a8db-43efc8b3cdf4 | note | HPP CON Key - S
189e9d75-b2d9-566f-817c-517cff1ef8c2 | note | HPP QA Key - S
| checkpoint | 2.2 - Pipe Laying and Joint Fitting
172b5dd8-e803-52d4-a331-b3196ec20037 | note | Ref docs - Drawings Manufacturer Specifications
d78c6bd1-c181-5c97-acc4-105ac1faa2df | note | Acceptance criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
ca9ca808-3275-5259-ad20-6d1196f1d026 | note | HOLD POINT
3e22bbd8-f51f-53d7-a043-2bc68d06e305 | button | Acceptance | Yes,No,N/A
6a9efb97-eb92-5ad4-84c2-c3899c85d09e | note | Key - H
be568008-0046-503e-be12-091db87a2878 | note | HPP CON Key - H
de336025-9d44-540e-891b-0451de605355 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Encasement Backfill
6818cbad-4cec-5d0f-afc5-b23ea28eef70 | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
ba1c2842-a799-58fa-81ce-0bf4ed8e9405 | note | Acceptance criteria - DICL & Flexible Pipes:
aead749d-54bb-5992-b146-0a4e622a8b2b | note | – – – – – – – – – – – – – – – –
8b65a366-8da7-5c3c-84ca-cbe81ef66df6 | note | Table 5.2 Trench and embedment dimensions
352e208e-2531-5a35-ae91-f06af237a4da | note | Dia (De)mm ¦¦ Min. dimensions (mm): x ¦¦ Min. dimensions (mm): s ¦¦ Min. dimensions (mm): o ¦¦ Min. dimensions (mm): y
0c9fc663-23d1-5df7-ac3f-bcfac79dbe8f | note | – – – – – – – – – – – – – – – –
9e53e0e7-eb62-5446-b676-fec9fba9fe3d | note | ≥ 75 ≤ 150 ¦¦ 75 ¦¦ 100 ¦¦ 100 ¦¦ Pipe dia.
7e7cd6a3-4207-5933-90c8-d915b6b00584 | note | > 150 ≤ 300 ¦¦ 100 ¦¦ 150 ¦¦ 150 ¦¦ Pipe dia.
189e1f7e-9ef8-526f-87ef-b5c9b2d8753d | note | > 300 ≤ 450 ¦¦ 100 ¦¦ 200 ¦¦ 150 ¦¦ Pipe dia.
83ae4c9c-1e49-5d52-a244-70198131dbba | note | > 450 ≤ 900 ¦¦ 150 ¦¦ 300 ¦¦ 150 ¦¦ Pipe dia.
b4029580-1735-5dbe-9d2b-48af4326b164 | note | > 900 ≤ 1500 ¦¦ 150 ¦¦ 350 ¦¦ 200 ¦¦ Pipe dia.
d0676d43-990c-5545-a9de-3f95c0864f6f | note | – – – – – – – – – – – – – – – –
68999223-6bc4-583e-93c9-211c18f8ed3a | note | ○ Compacted with handheld equipment to point of refusal.
8ed1b0cf-9690-5293-9c20-c1914b903e72 | button | Acceptance | Yes,No,N/A
f36a420f-f993-536c-9c47-b0c0fcc4b81e | note | Key - S
da791f29-b147-5b29-bb5e-64ba6717826e | note | HPP CON Key - S
5d092438-2356-5524-828f-68cc226d965d | note | HPP QA Key - S
| checkpoint | 2.4 - Tank Installation (supplied by HPP)
caf59768-a360-54c5-a67a-e0c59c009815 | note | Ref docs - Drawings Manufacturer Specifications
6f5873cd-db96-5cbd-bdc0-aa7027e1920b | note | Acceptance criteria - Install as per manufacture specifications and HPP instruction.
62053d57-84c8-577a-8831-12f784d36c82 | note | HOLD POINT
f5ab1d14-708c-57c6-9ab1-3484c03db73a | button | Acceptance | Yes,No,N/A
ad0ee77e-a95c-57cd-9012-21ecc3dad3d3 | note | Key - H
9d681ac3-ca86-5180-a175-2e17b30cf772 | note | HPP CON Key - H
4605588c-ddcd-55f5-bf14-4ebe2780db9d | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 3.0 Filling and Compaction
| checkpoint | 3.1 - Obtain Certificate of Compliance
a91cf096-7981-5c56-957c-524100735f26 | note | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 Cl.10.3
2d9ef262-366a-5451-84bd-df0cf2694221 | note | Acceptance criteria - Certify on completion of each component or stage that the works comply with the requirements of the BCA certifier and/or other authorities. Department of Fair-Trading Inspection to Sewer Pipe.
0ba9970d-065a-5b14-a349-4dc3d57810f9 | note | HOLD POINT
fb52193d-c9b6-5a85-b1b3-2b0b7773e3fe | button | Acceptance | Yes,No,N/A
5d88efd0-6efc-5abf-aa61-7eb9a97a3ad8 | note | Key - H
1df9f7a5-13cc-535b-96f5-18292f16112c | note | HPP CON Key - H
ff8b3799-eb89-5499-b9b3-71afc3c8c5cf | note | HPP QA Key - H
1191b004-cf61-553f-adb7-004640698a39 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
e7f30eea-561e-5bb0-8201-1b59a6348a4c | tickbox | Certificate of Compliance
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Marker Tape
779da37f-0be6-55cf-b87d-f798e612fa45 | note | Ref docs - Design Drawings
d0a70fac-1bd4-5001-8e93-2caffbdb81c1 | note | Acceptance criteria - Detectable Marker Tape to be installed a minimum of 300mm above the pipe.
df4e3947-02cb-51f7-8b29-219347d52889 | button | Acceptance | Yes,No,N/A
22d78070-1a80-5fae-b43d-64b10a551d1e | note | Key - S
330f259f-17e3-5bb8-8fd7-2dcc949b9a81 | note | HPP CON Key - S
b7cbd315-cc6a-50b1-8160-ae8d9aca1c7e | note | HPP QA Key - S
| checkpoint | 3.3 - Backfill & Compaction above embedded Sewer Pipes
6269c452-b9aa-5e2a-86a8-a55170bdb5a3 | note | Ref docs - Earthworks (Roadways) Cl 4.13, 7.1 Spec. 1352 Pipe Drainage [Cl 5.4]
451ec9ca-733e-53be-998e-dfafd1757ebb | note | Acceptance criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be: -
b939550a-cdb3-5bad-8258-16002d7a4823 | note | ○ 92% for general fill areas
daa74bff-4177-587c-a3a1-5a8bcd50bd63 | note | ○ 95% for pit and conduit bedding
ef9a92cc-51cf-5f26-b8eb-86aaf19f7e43 | note | ○ 97% for select fill areas and sections of the trench above the overlay zone and within 1.5m of top of pavement.
a39f6d81-5cfd-5261-ab66-01dbb9e86cfe | note | – Layers not to exceed 150mm compacted thickness.
2e7c923a-7152-52b0-be4e-416823418579 | button | Acceptance | Yes,No,N/A
c2436528-9672-5d3f-a8cf-45f013ee0bdd | note | Key - S
c8b8121a-8695-569f-98e8-08a12dbe1e7f | note | HPP CON Key - S
fac9f9fb-b119-5251-bbd3-d9cc39fd50b9 | note | HPP QA Key - S
7a4f47e3-e579-5186-b4d0-ca3f79e48e18 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
c5f5af5c-5922-5134-967f-ca9fb8cb8903 | tickbox | Test reports
| section | 4.0 Conformance check
| checkpoint | 4.1 - Carry out CCTV Inspection
201af0bb-ee25-5fd0-b84d-d61b87f8186e | note | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 Cl.9.3
37cc6b34-7aee-55b5-bb9a-4b9a33264f9e | note | Acceptance criteria - Inspection of all in-ground drainage systems after installation and prior to practical completion.
5d3441b5-6a4c-5c2a-96b6-b43d33586665 | note | ○ All defects disclosed during the tests shall be remedied immediately and, if required fresh tests shall be carried out
2dcc0306-f4ab-52be-884e-bcb856d1ce7c | button | Acceptance | Yes,No,N/A
1bb45aae-5024-5e56-addb-6ec683b7ed9e | note | Key - R
6ac44af0-982b-5cb2-a686-40bf6a28dcf3 | note | HPP CON Key - R
19b38e6e-0b9b-540d-b519-4c972d432fe5 | note | HPP QA Key - R
15fe0ba4-924d-50c1-a208-aa43e77e01a6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
d25fc937-0d89-52b4-9949-6475dc65aa4c | tickbox | Inspection Report
| checkpoint | 4.2 - Hydrostatic Test
68fcfc14-ad53-594b-9825-2f68716e52a1 | note | Ref docs - ASNZS_3500.2-2021 Plumbing and drainage Part 2: [cl 15.2]
89d29826-ea76-580c-9389-2072818c7e73 | note | Acceptance criteria - The sanitary plumbing and sanitary drainage shall be filled with water:
73af3209-d2df-535b-9b24-03c9958fba10 | note | (a) for sanitary drainage, to a height of not less than 1 m above the soffit level at the highest point of the section being tested;
a0267675-9fc5-51f9-a528-a28774a1a297 | note | (b) for sanitary plumbing, to the spill level of the highest fixture or to the flood level of the lowest sanitary fixture, whichever is higher; and
680b7922-7419-5e8d-9ec7-338d69ca3dd4 | note | (c) in either case, not exceeding 3 m at the lowest point of the test section.
4d201958-5db6-5cc0-bd6d-7028ef80bf21 | note | ○ The pressure shall be maintained without leakage for at least 15 min. The source of any leak shall then be ascertained, and any defects repaired. The section under test shall then be retested.
8a98c42c-958c-582a-9c6e-d52e70d359f7 | button | Acceptance | Yes,No,N/A
83a421c6-58f5-5f49-bf33-981daac538c8 | note | Key - R
42cefe1e-01b1-518e-aef9-d07a6918aaf6 | note | HPP CON Key - R
0678190f-883a-5b96-ab7a-efa5f0ac84b8 | note | HPP QA Key - R
0db272c6-5a2b-5289-9645-87ab2b363b4d | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
7daf8cd3-f77b-5b4e-b105-f3f7766ce9ce | tickbox | Inspection Report
| checkpoint | 4.3 - Survey Report
622b34e8-da00-5c8d-a7b5-83edc5926c54 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
487f210a-eabf-5ea2-b6bb-5a37efd98961 | note | Acceptance criteria - An as-built survey of the drainage system been completed to ensure all pipes are within construction tolerances.
6d859ccc-19ec-5821-be4d-050f1492411c | note | ○ Plan: +/- 200mm
9969014c-3952-5d44-99c3-82399d79baa8 | note | ○ Level: +/- 20mm
9da1059f-a3ed-5922-b7f0-62a19ea5aef3 | button | Acceptance | Yes,No,N/A
98595353-9de0-5745-a0d7-62c69179b8c2 | note | Key - R
2b5bcf38-9c3f-5f21-a379-b289dfdad9b3 | note | HPP CON Key - R
bb9a232e-924e-5153-a9f2-1877b87caee2 | note | HPP QA Key - R
ed024ab3-c2ac-5f57-b6e2-121366211171 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
21871f84-0834-5170-a52b-1434391bf75f | tickbox | Survey report
| checkpoint | 4.4 - Acceptance and closure of non-conforming items
69a93215-ef70-5f3b-b9cb-16ab89ccef21 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
49de2170-5068-55c8-b7a2-2e65f56e6945 | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
3ffdf23a-1b6e-53c9-ac82-99db508adb9e | note | HOLD POINT
6eebec61-c6f2-59fb-9829-a1ddbf65ae69 | button | Acceptance | Yes,No,N/A
51589217-bc6b-506a-8796-38b08c747a3d | note | Key - H
e442992e-0cfe-5b1e-8b97-3095c13a00b7 | note | HPP CON Key - H
b76d0b8f-35d3-5a7a-bce2-bf0290c5e196 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-027 Guardrail and Fence - Rev.1 | itp | INF-HSEQ CC0375-ITP-027 Guardrail and Fence - Rev.1 |  | d845b96a-d7fb-4e97-8ce3-59dbc94bb117
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
e39cf4ac-600e-598e-867b-899eb1dde377 | note | Ref docs - Issued drawings / Site copy drawings
647090de-0eb3-5325-98f9-83bb6134cbb5 | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
dd756a1b-1345-5e4a-869b-a16bc49fbc6d | button | Acceptance | Yes,No,N/A
fe859caa-80c2-562a-a8a7-38c69c9a08af | note | Key - S
a4a3679a-9f91-5b30-8dd7-dbe42cebdda8 | note | HPP CON Key - S
6505bc55-d980-5fbc-8c8f-d41f13afa4fc | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
b246b63a-829b-5b98-a260-cc29724964c1 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
bdb6c160-0efc-5e67-8f54-debcba4082e6 | note | Acceptance criteria - Prepare a lot map for traceability of the work area
f2d72e19-f40a-568e-a9d8-1a39551cf8d1 | button | Acceptance | Yes,No,N/A
3731d815-c1c8-5625-8c8b-74ca65a9cabe | note | Key - S
12d8b525-f150-5cec-a30a-bfa311bbe3e0 | note | HPP CON Key - S
c66bb236-a965-5eb8-8824-9343aa7d868a | note | HPP QA Key - S
77657394-f9c4-5889-a5ff-c0229b5170d0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
46871d28-3a73-5900-ae0e-44d210d29e7c | tickbox | Lot map
| checkpoint | 1.3 - Material
898b7585-1402-5173-a9c3-7c651054d764 | note | Ref docs - Drawings
10df8617-e42e-597e-bc7e-286847de3aa0 | note | Acceptance criteria - Correct class & type of rail or fence been supplied and free of defects
51d78501-1bc1-54f4-8f56-e9d336f37503 | button | Acceptance | Yes,No,N/A
63f6dac3-192e-50ca-a632-036f04f17242 | note | Key - S
41471d82-5c9f-51a2-9d85-0c42e596df58 | note | HPP CON Key - S
fd9ecffb-c0e9-5d32-b077-9ab0bef83d01 | note | HPP QA Key - S
| checkpoint | 1.4 - Underlying Lot Conformance
6761d2df-ba7e-5923-832d-92eefd302d9f | note | Ref docs - Underlying Lot ITP
33b45e45-2b9a-5e6f-959d-feecd48b0675 | note | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
78774b56-4b4d-5fac-95a1-64dd825ccbe4 | note | ○ Refer underlying lot ITP(s)
e1d2a738-02a1-5128-ad15-962eccb0a62a | button | Acceptance | Yes,No,N/A
1360681f-4ecf-57e5-9da1-d7dc8992f2d2 | note | Key - S
1563d245-ba2b-5bf2-871e-3f951bea55e8 | note | HPP CON Key - S
e6dd3045-e953-50d4-ad4c-309dbc0226f9 | note | HPP QA Key - S
| checkpoint | 1.5 - Set out
3d58dda5-7433-5834-af02-909cb5bd790a | note | Ref docs - Drawings
091507a8-1646-5b8b-af71-7b38cf594763 | note | Acceptance criteria - Setout rail positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
009d1044-a483-5af2-a41d-5f110aa5597b | button | Acceptance | Yes,No,N/A
af018da9-e54a-5eb9-88ae-93c4d4780aff | note | Key - S
bde0a0dd-c86d-5d57-afc3-287ddddbadac | note | HPP CON Key - S
b3dc19c5-0834-5bc4-b9d4-0e5f433c90af | note | HPP QA Key - S
| checkpoint | 1.6 - Site checklist
| section | 2.0 Installation
| checkpoint | 2.1 - Location and length
a7872145-bce1-55ba-ab54-57517f1ded9b | note | Ref docs - Construction drawings
0c16aae9-1136-516a-9e6b-087cd3f6d8a4 | note | Acceptance criteria - Length and location confirmed by the Superintendent
15608712-d33d-535b-b279-5fc246538889 | button | Acceptance | Yes,No,N/A
23e8f158-0b82-552c-b756-dbc00e5fd3cf | note | Key - S
cb5a8941-0660-54f7-9414-9960d2846636 | note | HPP CON Key - S
a587a30c-328e-5d66-8471-fa5e62337ac0 | note | HPP QA Key - S
| checkpoint | 2.2 - Install
fd98dc6c-4863-5365-9cb2-7b83484de240 | note | Ref docs - Construction drawings
04f31ddc-a59b-5e17-ace7-b76d43c848d0 | note | Acceptance criteria - Guard rail or fence run been installed as per the relevant specifications and drawings
0034e818-a868-5589-a985-9c3682724de7 | button | Acceptance | Yes,No,N/A
8d91c1c5-c22b-5819-a70c-a19bc83735a5 | note | Key - S
f73ce631-68bd-50d6-be29-27ded1aec019 | note | HPP CON Key - S
44870a4e-c98d-5310-83b0-f6986b9214fe | note | HPP QA Key - S
| section | 3.0 Conformance check
| checkpoint | 3.1 - Survey Report
06bfc395-210e-5f71-bbc9-7319bdeb1a27 | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
fd78cf43-4295-5a79-8db7-7d589c049377 | note | Acceptance criteria - +/- 25mm Specified Level
3411d47e-12d6-5e67-b3d0-f7dca1199401 | note | ○ +/- 50mm Specified Line
91f71439-552e-55c3-aac3-f8608bc955e2 | note | ○ Notwithstanding above specs, line and level of guard fence shall be adjusted where necessary to provide a smooth and even vertical and horizontal alignment
3fbc4920-a902-58b9-9099-e8d0837d4820 | button | Acceptance | Yes,No,N/A
954add99-dd72-5bf8-9580-44798824e93d | note | Key - R
7c32eba6-a85a-5126-8505-2cfdbb43683b | note | HPP CON Key - R
4d4dfa2c-2f04-5427-9718-f74bb6347f22 | note | HPP QA Key - R
00551019-9922-53c0-98eb-e8ece8281f98 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
0414f6fe-3186-57f3-a35f-1d143809f1f3 | tickbox | Survey report
| checkpoint | 3.2 - Acceptance and closure of non-conforming items
4ce20cbf-2afe-56d3-962a-f4c357a8f0d0 | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
85793979-bd01-5f11-860a-48460cb9a06d | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
9071698b-5397-5c0b-bfab-65cc5077418c | note | HOLD POINT
74d27bb0-5b22-5793-ad20-7a8b471979c9 | button | Acceptance | Yes,No,N/A
132448f8-2cd1-584d-adcc-bea0e00c3929 | note | Key - H
b3ea1790-a3a8-5a24-987c-17b60eaf2934 | note | HPP CON Key - H
86d79593-66fa-57b7-b3c6-af4b0cb94185 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checklist | INF-HSEQ CC0375-ITP-028 Spray Seal - Rev.1 | itp | INF-HSEQ CC0375-ITP-028 Spray Seal - Rev.1 |  | 0ee8a0fb-133f-4c26-b28c-f04dd1183dca
| section | 1.0 Preliminaries
| checkpoint | 1.1 - Documentation
857810bd-4238-52c9-9c19-85599628e22c | note | Ref docs - Issued drawings / Site copy drawings
445d60e6-4f13-54f1-b83f-1c4ce7421116 | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
c1666034-c6f2-5670-b513-9b7393031b35 | button | Acceptance | Yes,No,N/A
7cddbfa3-637c-56e1-a8b9-cd91c2005e62 | note | Key - S
0c7dcdde-e539-561a-8e06-971d933ae86f | note | HPP CON Key - S
bac45aac-3028-534b-be49-6ce10bf50d1a | note | HPP QA Key - S
| checkpoint | 1.2 - Lot Traceability
0ffaf5a9-1555-5a34-8e04-aa24409139d9 | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
ddc87642-c21d-5a47-b99f-e91f3c5df212 | note | Acceptance criteria - Prepare a lot map for traceability of the work area
0e0ca5ca-a585-583e-8387-8afa792ab18f | button | Acceptance | Yes,No,N/A
181df335-d14c-5b97-8692-e2440e5a9e4d | note | Key - S
cbf0bfb5-b5ab-5a56-a342-d371aba3e63a | note | HPP CON Key - S
b565139e-2325-5e23-8454-152e40c7ac21 | note | HPP QA Key - S
a1271aba-fce1-56c3-a71b-9d04f5a12113 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
8fba525a-3923-5684-a9dc-0dfc97c9a549 | tickbox | Lot map
| checkpoint | 1.3 - Material
665755ef-7c16-5b74-87a0-63d45bb7085a | note | Ref docs - TfNSW 3151, 3252,3253, 3258, 3259, ,3268, 3269
953dd4a7-8db1-56d7-a7bf-bacb3a83a15e | note | Acceptance criteria - Correct class & type been supplied and free of contaminations.
acaa9180-623d-5c5c-8649-255ec9efcdcc | button | Acceptance | Yes,No,N/A
b5079435-c3e0-5886-9ecb-9a0e0462ffc0 | note | Key - S
ed7b3762-84e2-57b4-96cb-420e44de0df4 | note | HPP CON Key - S
aca0bb03-7c90-5db5-851b-cd12ba43b2fc | note | HPP QA Key - S
c66681b9-5c19-51e6-9ad0-336504c056f0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
37c3bd74-dd73-514d-a504-339e81cc66f2 | tickbox | Material Test Report
| checkpoint | 1.4 - Underlying Lot Conformance
28d77c5a-2f6a-51f9-8a56-70fc83d18f96 | note | Ref docs - Underlying Lot ITP
9c6b494b-0d4c-5de4-9b8c-02278b5ad036 | note | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
fb3753a8-f644-5013-971a-f0e8b52858f3 | note | ○ Refer underlying lot ITP(s)
0303eae6-e3e6-552e-af25-dfb1d3007ff3 | button | Acceptance | Yes,No,N/A
58c45de9-bf6b-58a5-987e-d6cf755a588f | note | Key - S
3b66ba08-c059-57a3-abee-ba67593d5fea | note | HPP CON Key - S
b83bbf2d-6347-51cf-be18-33c31fa8c884 | note | HPP QA Key - S
| checkpoint | 1.5 - Set out
208136cf-019e-5dda-aef9-517c4d3dcff9 | note | Ref docs - Drawings
6c9f041c-17a9-5d24-a65d-bc16bf2446f1 | note | Acceptance criteria - Setout to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
1c1b9211-b321-544d-9b93-dc9100a8265d | button | Acceptance | Yes,No,N/A
b9032774-4a01-553d-8a6f-890952fc5d16 | note | Key - S
6295fcb9-b0fc-54a0-a200-b6268c6ae70d | note | HPP CON Key - S
abc41b76-dd22-51f9-9d81-cdfe1893809c | note | HPP QA Key - S
| checkpoint | 1.6 - Nominated Application Rates
1b6bf8be-875b-554e-abf1-3c45a2cb4ee9 | note | Ref docs - TfNSW R106.3 & R107.3, 5.4
cb245bc6-7ca0-5d0e-ad0e-c75ace48bf44 | note | Acceptance criteria - 1. Selection of Spray Seal Types and Binder Types - TfNSW R106 Annexure R106/L & R107 Annexure R107/L specifies Seal and Binder Types
61dde5f1-6fd3-530a-91c1-8fce678a0f4c | note | 2. Submission of Nominated Application Rates for each Segment.
e769bdd6-d7db-5bda-9b3a-ecc061e7abd2 | note | (Hold Points)
5e791dd0-bd6f-5098-98c0-9e0118409d17 | button | Acceptance | Yes,No,N/A
e53d92fc-8839-58ac-90bd-0dc67ad327b2 | textbox | Acceptance: |  |  | litres/m2
5bc5ac5a-8afd-5525-bb8f-fcd7a1da485e | note | Key - H
f04138d6-893f-5ea2-82d7-59d628a504b5 | note | HPP CON Key - H
d850d93c-47f3-5454-b64c-72a0738c928f | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.7 - Bitumen Sprayer Certification
5e41431e-ebc5-580d-b45d-f5866bb3c370 | note | Ref docs - TfNSW 106 6.1& 6.2 & TfNSW R107.6.1 & 6.2
82f49d64-4deb-5b72-bd0d-9cbadf9c6f1e | note | Acceptance criteria - Current Sprayer Certificate
4fbbb0ea-48d7-5b0a-b4c9-5d872d17dae9 | button | Acceptance | Yes,No,N/A
833401d9-e91b-5f8c-bfb5-43b0ea2dd923 | note | Key - R
346aebbd-554f-58f1-aa99-f63d37fcc8a6 | note | HPP CON Key - R
308450ad-91fa-5c77-9747-bc12e1d2dd02 | note | HPP QA Key - R
64837f47-2498-5b3c-ae25-5b9c3136eb3e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate (within 12 Months of Test)
| section | 2.0 Application of Spray Seal
| checkpoint | 2.1 - Pavement Temperature & Weather Conditions
26f71525-4a3f-5d1e-bf64-2578384d3283 | note | Ref docs - TfNSW R106 5.3 & TfNSW107.5.3
b3c93b85-63ab-5b53-a8b5-931631b959b1 | note | Acceptance criteria - Prior to Commencing and throughout Operations. Spraying shall be undertaken only if the pavement > 10oC for at least 1 hour and > 20oC for at least 1 hour for PMB
f4782ac1-a54b-550d-afd8-91ef3c99ccb8 | textbox | Acceptance (air): |  |  | °C
a530a1b5-c14f-5a54-9cd0-db4aeb51fb39 | textbox | Acceptance (pavement): |  |  | °C
508f1480-5769-5066-add7-beda65f9e563 | note | Key - S
bf336710-364b-538c-80da-76833691dce8 | note | HPP CON Key - S
e7fe5555-16f7-5b9c-94fd-0b76b0a6de6d | note | HPP QA Key - S
491c7282-ce5a-528a-8f65-9cbe10a38d8f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Monitor -Thermometer
| checkpoint | 2.2 - Preparation of Pavement Surface
b1338275-b646-55c6-b108-9351922fa7d2 | note | Ref docs - TfNSW R106 & TfNSW R107
5873a8c6-3160-574a-93ca-b375e45f44bb | note | Acceptance criteria - Surface visual inspection by Superintendent as per job specific requirements prior to operations.
74e4bd23-6451-5794-8acb-ff85f231f8d2 | note | ○ Ensure protection of existing services & fixtures Prior to Commencing Sprayed Bituminous Surfacing
53bac230-12ae-5f45-b420-e6a100a7609d | note | ○ Sweep surface with rotary broom 300mm beyond edge of seal
aaa994f1-0440-50c2-8f46-aae4f10185b7 | button | Acceptance | Yes,No,N/A
e766226d-574f-5a55-9918-260824158284 | note | Key - S
3b951476-ff36-5cc5-ac17-84c5b9b183a7 | note | HPP CON Key - S
ffc0d60c-b3d0-5904-89c7-5b5b9b0e13a8 | note | HPP QA Key - S
| checkpoint | 2.3 - Preparation of Binder - Incorporation of Cutter, Flux, Adhesion Agent
6716256e-d8f8-5445-8ed4-737edd8b2607 | note | Ref docs - TfNSW R106 6.7 & TfNSW R107.6.7
a573ec44-15c2-5fc9-840a-8033ab05cf6e | note | Acceptance criteria - Prior to each spraying surface, check Bitumen to cutter and circulate for 700 L/min for 20 minutes. For PMB circulate at 700l/min for 15 minutes.
7c4f9d93-cddc-54dd-b7f2-265523a5e9f8 | button | Acceptance | Yes,No,N/A
848ee708-ead4-5606-9913-fe0660056163 | note | Key - S
aab41af6-4222-552c-a68c-79f8e0be629d | note | HPP CON Key - S
f9d354df-0b76-5d7c-997f-af6498cf364d | note | HPP QA Key - S
| checkpoint | 2.4 - Binder Temperatures (for Spraying)
fd870537-8397-56a3-bf28-d9b3aa58d813 | note | Ref docs - TfNSW R106.6.6
963fd7ff-7c0e-5df6-a93b-dc0732ed6a67 | note | Acceptance criteria - Bitumen must be within the temperature range shown in Table R106.2 when cutter oil is incorporated
98eed96e-ee16-5bb6-aacd-fba5d6a59ef3 | note | – – – – – – – – – – – – – – – –
6b0c9b72-d928-5121-a1eb-e1ed852a79b3 | note | Table R106.2 - Bitumen Temperature
f60a2e18-29c3-5a0c-b9df-8a5408328945 | note | Class ¦¦ Temperature Range (°C)
5e93f5e4-4c64-581e-8ed0-482861b84b7a | note | – – – – – – – – – – – – – – – –
30df5ad6-d08b-5f7d-bbd3-7c71e079ef98 | note | 170, Multigrade 600/170 ¦¦ 160 - 190
70cd69de-0ea7-568a-b2af-5b9b1bcdb3a7 | note | 320 ¦¦ 170 - 200
a5333459-2a90-5190-90b8-1ffbf475528a | note | – – – – – – – – – – – – – – – –
404d3015-f6af-53b6-ba3c-332a9b1bd2d0 | note | ○ Cutback bitumen must be within the temperature range shown in Table R106.3 at the time of spraying.
8575a743-36db-5abe-b807-1d8efe931e86 | note | – – – – – – – – – – – – – – – –
7654dd82-ab74-5773-adff-f400279fcf1f | note | Table R106.3 - Cutback Bitumen Spraying Temperatures
161634fa-9c57-5fcd-88ea-b9008114ab7c | note | Grade ¦¦ Equivalent Cutter (%) ¦¦ Temperature Range (°C)
dbb13a23-bc87-5ffc-8b0e-dad18414c8a6 | note | – – – – – – – – – – – – – – – –
7a89150a-1f93-5aeb-bce2-22894f5c86d3 | note | AMC00 ¦¦ 56 ¦¦ 10 - 30
10badf10-452e-5daf-8c62-8699157c85cb | note | AMC0 ¦¦ 44 ¦¦ 35 - 55
ceb7febf-4ae7-57cc-9917-2d1745d51d4c | note | AMC1 ¦¦ 34 ¦¦ 60 - 80
c171da6d-85be-5907-8179-bcf827377545 | note | AMC2 ¦¦ 27 ¦¦ 75 - 100
28f62305-97c7-5414-a59b-87d597368df4 | note | AMC3 ¦¦ 21 ¦¦ 95 - 115
57c53251-3787-5cf0-9a5b-a201edb73b6e | note | AMC4 ¦¦ 16 ¦¦ 110 - 135
348ae28c-2eb6-515c-882b-3a490e7f7a7d | note | AMC5 ¦¦ 11 ¦¦ 120 - 150
03eefdad-c8aa-5d79-8db2-b43f53d2d200 | note | AMC6 ¦¦ 7 ¦¦ 120 - 150
96b0b4bb-e2d3-5e9d-956f-8bcf2e0cc8b5 | note | AMC7 ¦¦ 3 ¦¦ 150 - 175
9f3857d7-2d43-5dec-94ce-c03ff994d3c7 | note | FC2 ¦¦ 25 ¦¦ 70 - 95
fff56f97-bc06-54dd-8553-e1c88ff7a925 | note | FC3 ¦¦ 20 ¦¦ 80 - 95
1dd6577c-74fb-5a70-998f-b4c56e8cfae7 | note | FC4 ¦¦ 15 ¦¦ 95 - 110
18760362-f27e-5d43-aac3-88c500c02910 | note | FC5 ¦¦ 10 ¦¦ 120 - 140
f60c603c-20e5-5a23-b839-1c94103d0b6f | note | FC6 ¦¦ 7 ¦¦ 130 - 150
d08b8f9e-10ed-5fa1-a1f4-25ed5cce6284 | note | FC7 ¦¦ 3 ¦¦ 140 - 160
6d1ddac5-7b3f-5f75-8ced-ee1ba56f5705 | note | – – – – – – – – – – – – – – – –
7f02d38f-6b7f-532c-b4ec-d5d09151d6fc | button | Acceptance | Yes,No,N/A
2242d230-b19a-5480-a99b-6466e691394e | note | Key - S
6585d675-7440-564f-94be-55a383ffe5b5 | note | HPP CON Key - S
4e9fa34b-d3e9-58f5-88f0-e3648f75ad57 | note | HPP QA Key - S
5bcaf03f-9aea-58d9-a5a3-8eb68f68efd9 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Monitor -Thermometer
| checkpoint | 2.5 - Binder application and aggregate
b03f92c4-49ca-55ae-8dee-0e554b43f227 | note | Ref docs - TfNSW R106 7.0 & TfNSW R107.7.0
1282e657-f987-58dd-a0d1-1c3d37b5b20b | note | Acceptance criteria - ○ Period between application Seal over Prime/Primeseal
4ff78d82-1e2a-518c-b1d1-71857b85b960 | note | – Apply - Seal > 48 hours after Prime
e386909f-25d2-5208-b806-bc080c298161 | note | – Seal > 12 months after Primerseal
b3f2f91e-18fc-56ce-9c6d-3e9ec0669b5c | note | ○ Application Rate of Binder
6a6d1377-b43e-56f3-9ace-6b07740af312 | note | – Binder + / - 5% of Target Application Rate
b21cd238-7110-5e8e-853b-39f5ab73ef2b | note | ○ Spread Rate of Aggregate
2fb81f62-00ad-515c-8daa-fde2d0a2104e | note | – Target Spread Rate
6369cfcd-78f6-5e1e-97ac-bed41d1895af | button | Acceptance | Yes,No,N/A
44e4c7d0-177f-5f40-b8f5-226e637a14f1 | note | Key - S
6559c9b4-fa74-52af-b3f3-65daf9a050f2 | note | HPP CON Key - S
03dc6cd0-30ec-51d6-b516-d96cef8f503e | note | HPP QA Key - S
| checkpoint | 2.6 - Rolling of Sprayed Sealing
e76f8e33-ae9c-5d2f-a6a2-12ffe66542f1 | note | Acceptance criteria - Initial Rolling shall be carried out by 2 or more multi tyred rollers (mass min 1 tonne per wheel, tyre pressures 550kPa) until agg embedded, backrolling at 1 hr per 1,500m2 for > 500 V.L.D. and 1 hr per 1,000m2 for < 500 V.L.D. (for 1 multi tyred roller)
dcd1c753-11f9-52dc-9313-a56b051902bd | button | Acceptance | Yes,No,N/A
021fe294-c7c6-5c86-b98f-515b24d9134f | note | Key - S
190473d0-f218-5a88-b294-7ef42a1ef6e0 | note | HPP CON Key - S
56226a91-14ad-52f0-90b0-c2e4f84d7f47 | note | HPP QA Key - S
| checkpoint | 2.7 - Sweeping of Sprayed Seal (if required)
3713893e-c8f1-5345-8f5b-badb2656f25a | note | Ref docs - TfNSW T277
e26f4a18-f047-5afd-a525-570388f123de | note | Acceptance criteria - All Loose Stone to be removed, as a minimum the final sweep shall be with a suction broom as long as the suction broom does not damage the fresh seal.
d294ff9a-d9fd-5c40-868a-60d1a0b83a8f | note | ○ Measurement of loose aggregate for 10 & 14mm seals after sweeping operation.
ba32ca17-6da0-57e1-a629-048c6cffa364 | note | ○ Urban areas = 20 particles/m2: Medium - High areas = 30 particles/m2: Low traffic areas = 40 particles/m2
638416c8-4de3-5eae-a76d-a9b2b13e530b | button | Acceptance | Yes,No,N/A
3f0b0b61-b4d7-548c-87d0-348d6141107d | note | Key - S
f9227f96-22e8-5bb5-a684-c851632464d3 | note | HPP CON Key - S
b121c7d6-6f33-5330-8934-0560de442a55 | note | HPP QA Key - S
| section | 3.0 Conformance check
| checkpoint | 3.1 - Acceptance and closure of non-conforming items
747760d0-44bb-52c9-ba2f-674bb599221f | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
c568bac1-7109-599d-8582-4f867ddd993a | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
42725c87-0023-56ea-a35d-259649899608 | note | HOLD POINT
951272f8-a683-5d26-9000-6c9c6eceec35 | button | Acceptance | Yes,No,N/A
ae3c002d-bcc2-5327-87ee-56749499a00b | note | Key - H
1aa2fff8-fa62-5927-9421-b7a976abafb0 | note | HPP CON Key - H
8989c414-33a1-59a3-8586-edaffddef876 | note | HPP QA Key - H
| signoff | AUTHORITY HOLDPOINT