## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | ITP - Fall Protection Fencing - 304 - Rev B | itp | ITP - Fall Protection Fencing - 304 - Rev B
4bda4dd5-6c7e-5f3b-95d6-b355b65894a7 | section | 4.20 Fall Protection Materials
0f8be9ea-2f02-50c1-9123-8159ff69358f | checkpoint | 4.20.1 - Fall Protection Fence Materials
d534393e-c98b-5a5f-88e5-64e66d165722 | note | Acceptance / Conformance Criteria - Safety fence design load shall be in accordance with NZS1170.1: Table 3.3 Type C3. All steelwork shall be hot-dip galvanised in accordance with AS/NZS 4680:2006.
12d18b70-4754-54df-b0ff-579be8bd10d9 | note | Standard / Specification - PS 18.6.1, PS 19.25.1
90acc04b-3d0d-5510-8d15-444e09a6130d | note | Verifying Document - Datasheets and Mill Certs
6f9bf2a8-5f37-5ea8-96fd-e2d3b5780181 | note | Frequency - Prior to use
d48e1a79-c7aa-5ef1-a62c-d564c2cf9fec | note | Verification Activity: Activity - R
f7301aa3-b12f-5a7d-9e03-de6ee2710e05 | note | Verification Activity: By - SE
46972395-5948-5e78-9495-0c404383cb43 | checkpoint | 4.20.2 - Fall Protection Fence Epoxy
3ffc1176-4a53-5979-a72b-936c446736ff | note | Acceptance / Conformance Criteria - SikaDur UA Epoxy Repair Mortar or a similar approved mortar.
888857b2-3f93-58fe-89ac-a581671c2523 | note | Standard / Specification - PS 18.6.1, PS 19.25.1
392e97e3-2841-5c62-b773-b72f484c18da | note | Verifying Document - Datasheets
40f5841d-63d4-5d85-b325-fa88721ace0b | note | Frequency - Prior to use
4fdf8ad1-79ab-520b-9bfd-d56df3e219ec | note | Verification Activity: Activity - R
06fbaaf7-5803-56b0-8dff-d480289c2989 | note | Verification Activity: By - SE
37a8b92e-54e2-52c6-a615-1158e70eafb6 | checkpoint | 4.20.3 - Fall Protection Fence Base plates
c6075165-c7cf-5771-a980-559c64682dfc | note | Acceptance / Conformance Criteria - Mild steel baseplate with holes shall be Hot Rolled Grade 250 complying with AS/NZS3678:2016 (AS/NZS3678-350).
4b41d91b-c9a0-5537-9d27-94e2b233a4e8 | note | Standard / Specification - PS 18.6.1, PS 19.25.1
e3de1f7a-75d1-5e92-a5f5-25a2f3f42cae | note | Verifying Document - Datasheets and Mill Certs
feb96f00-8423-5b78-8e42-23e3024b5011 | note | Frequency - Prior to use
548f3da1-c304-57d3-ad68-0a54878b7681 | note | Verification Activity: Activity - R
98c6c5e0-35ec-5a25-a348-f81fafe1cdd7 | note | Verification Activity: By - SE
c8b391db-10fa-5ea9-aff5-2da1abe64716 | section | 11.01 Fall Protection Fence
5b0cf638-dc9b-51ce-a49e-4d9030375a52 | checkpoint | 11.01.1 - Fall Protection Fence Installation
5e78e5a0-023d-5358-87d2-60f1d570d583 | note | Acceptance / Conformance Criteria - Safety fence system shall be Webforge and shall be installed in accordance with Manufacturers Specification. Posts are to be positioned vertically in both the longitudinal and transverse directions. All rough or sharp edges or protrusions to be buffed smooth. All rails should be jointed within post sphere. Rails should be fixed to spheres at every post by welding.
58981d55-b82d-5013-be23-19f6a0267f28 | note | Standard / Specification - PS 18.6.1
f67d5198-9982-5f30-a180-5d651f23c570 | note | Verifying Document - Site Records
dff54f59-1628-534e-baf3-fba07a7a30f1 | note | Frequency - Each Fence
e9a223e5-bd46-5699-8728-f4c94082ad53 | note | Verification Activity: Activity - S
ded1d516-b4e0-5a76-9117-231f6508bb02 | note | Verification Activity: By - SE
8a59d9b1-2b89-5675-8bbe-6baaede81f3a | checkpoint | 11.01.2 - Remedial Painting
59882d18-98a9-5b49-9eca-a354a36e21e3 | note | Acceptance / Conformance Criteria - Damaged galvanizing shall be coated / repaired in accordance with Appendix E of AS/NZS 4680, e.g., painted with 2 coats of an approved zinc rich paint, such as Resene AmorZinc110.
a7c73dbf-05f7-5c63-a377-239927478c22 | note | Standard / Specification - PS 18.2.3, PS 18.2.1, PS 18.2.2
3a5234fa-ebd5-563a-ba5c-4f8600ceb0c9 | note | Verifying Document - Site Records
5a7b2e2d-a230-5478-a31c-3f8c81bc4ccb | note | Frequency - Each Occurance
a56d27ed-980e-5558-9655-59ad0eed1938 | note | Verification Activity: Activity - S
85fd877f-efe2-5dd3-87b6-85be6753d510 | note | Verification Activity: By - SE
311c9835-2305-59cb-abe7-1a9a995c3533 | checkpoint | 11.01.3 - Fall Protection Fence Post Spacing
f639cf18-f630-5fb8-906a-fed0ebdeef22 | note | Acceptance / Conformance Criteria - Post spacing shall not be larger than 2m. Posts should not be placed closer than 200mm from the edge of the wall joints.
3fca7d61-5a9f-5414-8dd6-69d272fe991f | note | Standard / Specification - PS 18.6.1, PS 19.25.1
3cc53b4f-b9f6-57c2-933c-b08339d96eed | note | Verifying Document - Site Records
dade21b3-c1a5-500b-81be-06503d6f7c03 | note | Frequency - Each Fence
bbda1d13-8103-5702-bf81-4e5c8bb99689 | note | Verification Activity: Activity - S
f40856f5-5826-5d3a-b06c-42750adb6290 | note | Verification Activity: By - SE
98d6617f-4b8b-5df7-9a26-783cfab914b1 | checkpoint | 11.01.4 - Fall Protection Fence Reinforcement scanning
db453017-d7c8-589f-b7ad-7c09b620e0d9 | note | Acceptance / Conformance Criteria - Reinforcement scanning shall be carried out at every post location. If clashes with reinforcement are identified, the following amendments shall be taken, posts at which the rail is not spliced shall be moved +/- 50mm along the handrail alignment.
3e78432c-2413-5ef8-8642-0819e67f694d | note | Standard / Specification - PS 18.6.1, PS 19.25.1
072b2370-4443-5d28-afb5-f91880ef6c56 | note | Verifying Document - Site Records
b56d3717-9372-545d-b5df-1f4d2ea9a0c6 | note | Frequency - Each Hole
393d8ad4-7644-53f4-b957-61455f4e1e00 | note | Verification Activity: Activity - S
a2e7cf3f-513b-52b3-9d45-b6c04ed64340 | note | Verification Activity: By - SE
c0ed3146-519c-5f38-a733-ab540b4b40de | checkpoint | 11.01.5 - Fall Protection Fence Drilling
c29235a9-78ce-5757-a844-f72a53d871a1 | note | Acceptance / Conformance Criteria - Holes for fixings shall be formed using a rotary hammer drill. It is not permissible to cut or core through reinforcement. Should reinforcing steel be struck, the hole shall be abandoned, cleaned out using compressed air and backfilled with SikaDur UA Epoxy Repair Mortar or a similar approved mortar.
b8afa223-5de7-5985-a995-a1efb68e2212 | note | Standard / Specification - PS 18.6.1, PS 19.25.1
4ead022c-6ddc-53fb-8d95-666535df23e7 | note | Verifying Document - Site Records
db05bafc-3fc0-5f5b-80be-cc5c53ad72dc | note | Frequency - Each Hole
d3d31e7f-a8cd-59f8-bb88-21465b794f98 | note | Verification Activity: Activity - S
78441b7e-6dcf-5ac2-9c0c-7c3e7e63037d | note | Verification Activity: By - SE
| checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
| textbox | Contractor's Rep Name:
| textbox | Engineer's Rep. Name:
| date | Date:
| signoff | Add Signature