## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
0f87aceb-230c-445c-bce9-472d50eb0dd7 | checklist | Ω (DEPRECATED) ITP - Stormwater (Structures) - 202 - (alternate Rev B) | itp | ITP - Stormwater (Structures) - 202 - Rev B
e48adf96-a921-5393-9ab6-5ff61a725470 | section | 1.01 Stormwater Aggregate Materials
a95ca035-74c8-594b-8085-a1d9aa423a24 | checkpoint | 1.01.1 - Controlled Low Strength Materials - CLSM
b9cb59d3-622b-5902-82ee-48040e0dc331 | note | Acceptance / Conformance Criteria - The use of CLSM by the Contractor will require approval from the Engineer on a case-by-case basis.
d554de1a-f0a4-5766-9fab-bcabe212688d | note | Standard / Specification - PS 16.8.1, PS 16.37
fd9db4d6-b13f-578c-8a31-3a884af41cc9 | note | Verifying Document - Engineers Approval
293ada82-74e5-50ff-abe1-0c3759c6dfc0 | note | Frequency - An application submitted to the Engineer for approval, to use CLSM.
a0d796f0-ae9b-550b-83fb-f5fb3235c7bc | note | Verification Activity: Activity - HP
d9065f6e-0e33-5678-b156-92376f309262 | note | Verification Activity: By - ENG
cb3b8a82-5309-5c00-9c64-feba92dfeae8 | signoff | AUTHORITY HOLDPOINT
25ba88a4-4910-5004-8d64-eec2b2d9f977 | checkpoint | 1.01.2 - AP65 Aggregate
af80170f-9aed-5408-bec8-4a356e26bf00 | note | Acceptance / Conformance Criteria - AP 65 Aggregate is to be a crushed product with a maximum granule size of 65mm and be a graded, clean durable aggregate which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
bee0afb1-20d8-5697-b6a2-6c782b16c71a | note | Standard / Specification - PS 16.8.2.1, PS 16.9.1.2, PS 16.6, PS 16.37
c4a66042-2771-5b74-a492-ca79dea11dba | note | Verifying Document - IANZ Lab Reports
13ea5eba-d119-5ef1-b17c-3554240289eb | note | Frequency - Submitted to Engineer for approval
cd7d29b9-6f4c-5665-b93d-90316e17cf36 | note | Verification Activity: Activity - HP
d7fdc9ce-90a5-5e16-b637-b1f83456885d | note | Verification Activity: By - ENG
d104ba0f-f41a-5817-8d54-5b844a37c26a | signoff | AUTHORITY HOLDPOINT
6dd2f2ca-856f-5198-a519-10cfd10b5e41 | checkpoint | 1.01.3 - AP40 Aggregate
0d99e137-981e-585d-900b-c0c4ba5ebe81 | note | Acceptance / Conformance Criteria - AP 40 aggregate is to be a crushed product with a maximum granule size of 40mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requitements
47ee1303-2574-50ae-b3c6-beb51f336151 | note | Standard / Specification - PS 16.8.2.2, PS 16.9.1.2, PS 16.6, PS 16.37
6e63f27c-18db-5df0-9168-7215f6097c85 | note | Verifying Document - IANZ Lab Reports
71d6a36c-6da9-5b27-ad80-11fc671a8e9f | note | Frequency - Submitted to Engineer for approval
94a9d1bf-48a9-59d5-9052-be3d45e3b182 | note | Verification Activity: Activity - HP
d1d25752-f92f-530a-ab79-2acc8f9d8256 | note | Verification Activity: By - ENG
c5c5034d-17c0-530a-a8db-4f8cf9313412 | signoff | AUTHORITY HOLDPOINT
60b51c6d-53b8-52b8-86b9-6f6cb8e7a404 | checkpoint | 1.01.4 - AP20 Aggregate
8752c5af-e588-5e11-b8bc-3ac23a4c8173 | note | Acceptance / Conformance Criteria - AP 20 aggregate is to be a crushed product with a maximum granule size of 20mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
852076c2-b933-5c7d-9cb6-66271e63669f | note | Standard / Specification - PS 16.8.2.3, PS 16.9.1.2, PS 16.6, PS 16.37
b360cd9b-409d-59ba-9154-d674c6997095 | note | Verifying Document - IANZ Lab Reports
c6b0b3a7-6dcf-50c1-9752-a9b5e6c216f4 | note | Frequency - Submitted to Engineer for approval
84aee3af-5288-58df-8681-3745321c5d83 | note | Verification Activity: Activity - HP
36d91c27-e601-58f0-bfc9-7e77fbbbba59 | note | Verification Activity: By - ENG
c815d7ea-eda2-5e1b-92bd-9dc6bba41adc | signoff | AUTHORITY HOLDPOINT
218c5f06-0ccd-560e-b6b0-c9b027b59a28 | checkpoint | 1.01.6 - Alternative Bedding
a85001ed-6c8b-5551-9216-b5b9ec0d7a89 | note | Acceptance / Conformance Criteria - If the Contractor wishes to propose a different material from that specified in this section, the Contractor shall submit to the Engineer
cdd195da-360a-5eb0-9f67-da0bb290ce41 | note | Standard / Specification - PS 16.9.2.1, PS 16.9.1.2, PS 16.37
094abc90-e93f-59f2-8f58-4a3416f1fec3 | note | Verifying Document - Statement from the concrete pipe supplier
2a6a8f95-5476-5bd0-909d-f9d7bc293854 | note | Frequency - Submitted to Engineer for approval
7853bd94-b417-5dfe-865f-db7f733661b9 | note | Verification Activity: Activity - HP
f0e0455f-bafc-5c44-9fdb-2cfb183fee07 | note | Verification Activity: By - ENG
fa2dd314-75f8-5cd2-8157-2cf844b50ad4 | signoff | AUTHORITY HOLDPOINT
878ad85c-37ec-5b05-aa55-b8b309cd8376 | checkpoint | 1.01.7 - Overlay Zone Material (for concrete pipes)
73d0dffb-72de-5c06-abf2-f02ee29527da | note | Acceptance / Conformance Criteria - Materials for the overlay zone GAP 20 shall be used which has been tested for Grading, Weathering Index, Crushing Index
c1fc6083-d497-512b-899f-211d02bc7bb0 | note | Standard / Specification - PS 16.9.2.2, PS 16.37
78c23021-09c1-50ce-b93d-a1424387d6c7 | note | Verifying Document - IANZ Lab Reports
4b9eaaa1-c003-502f-a6c4-adc0743d8a8e | note | Frequency - Submitted to Engineer for approval
eb0d75c9-c21d-52e8-837d-9d2632d925b0 | note | Verification Activity: Activity - HP
674ddbf1-b044-5339-b386-a5448fe068f7 | note | Verification Activity: By - ENG
f8091fef-c776-5fa2-af04-7a9b6e0462dc | signoff | AUTHORITY HOLDPOINT
4a4e4a8a-7cb6-582c-93dc-909ff02072ba | section | 1.02 Stormwater Pipe Materials
69e09f41-d841-56ba-b5dd-cc6933a78e4f | checkpoint | 1.02.2 - Steel Work
7983486e-24cd-50d5-a88a-077d77907780 | note | Acceptance / Conformance Criteria - Unless otherwise specified, all steel work shall be fabricated from mild steel conforming to the requirements of AS/NZS 3679.1:2010 and AS/NZS 4680:2006. All cut surfaces shall be protected with a corrosion protection coating i.e., zinc rich paint.
096536d9-25d7-5385-a9ab-7329e68ac748 | note | Standard / Specification - PS 16.8.1, PS 16.8.4
a67baf84-4f4e-5af7-9f49-3d508d370eb0 | note | Verifying Document - Datasheet
8e8f3895-996a-571f-8a07-9807f33a4bf9 | note | Frequency - Prior to use
259e532f-e49b-52fa-a769-9900f1bcbbce | note | Verification Activity: Activity - R
c6d0f086-4e55-5120-9b06-7082f5a74ce6 | note | Verification Activity: By - SE
60ecbba7-61f7-5ae0-85a1-a18bef3de7c5 | checkpoint | 1.02.4 - Steel Fitting Corrosion Protection
01185b10-0157-5713-b427-207939b2ade7 | note | Acceptance / Conformance Criteria - Steel fittings shall be shop assembled as large as practicable before hot dip galvanising or zinc metal spray to AS/NZS 2312.2:2014 and AS/NZS 4680:2006, to minimise the number of field welds and bolted joints required.
25ea048e-44e9-5283-8d13-d016e3882bcc | note | Standard / Specification - PS 16.8.4.1
baa12f3d-f909-5cfb-8bf9-7107d00dcbe0 | note | Verifying Document - Datasheet
3b0dd7b1-6557-5e42-b3be-12318e43d8f1 | note | Frequency - Prior to use
35ab5a0f-10e0-5d1b-8df2-6eadfb534c2a | note | Verification Activity: Activity - R
2a194199-2148-53af-9e58-783ccc2f0809 | note | Verification Activity: By - SE
64f50980-c6f3-5fcc-9255-86d784630f99 | checkpoint | 1.02.5 - Hot Dip Galvanised
b513d5d2-10aa-5f60-89c6-58c9d7e3abda | note | Acceptance / Conformance Criteria - All ferrous metalwork except standard galvanised pipe shall be hot dip galvanised to HDG900 unless otherwise specified.
5d82e457-0b21-59b4-9eba-46c2b85cc2a0 | note | Standard / Specification - PS 16.8.4.1
1a0913ce-7898-56e3-892a-ed544fffcb61 | note | Verifying Document - Datasheet / Cert
b7fa39ed-7c9f-533f-a6b4-0b740b67c96b | note | Frequency - Prior to use
a9c395dc-0d70-5ef4-85ae-4190b4c6b5dd | note | Verification Activity: Activity - R
f08d80a0-bb58-5b29-bd7c-ee503311a19c | note | Verification Activity: By - SE
2fc23d9c-901d-57bc-b711-629672507c09 | checkpoint | 1.02.6 - Fastenings
1b59b4f3-9733-5b2b-a421-64721b8a2f98 | note | Acceptance / Conformance Criteria - All fastenings associated with manholes or drainage structures shall be either hot dipped galvanised or stainless steel. Zinc Plated fastenings shall not be permitted
8fbbe4db-f8ac-5d54-8095-fd3bd975af7c | note | Standard / Specification - PS 16.8.4.2
05cafc36-f9b1-58d4-95d1-2579f2dea1b3 | note | Verifying Document - Datasheet
3df46a37-58ed-533e-b9e5-00d053f7dddb | note | Frequency - Prior to use
d14e8d20-e9f8-5d12-b4c3-5bc088c6d24c | note | Verification Activity: Activity - R
6c9ac783-c583-5a72-911d-15db94b028e5 | note | Verification Activity: By - SE
35d72f2d-cc19-5c7a-90cc-ec774c712f02 | checkpoint | 1.02.7 - Concrete pipes and fittings
bd5c47f4-cf1f-50dc-8976-169e73db3ae0 | note | Acceptance / Conformance Criteria - Concrete pipes and fittings shall comply with the requirements of AS/NZS 4058:2007 for concrete pipes
1731c56c-d3a6-5dad-aca8-69a3ba67f45f | note | Standard / Specification - PS 16.9.1.1, PS 16.37
775f9007-c66b-5956-8a36-44d03630cc33 | note | Verifying Document - Datasheets
66c80b3d-245b-5bf8-a54f-fd82cf27bf23 | note | Frequency - Prior to use
eb064c25-c76c-5ed0-affe-481bf3ed01b1 | note | Verification Activity: Activity - W
386e7a4c-f276-54f6-92f6-7be2b7ac52f1 | note | Verification Activity: By - ENG
f5e951c8-6f34-5e62-aa3c-51bb1cf65da1 | checkpoint | 1.02.8 - Quality of Pipe and Precast Units
645f8a5c-6968-5a6e-9c36-2decea5a5c54 | note | Acceptance / Conformance Criteria - IANZ Accredited Manufacturers certificate to NZTA F/3 (refer to Appendix F)
effdac09-57ab-5c96-9fa7-9c71b362880a | note | Standard / Specification - PS 16.34
340eb304-3e6a-5a2c-b3f2-e90da12f49de | note | Frequency - For every pipeline delivered (as soon as they are delivered)
e84e9ff3-3308-5e82-b5e6-74a8c9354723 | section | 1.03 Stormwater Structure Materials
91fce285-1472-507c-b6a3-7c424a6057d7 | checkpoint | 1.03.1 - Precast Catchpits
e407ffbd-9200-5da7-8e25-bd5b9f3d1b32 | note | Acceptance / Conformance Criteria - All catchpits shall be precast concrete suitable for HN-HO-72 traffic loading.
87577e7f-5f3f-57fe-ba74-a703edcfd570 | note | Standard / Specification - PS 16.10.1
8ceb1190-a1de-51bb-88c4-3d29675f7809 | note | Verifying Document - Datasheet
ca0b164a-0c34-5e15-b97a-2254b55e46c8 | note | Frequency - Prior to use
7894f69f-6143-5628-a852-3155e5566e76 | note | Verification Activity: Activity - R
c902d63f-8497-5ec0-a66e-4f94fb56a84c | note | Verification Activity: By - SE
56cb0cef-ffb7-59aa-8cfc-680a0a3fe297 | checkpoint | 1.03.2 - Catchpit Lids
e6170961-e3f3-502c-9fa2-e7510f1f4cae | note | Acceptance / Conformance Criteria - Non-Rock 510mm Class D Heavy Duty type lids or similarly approved shall be used unless otherwise specified on the drawings. Heavy Duty type lids to be suitable for HN-HO-72 traffic loadings that are cycle friendly.
bd39b4d6-1ae8-5971-8291-8e90c4274f69 | note | Standard / Specification - PS 16.10.2
5e113349-3b70-5825-8b06-060f2df94543 | note | Verifying Document - Datasheet
d909513c-266a-59da-a468-cc109b3621ff | note | Frequency - Prior to use
8b226bac-b2e0-5a85-943a-14307bb421ad | note | Verification Activity: Activity - R
12c18111-0bd8-55c3-a804-82722e87321e | note | Verification Activity: By - SE
130a6f97-8fb9-504e-bcea-a3dfe8267d7c | checkpoint | 1.03.3 - Precast concrete manhole
634be762-717c-515c-a554-d8979387f70c | note | Acceptance / Conformance Criteria - All precast concrete manholes shall be manufactured in accordance with NZS 3109:1997. All manholes shall be suitable for HN-HO-72 traffic loading.
ca8a9af4-798e-50fd-9e4c-3b5ec7898656 | note | Standard / Specification - 16.15.1
420f8c7e-04f9-59fb-ab74-7fc35388c82a | note | Verifying Document - Datasheet
b1584ed3-02ad-5e48-9c73-8390b3407f96 | note | Frequency - Prior to use
227984e3-99ed-57ad-95cc-c3048e175ddf | note | Verification Activity: Activity - R
c063324e-399e-58e1-b115-43ed816dab2f | note | Verification Activity: By - SE
3000c124-dd41-5f1e-9807-ca9596c2438a | checkpoint | 1.03.4 - Catchpit Grates and Frames
7453bb2e-b4ad-51dd-9022-e5680ffe2cd4 | note | Acceptance / Conformance Criteria - Catchpits grates and frames shall be grey cast iron suitable for HN-HO-72 traffic loadings.
33d34d62-d9ad-5330-b2b5-b6de920f060f | note | Standard / Specification - PS 16.10.1
380387b8-ed28-5375-a13c-4823092ea855 | note | Verifying Document - Datasheet
29e240df-4bbb-5c0d-9430-412f7612a924 | note | Frequency - Prior to use
fd3c952a-02b6-5538-8278-9f9afdd806ac | note | Verification Activity: Activity - R
f6f94745-3ea0-5aa9-95a9-ecdd44c3b113 | note | Verification Activity: By - SE
14e1a3a3-be4a-5b23-8bcf-99effdb4e476 | checkpoint | 1.03.5 - Scruffy domes lids
4723b51d-d9f5-53fa-99d6-78bd334e89d7 | note | Acceptance / Conformance Criteria - Scruffy domes lids shall be galvanised steel Hynds Type 2 scruffy domes (unless noted otherwise in the drawings), or similar approved.
4e4d8c5e-c79d-5145-b794-2d0297d94056 | note | Standard / Specification - PS 16.16.2
93555c26-b70e-51b5-a4f5-21678789eb95 | note | Verifying Document - Datasheet
25a85b6d-506c-59a5-be45-0512b40f6556 | note | Frequency - Prior to use
fe1d8a9b-ab9d-503e-a92d-fb29067fb9de | note | Verification Activity: Activity - R
cac01b62-8654-5dd6-9bb0-1bb924597fea | note | Verification Activity: By - SE
cf286ccb-3176-5052-9aa2-4d85340f725f | checkpoint | 1.03.6 - Cement Mortar
7cc40a29-dfc7-5c71-bb96-d455b3dfbcfe | note | Acceptance / Conformance Criteria - Cement mortar shall be Durability Class M4 in accordance with NZS 4210:2001, with a minimum compressive strength of 12.5MPa.
3bec60e2-bed1-5d40-87da-604172d29ee4 | note | Standard / Specification - PS 16.8.1
48a9e6b5-f12f-5ebb-8a40-aa28c96b3a3e | note | Verifying Document - Datasheet
b8172244-144e-56dc-ada3-fe04a0d79433 | note | Frequency - Prior to use
63fa2a58-3fa3-59d6-81a3-1a7e80f98de3 | note | Verification Activity: Activity - R
d22fba64-a915-50fb-8599-28b0232fa4de | note | Verification Activity: By - SE
254f5570-ad69-595d-a595-909b315f255c | checkpoint | 1.03.7 - Epoxy Mortar
f2d4d949-c995-5eb8-b960-03edc644762e | note | Acceptance / Conformance Criteria - Epoxy mortar for use in manhole riser joining or repairing of damaged or cut concrete (to provide cover to reinforcing due to cutting of precast units) shall be Hynds (MSR) or Humes Hume bond (or similar approved), applied in accordance with the manufacturer’s recommendations.
71d12180-4709-548f-b9fd-e42220292653 | note | Standard / Specification - PS 16.8.1
ac466c57-262c-593d-865b-8e021eafb278 | note | Verifying Document - Datasheet
d5ae3c63-f547-5786-9da6-99bcaa04f4cb | note | Frequency - Prior to use
d384304a-0ceb-5f2d-888a-0af115e6cd57 | note | Verification Activity: Activity - R
9dc04b08-af9e-5e8d-a29f-397601fe007d | note | Verification Activity: By - SE
b290cd34-1606-50fd-995d-df90428ff8a7 | checkpoint | 1.03.8 - Precast Headwalls and Wingwalls
2aea9831-44c8-502d-9cb4-31bfea24869e | note | Acceptance / Conformance Criteria - Precast concrete headwalls or wingwall units shall be manufactured in accordance with NZS 3109:1997.
b466059e-18fa-56e3-b8cf-ddeef46ef999 | note | Standard / Specification - PS 16.13.1
48868a3c-d614-5565-a13b-3b8f5032cb2e | note | Verifying Document - Datasheet
f4edb9cc-17ef-573d-9611-0b663f37b336 | note | Frequency - Prior to use
88a8147e-3ae8-586e-bc5a-79c822b94136 | note | Verification Activity: Activity - R
972e5ea3-2701-56c8-8ea7-03dc2399cec3 | note | Verification Activity: By - SE
6d0f6d8c-7ec1-5e25-8613-a36245635455 | checkpoint | 1.03.9 - Erosion protection matting
8eb1e8c5-c77a-5966-adaa-594f0a07fcbc | note | Acceptance / Conformance Criteria - Erosion protection matting (coir Blanket or similar approved) is to be 100% biodegradable.
c6b9dac9-8519-5998-9374-3b2b45d725c4 | note | Standard / Specification - PS 16.13.1
29ecd1a9-bd78-5f4a-a647-f5557c620ca5 | note | Verifying Document - Datasheet
3d8ed03f-0f2e-5d3c-8f31-577b8d129216 | note | Frequency - Prior to use
5f1a4837-9a24-52cd-8f2c-b3337d7cc032 | note | Verification Activity: Activity - R
b118e925-1b38-51f6-9362-5aef40b69302 | note | Verification Activity: By - SE
0a061ecb-47c1-5451-be12-856fee80de39 | checkpoint | 1.03.10 - Precast Soakage Pit
649e01bd-8154-573f-a3cd-3a6bf4c78811 | note | Acceptance / Conformance Criteria - All precast concrete Soakage Pit manholes shall be manufactured in accordance with NZS 3109:1997.
da94e9ba-3fa9-5a42-a147-241634ca73f7 | note | Standard / Specification - PS 16.12.2.1
343f10c2-efa2-5d81-957c-64c8e8bdb937 | note | Verifying Document - Datasheet
9800ac4e-fc96-5395-950d-8f5d97f3c838 | note | Frequency - Prior to use
d7130151-50ad-5933-8505-02ac8efcc1fd | note | Verification Activity: Activity - R
9a83194e-2fcc-5fd2-829a-4671ef5e4184 | note | Verification Activity: By - SE
10e6e077-15d2-56b2-ae1c-2a0894025b52 | checkpoint | 1.03.12 - Manhole Sealant
b1fba66c-fa51-5ab6-81a5-9257673353b1 | note | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
caf60dd5-2587-512e-bbdd-38748f7b581a | note | Standard / Specification - PS 16.12.2.2
5ec3bfd4-4b89-5406-ab56-a51192d66787 | note | Verifying Document - Datasheet
f7f757c0-2fc8-5eda-9eef-951f1d89f780 | note | Frequency - Prior to use
c0d00499-e831-54eb-9b2e-23ab7d09c556 | note | Verification Activity: Activity - R
4e5d5d68-8c05-5b42-8538-4830a13ae01f | note | Verification Activity: By - SE
a0739509-7e17-5960-a813-ae432cb4ebad | checkpoint | 1.03.13 - Head and Wing wall Insitu Concrete
11245d58-c1be-5a1a-8561-10399a85f634 | note | Acceptance / Conformance Criteria - Headwall and wingwall insitu reinforcing shall be steel grade 500E.
83fd79c8-c568-5f06-b17b-fa3bfd3e896d | note | Standard / Specification - PS 16.13.2
ca6591b6-ef01-56bd-a720-fd5ada9551f6 | note | Verifying Document - Mill Certs
b8d16d43-5094-524b-a9b2-ca92ec2bacc3 | note | Frequency - Prior to use
d1f6fdc0-3c1e-57a9-9054-59c64e60d928 | note | Verification Activity: Activity - R
c16fa753-e1b4-54ed-a760-2245d5fd5043 | note | Verification Activity: By - SE
de604162-2266-58c3-bfef-680800f0396a | checkpoint | 1.03.14 - Head and Wing wall Reinforcing
847b76a9-15d5-55c4-b19c-eb2c5a847275 | note | Acceptance / Conformance Criteria - The headwall and wingwall cast in-situ concrete shall be 40MPa
d9d7a9b3-c50c-5307-a76a-28e05a25bf40 | note | Standard / Specification - PS 16.13.2
dd353d74-2cb8-56cb-8460-a70faefad9b6 | note | Verifying Document - Mix Design
7ca5b1a0-d31f-58f7-93ac-dbaaf779d679 | note | Frequency - Prior to use
14f6f916-9c9c-5212-9cec-e45904c012ad | note | Verification Activity: Activity - R
32984417-a5f4-58d6-99d3-db5e7d3b819e | note | Verification Activity: By - SE
0e382e0a-0547-590f-bae7-3624e64784f6 | checkpoint | 1.03.16 - Benching Concrete
928c057a-d29f-5ffd-9593-552cb38134d0 | note | Acceptance / Conformance Criteria - Benching shall be 20MPa concrete
9df84dda-e75c-5d87-93b0-1a1ccc670043 | note | Standard / Specification - PS 16.15.2
04317dcd-5b01-5c4b-9300-a09ab978053d | note | Verifying Document - Mix Design
05b8be1e-8ffd-5b62-b63d-ccce3b85adfa | note | Frequency - Prior to use
c1838719-7c4e-5bad-8f7a-ffd337adbe42 | note | Verification Activity: Activity - R
b0282277-0faf-5295-93be-7133bab0b29d | note | Verification Activity: By - SE
3f8a50a6-974f-54d2-989e-817719c48b96 | section | 2.01 Stormwater Drainage (Existing Assets)
9e4cc768-b88c-500f-afbb-8755a862e601 | checkpoint | 2.01.1 - Obsolete Stormwater Structures
2c3d3a9c-b156-5097-ba15-7a0782b26fa6 | note | Acceptance / Conformance Criteria - Obsolete catchpits, manholes, kerb and channel shall be demolished, uplifted and removed to an approved tip site.
31173915-c7cd-5f74-9e62-c25e15a35923 | note | Standard / Specification - PS 14.2.1
0e6c9191-8281-5d8e-bdec-7784bbdf645f | note | Verifying Document - Site Record
504dcb0e-f3f8-56a6-981a-a8725478c73a | note | Frequency - Each Obsolete Structures
00a8535f-eec8-5fab-ab44-c16900a827ac | note | Verification Activity: Activity - R
6f3ca366-5b19-5a6c-b489-12eabf0934d2 | note | Verification Activity: By - SE
c7f50f69-b0f9-5fdc-8f19-342f12ec544b | checkpoint | 2.01.2 - Cutting Existing Pipes
747c8d6f-5003-5245-8865-225a4eae1ad0 | note | Acceptance / Conformance Criteria - Where the catchpit will be replaced by a new drainage structure and/or constructed in a new location the existing stormwater pipe shall be neatly cut perpendicular to the line of the pipe to allow it to be easily extended.
043b091e-ccd0-5604-b95c-01ec23a83c89 | note | Standard / Specification - PS 14.2.2
70cd7d22-0581-5e3b-9735-36bdd4a03618 | note | Verifying Document - Site Record
dc9b9aeb-7227-58a1-b53a-b0365ca89b19 | note | Frequency - Each Occurrence
4ab71c05-9078-50f8-8dfd-bac50912375d | note | Verification Activity: Activity - R
f5bffa36-df23-5049-8e3e-f04aa5756571 | note | Verification Activity: By - SE
4825206e-1201-5e97-939a-dd7bb149a61d | checkpoint | 2.01.3 - Debris Removal and Void Filling
00ae3615-b5f8-5515-94bb-cc4af1790b3b | note | Acceptance / Conformance Criteria - All debris shall be removed to waste. The resulting void shall be backfilled with well compacted approved fill material.
91a12ac3-25c7-566b-abb0-fefe6dfa0cca | note | Standard / Specification - PS 14.2.3
59b99207-5c92-5b0f-a4c1-38b1f9762fa8 | note | Verifying Document - Site Record
b3dd4f55-1940-51f5-b8a9-d5b14a8c3cc6 | note | Frequency - Each Occurrence
4c9006bc-ce0a-54e5-93ea-32a656e3b7b9 | note | Verification Activity: Activity - R
2f04c4ac-fc2c-5b19-8eea-b4af3bf524f2 | note | Verification Activity: By - SE
7d731da0-9d36-5dc2-bbaa-36fd489fe260 | checkpoint | 2.01.4 - Obsolete culverts
64a008ec-0d3d-565f-a7e7-15e9e3229bec | note | Acceptance / Conformance Criteria - Obsolete culverts shall be removed or may be left in place subject to the agreement of the Engineer. Abandoned culverts shall be plugged with concrete at each end or if the culvert is within 1.0m of the surface it shall be completely filled with a cement grout.
43d90bc1-c134-5f6c-aa7a-a4cb1dce5bbb | note | Standard / Specification - PS 14.2.4
1a18f3e3-6c2e-5f7e-8b12-ff9be1c34d9b | note | Verifying Document - Site Record
17297358-32fe-5c3e-892b-c9de06eef71f | note | Frequency - Each Occurrence
0f0f5c08-98a1-5108-b306-bd9adf7ac08f | note | Verification Activity: Activity - HP
bb150a45-ee07-55a1-9ca5-6948c1428315 | note | Verification Activity: By - ENG
07db67e3-cab4-5ae7-ac32-126b928f841a | signoff | AUTHORITY HOLDPOINT
fafc21ec-637c-525a-8389-661e2d0e99f5 | section | 3.01 Stormwater General
a210fb2a-8fbf-5a1e-b274-262fc5b0bdb3 | checkpoint | 3.01.1 - Setout
885e5323-57d8-5a8e-8c9c-69f94e63bfc0 | note | Acceptance / Conformance Criteria - Prior to the commencement of any drainage works for a particular drainage line, the Contractor shall set out the line, level, and position of the proposed drainage line, including inlet and outlet positions and levels, and present it to the Engineer for their consideration. The Contractor shall provide at least 48 hours’ notice to the Engineer ahead of set-out and allow 48 hours for the Engineer to respond prior to commencing work.
a1a93af7-9b43-51ef-bc2a-c6ab37b27930 | note | Standard / Specification - PS 16.6.1
da135260-1772-5a7f-b957-b57a6f72a4b6 | note | Verifying Document - Survey Records
6463a494-9a7f-549e-b734-fca2b7301daf | note | Frequency - Prior to the commencement
c3f2d9fe-1cf3-5d58-8d66-3279709c13ef | note | Verification Activity: Activity - HP
0fbb3873-7a54-56b0-8c33-adb06319ad03 | note | Verification Activity: By - ENG
1de8f978-8a84-5ff3-a1fb-37a4c0083aee | signoff | AUTHORITY HOLDPOINT
654daa1a-e7a3-569d-81c4-4329920ea593 | checkpoint | 3.01.2 - Dealing with Water
e37040ee-67a4-5058-bddd-36d0b3da0335 | note | Acceptance / Conformance Criteria - The Contractor shall maintain all trench inverts free from flowing or accumulated water. Water arising from, or draining into, the trench shall be drained or pumped. Any sumps required shall be refilled to formation level as directed by the Engineer.
de17876a-efdd-5ba7-9620-afee920b2a56 | note | Standard / Specification - PS 16.7.1
ceacfe1a-148e-5994-9711-e757a9db3c38 | note | Verifying Document - Site Records
c22ecdcc-0b52-5ca0-a9b6-402c2b0a5cd4 | note | Frequency - During Works
852d3cca-741a-5c6b-bae5-c08aab69d59d | note | Verification Activity: Activity - S
83d23992-8d12-589d-bac6-5768b9173ac3 | note | Verification Activity: By - SE
4f09ae7c-2a93-5390-810b-532208062fd7 | section | 3.02 Pipe Installation and Backfill
4783c80c-dbfc-527d-b81d-044fdec625f6 | checkpoint | 3.02.1 - Open Trenches
09aa8ea3-d78c-5998-a238-4b3026117470 | note | Acceptance / Conformance Criteria - All open trench excavations for pipelines shall be to a minimum depth of 100mm below the pipe external walls. Where excavating in natural ground or existing carriageways, no more than 100 metres of trench (per drain laying operation) shall remain open at any one time.
88a69342-365e-5e42-a7e8-e3c6c51fca3f | note | Standard / Specification - PS 16.9.2.10
902b85a7-4238-5c3d-806d-1ecd05255206 | note | Verifying Document - Site Records
4c1d8f7d-813a-521e-a636-9694c762f276 | note | Frequency - During Works
da90614b-9307-53fd-b41d-fe6c6505e67b | note | Verification Activity: Activity - S
125dce34-a0b8-5c8e-9aa3-89d65eeb7792 | note | Verification Activity: By - SE
79d789f7-cd98-5db7-b2f4-1f8fdbbb5348 | checkpoint | 3.02.2 - Saw Cutting
7083baa1-f4ba-576a-9369-c64c5cd7ce85 | note | Acceptance / Conformance Criteria - Where trenching through roads, prior to excavation, the surface shall be saw-cut a minimum of 100mm beyond the trench wall and parallel to the proposed alignment.
a0c13b34-28e9-56eb-8a82-c6e5b95af9ac | note | Standard / Specification - PS 16.9.2.10
cf928557-7adc-596e-904a-56ec05e0b42f | note | Verifying Document - Site Records
4104cdb9-cc9b-500b-871f-c0111fa2e36d | note | Frequency - During Works
d86780b1-d4c5-5e9d-abf9-5e44c4bdd0cf | note | Verification Activity: Activity - S
00ba596c-9795-5d07-8837-a5a71c95e0cb | note | Verification Activity: By - SE
6afb86e1-05de-5ae2-af76-09e9e705fa80 | checkpoint | 3.02.3 - Stability check
47b6fbab-02d3-5836-97ee-8511a70f8f3b | note | Acceptance / Conformance Criteria - Where trenching is near new or existing structures (within 5m horizontally, or where the trench invert is below a plane projected downwards at 1(V) in 2(H) from the base of the structure), a stability check shall be undertaken to ensure undermining of the structure is avoided. The Contractor shall undertake a stability check in these situations.
65869707-4fe2-58ed-b155-b3d7f914ca95 | note | Standard / Specification - PS 16.9.2.10
24b41d81-4dbb-5068-b0b2-ab34686eb8f3 | note | Verifying Document - Site Records
421bc9e6-cc7a-5ae7-9b74-578305ddcb58 | note | Frequency - Each Occurrence
c41ed935-4c7a-5e88-a959-ecb8e593f2cb | note | Verification Activity: Activity - S
7c04dfdc-5014-552b-bdb3-c3c5864e58fa | note | Verification Activity: By - SE
e9ca101b-c573-5a5a-8cd3-20d24be499e4 | checkpoint | 3.02.4 - Trench Width
1382f0b1-e246-5e57-b1b5-bbf95fbb4846 | note | Acceptance / Conformance Criteria - The minimum trench widths are as indicated on Drawing WD-0131 but not less than the external pipe diameter plus 600mm and not more than the external pipe diameter plus 1200mm.
89af5cbd-572b-5da8-bbfe-fa831f19db81 | note | Standard / Specification - PS 16.9.2.10
6fb17de3-604d-5920-99ed-204096c22c36 | note | Verifying Document - Site Records
aed67127-c926-57b1-8a8a-9a6f3d561375 | note | Frequency - Each Pipe
101b3e87-da0a-5028-91fc-d6aaab781a46 | note | Verification Activity: Activity - S
98913d78-758c-5c78-992c-291397a970db | note | Verification Activity: By - SE
58a4d71f-6dbc-5a10-a296-7ed58b085508 | checkpoint | 3.02.5 - Unsuitable Material
c6296427-fd57-57c3-b04f-ea539a1fe192 | note | Acceptance / Conformance Criteria - All material deemed to be unsuitable shall be removed to a depth of 600mm or a greater depth as specified by the Engineer, until suitable material is reached.
c8cac576-c80e-519a-999d-fbe4ecb38f6d | note | Standard / Specification - PS 16.9.2.10
0d96338e-1a5a-56c4-9c36-899cb10f1543 | note | Verifying Document - Site Records
45547264-56db-57ea-8512-83b968e480f2 | note | Frequency - Each Occurrence
d8af951d-38ea-5c47-aec6-e9bc9dd3268a | note | Verification Activity: Activity - S
20405893-728a-5401-a025-cda48715762b | note | Verification Activity: By - SE
ea7ad893-3773-5813-936f-69f88f144761 | checkpoint | 3.02.6 - Trench invert subgrade inspection
bace89a8-4114-5657-81a1-40b92186c5df | note | Acceptance / Conformance Criteria - The Engineer shall have the opportunity to complete a Visual Inspection to NZTA F/3:2010 on the trench subgrade each day on each pipeline during installation.
00ea6f44-a237-5f33-aab0-a38ae488e46d | note | Standard / Specification - Suitability
20479204-28f3-5202-92fd-1ae43a431474 | note | Verifying Document - Engineers Record
c73433d7-959b-5a93-a184-87741fdb7a61 | note | Frequency - Daily
728831df-b427-54c1-a8a4-4f4bd16296c2 | note | Verification Activity: Activity - WP
2c263ad2-49c7-5642-84b3-8f731b614797 | note | Verification Activity: By - ENG
d818a004-d73b-5d9a-b27c-6159bea11363 | checkpoint | 3.02.7 - Trench invert subgrade testing
8b34e583-94dc-5dfb-b119-bd27d6f83fff | note | Acceptance / Conformance Criteria - The subgrade shall be tested for CBR>5 by Scala or shear vane. This test shall be undertaken at the design subgrade level and at a depth of 300mm below the design subgrade level.
08fcbbae-abb7-5e65-b1b2-c4fe011ef492 | note | Standard / Specification - PS 16.9.1.3, PS 16.32.3
95b337db-a279-5b5a-a0c7-27a2721b36bd | note | Verifying Document - Scala or Shear Vane Report
437ab222-615b-5929-9da8-43c25d6a192d | note | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
5a2fadf0-aebc-5245-bc96-3eafea8e905a | note | Verification Activity: Activity - I
dca8baf3-bc11-5d22-84ab-f82af75330a5 | note | Verification Activity: By - SE
270c1a1e-7412-5580-a7d8-4802dc5d53ca | checkpoint | 3.02.8 - Subgrade Undercut and Replacement
4676078b-2efe-5dc6-81cb-0e0a70c92c55 | note | Acceptance / Conformance Criteria - The insitu trench base shall be tested and if CBR is less than 5, it shall be undercut and backfilled with AP65 compacted to compacted to a MDD of 90%
a668908e-2871-52bc-a3c7-42391c06b4b7 | note | Standard / Specification - PS 16.9.1.3
6e6c8c2c-9779-5dc9-bd5a-27df674a3f76 | note | Verifying Document - Site Records / NDM / Clegg Report
378e22fe-6714-51fa-976a-92b94c3fc07b | note | Frequency - Each Occurrence
ee1a250d-8642-5b6d-ac2b-1416d50fd965 | note | Verification Activity: Activity - S
625d8e04-1d03-5fe5-a673-aecd649281f2 | note | Verification Activity: By - SE
81f73ef2-bdc8-5939-aa6d-cff64bb295e5 | checkpoint | 3.02.9 - Pipe bedding and haunch zone inspection
80afe4fd-6f35-59f9-aae3-29e56c3792c0 | note | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe bedding and haunch zone
8f0b796f-53c8-50ac-9132-c77a670c3d03 | note | Standard / Specification - PS 16.32.3
60b5717d-85de-5442-b8a9-bef95f12d06d | note | Verifying Document - Engineers Record
dae45631-30e1-5857-ad4d-6a92517ebf2e | note | Frequency - 1 per trench length (Between Chambers)
bde049dc-34cb-5219-bb69-b986c7ef030a | note | Verification Activity: Activity - HP
3ff31980-c7e1-5278-91d2-473bdcff7c1b | note | Verification Activity: By - ENG
5cf170fc-8df5-5e2c-b092-708051a3742b | signoff | AUTHORITY HOLDPOINT
5814668f-ccd5-5d72-badb-415127e4c7e4 | checkpoint | 3.02.10 - Pipe bedding and haunch zone Density Testing
7780f82b-4990-59fe-a8bc-884f232a201f | note | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The pipe bedding and haunching zone shall be compacted to a MDD of 90%
6cccbd2f-65ba-5ea9-b97a-8c4bb86632a0 | note | Standard / Specification - PS 16.32.3, PS 16.6
2eb44e5d-5e21-5d11-86b9-6530b43ab9b2 | note | Verifying Document - NDM / Clegg Report
641ea46d-f966-5b91-abc5-a0ffcf8610fd | note | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
56dadca6-874d-5d2f-b167-2a5a6ce18b08 | note | Verification Activity: Activity - I
c5d6fc74-488c-57b1-af27-39ac3a5333f6 | note | Verification Activity: By - SE
c03d2694-c46a-5d17-84c5-81dfdcdc396f | checkpoint | 3.02.11 - Backfilling of pipes and culverts with embankment fill - QA Acceptance
54c8cf14-a7e5-56f3-b2a5-031afc96d58b | note | Acceptance / Conformance Criteria - Prior to Backfilling of pipes and culverts with embankment fill the test results for bedding, haunching, side zone, and overlay zone material properties, grading curves and compaction tests are accepted by the Engineer.
556bb476-5c8b-5e81-9d97-402026fc5cfa | note | Standard / Specification - PS 16.37
6f63a7f2-ad23-523a-9aa8-8c354adb37e8 | note | Verifying Document - Engineers Acceptance
163a2091-7069-560a-aeae-aea14f580ae8 | note | Frequency - Prior to Backfilling of pipes and culverts with embankment fill
e3b88e8c-a85b-55ce-8e53-66de6475b952 | note | Verification Activity: Activity - HP
e5489cde-3c63-5f55-816c-9c60ec1bc44a | note | Verification Activity: By - ENG
19a18f40-a4da-5db3-aeba-1eabda497cc4 | signoff | AUTHORITY HOLDPOINT
f8a5db8b-7b9c-5b42-9bdd-2aee0aee659b | checkpoint | 3.02.12 - Pipe laying in Embankments
9333aaaa-bb90-5a92-8fc4-21b56f24ee09 | note | Acceptance / Conformance Criteria - The Contractor shall have each pipe checked for level as it is laid, by a competent technician using an Engineer’s level, pipe laser or other approved equipment. Pipes shall be laid on uniform gradients between successive designated manholes at the gradients specified on the Drawings.
de949b47-e5bb-596e-9340-959a6b481c11 | note | Standard / Specification - PS 16.9.2.8
81d88739-b339-5b45-af6b-cd0cd37dddc1 | note | Verifying Document - Survey Records
7967b6ad-cc3e-50c1-bac5-90d180ab9963 | note | Frequency - Each Pipe
ae552d7c-6f4e-5bd3-92a6-85659f422a67 | note | Verification Activity: Activity - I
50ae43b8-b7f8-58a1-8966-b0ac0ff3fd4c | note | Verification Activity: By - SV
f9ac2429-13b8-58d3-8851-eab84a3fd0e7 | checkpoint | 3.02.14 - Cutting of Concrete Pipes
30041ea1-5673-5c52-a5cd-006cccb974ee | note | Acceptance / Conformance Criteria - Where it is necessary to cut a concrete pipe the pipe supplier should be informed of such requirement specifically where the dimensional tolerance for the pipe is deemed critical.
dfb00597-946b-5992-96c2-1bdbabaf4b18 | note | Standard / Specification - PS 16.9.2.16
acdcf809-4c9d-56c3-aaaa-d8ac32594b5a | note | Verifying Document - Suppler Approval
212d01d3-4f70-56eb-be43-3cc662da4072 | note | Frequency - Each Occurrence
c40e6911-bdab-5cfe-abbe-45ef70d12450 | note | Verification Activity: Activity - S
3835eda0-ea57-5160-b112-c942f617dbdc | note | Verification Activity: By - SE
035129dc-7d0e-5a42-b6fe-5dee75371088 | checkpoint | 3.02.15 - Cut Pipe Sealing
e65c9d26-4d1c-5d84-aa1d-8dfc0f16d611 | note | Acceptance / Conformance Criteria - All cut surfaces, not encased within benching or other in-situ concrete, shall be coated with an epoxy resin mortar in accordance with the manufacturer/supplier recommendations, leaving no exposed reinforcement.
aec9e4ca-b54d-53bb-9102-878cdc4379f9 | note | Standard / Specification - PS 16.9.2.16
99d2b016-c059-5f7e-9ac0-71ba4c2ddadc | note | Verifying Document - Site Records
f55294a3-ad52-5c4f-a1bf-68db916a46b1 | note | Frequency - Each Occurrence
e4b52e80-c90e-578b-9ac0-b43990ecba07 | note | Verification Activity: Activity - S
afd4d60d-0ac2-5818-a90f-71bad8ab5770 | note | Verification Activity: By - SE
e4c33cd6-d38e-587d-aa5c-a623c74935ed | checkpoint | 3.02.16 - Side zones Density Testing
7777ec8b-3bbc-5f47-a3c1-fb31188bf4ba | note | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The Side zones shall be compacted to a MDD of 90%
5309e99a-d68c-5d9d-99b5-c598629cd3ab | note | Standard / Specification - PS 16.32.3, PS 16.6
e428b8f0-4950-5176-9b15-a16d4dccc3da | note | Verifying Document - NDM / Clegg Report
aa408326-72d2-5db2-9779-1f9780278be5 | note | Frequency - 1 per backfill layer per 15m trench length. Minimum of 2 tests backfill layer per trench between pits/manholes
55baa83d-214f-55d4-a515-b2b744d467da | note | Verification Activity: Activity - I
1565a9de-acd7-55a7-bee4-ab67d56d629a | note | Verification Activity: By - SE
3382e817-6a28-577d-8653-2be0f10dfb15 | checkpoint | 3.02.17 - Compaction above Pipe
0f621c95-2add-5163-9e74-674f0236295a | note | Acceptance / Conformance Criteria - Only hand operated compaction tools shall be used until the backfill has achieved a depth of 300mm above the crown of the pipe.
cb8dbe72-2c7e-5a2a-8e84-ac948c72432b | note | Standard / Specification - PS 16.32
5e993aac-af3d-5c0e-b7ba-f7f7d54f8028 | note | Verifying Document - Site Records
68b95351-d29b-59e3-97b6-2cd5e950a0ce | note | Frequency - During Works
ac98194b-42f1-503f-b174-bde1d7e887ca | note | Verification Activity: Activity - S
6cdf8e68-eeac-52a3-b3fd-e8cf26a5a558 | note | Verification Activity: By - SE
51eb3361-8108-503c-8a25-987fd585578d | checkpoint | 3.02.18 - Pipe overlay zone inspection
d759fc60-4644-58f5-bd79-b55b5bd1fb89 | note | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe overlay zone
41f61bb4-c281-5e16-92d2-15f1fa5eab78 | note | Standard / Specification - PS 16.32.3
53c317a1-55ba-55c1-82e1-8fc0cdfe0a82 | note | Verifying Document - Engineers Record
f299943b-7879-52a3-a141-0d281743d90b | note | Frequency - 1 per trench length (Between Chambers)
bd215c41-c17d-5954-9ec4-b311106ae3ba | note | Verification Activity: Activity - HP
cc936f89-e555-5592-a1c5-7752671b456a | note | Verification Activity: By - ENG
bd74d56a-352f-5342-982f-d30a401d4e76 | signoff | AUTHORITY HOLDPOINT
35acfe1b-9d28-5cb4-9eb1-8f3050ddfbcf | checkpoint | 3.02.19 - Pipe Overlay Zone Density Testing
ea4a7c21-2cd6-51ba-89f9-65f4083ee4cd | note | Acceptance / Conformance Criteria - Backfill material shall be built up in layers not exceeding 200mm. The Pipe overlay zone shall be compacted to a MDD of 90%
a786b17d-34ea-57ec-8ba3-7fef24b9424a | note | Standard / Specification - PS 16.32.3, PS 16.6
4b32e01c-ad41-5413-ac29-af993bd155bb | note | Verifying Document - NDM / Clegg Report
9f21ec6a-04d0-5ba8-96f3-1eb9421522e9 | note | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
d93c0d3c-1206-53b2-8982-bb08eccc3924 | note | Verification Activity: Activity - I
50a17376-53cd-53d0-8940-c74e1ab03a05 | note | Verification Activity: By - SE
91558f9b-dbd3-5b49-8a78-7e78124ef5d3 | checkpoint | 3.02.20 - Pipe invert levels/lid levels at all drainage structures
aa555522-51f3-5980-b9d1-c3ab7c1e70fe | note | Acceptance / Conformance Criteria - Pipes shall be installed within 20mm of stated invert level (vertical tolerance) and within 50mm or 5% of the pipe diameter of proposed horizontal alignment (whichever is greater). Catchpits and catchpit manholes shall be located to align with proposed kerb and channel (or dish channel) and finished to be flush with the finished road surface unless otherwise specified on the Drawings.
aad2186f-af8e-5603-95b3-75a2c89579d4 | note | Standard / Specification - PS 16.34.2
a74d5719-acf4-58a9-9d3a-f363807a7440 | note | Verifying Document - Survey Records
0fa9e2a2-80d6-5268-9740-1a0c21764355 | note | Frequency - At the completion of each stormwater pipeline
3147a91c-0253-5526-a0a9-708fe114c933 | note | Verification Activity: Activity - I
03cc8ce8-f6f6-5939-a085-971d4562b8c9 | note | Verification Activity: By - SV
3cbaefad-09bf-5980-99ae-9f82d36421b2 | section | 3.04 Stormwater Structures General
55e0db49-0d55-5fcb-a32c-d06f9e360544 | checkpoint | 3.04.1 - Stormwater Structures Subgrade
7ccab956-c555-5c92-a515-ccd3161b2fa6 | note | Acceptance / Conformance Criteria - A hand Auger Scala / Shear Vane up to 4m deep shall be completed in the base of the excavation and the results submitted to the Engineer. The subgrade shall be CBR>5.
d1c3a282-502d-5571-9cb0-2708c6831439 | note | Standard / Specification - PS 16.32.3
7fb8daab-73b9-517e-9d03-e50aa11e5642 | note | Verifying Document - Scala / Shear Vane Results
37c7858f-1d66-55e1-95e2-8ba4a1fec8a3 | note | Frequency - 1 per structure
ab9c59e4-05af-515e-b1c4-49227fe82f7d | note | Verification Activity: Activity - I
3629fb0c-7009-5d28-a077-787874d9e25d | note | Verification Activity: By - SE
11df0ca5-2244-56ff-87cf-6389bd9bd635 | checkpoint | 3.04.2 - Stormwater Structures Bedding material
48bc291a-2a29-5bc3-906f-3cdac2399e31 | note | Acceptance / Conformance Criteria - Stormwater Structures Bedding granular material shall be compacted to MDD of 95%.
c46f0835-2b13-58d9-99e7-d82b75d1a056 | note | Standard / Specification - PS 16.32.3
b42f32fc-9bfa-5fb2-be62-057e44830231 | note | Verifying Document - NDM Results
29fd4438-97bd-5577-b172-a518d3a3a8bd | note | Frequency - 1 per structure
c62da838-5b40-56be-8866-a002ab4b97fa | note | Verification Activity: Activity - I
720c64e6-0ca3-59a3-8768-96eb4f76fe64 | note | Verification Activity: By - SE
edf4ceda-4a42-5d83-8430-f5df17c20e6e | checkpoint | 3.04.3 - Stormwater Structures Backfill
b34f1f7f-0938-5b21-a47f-6db328924c17 | note | Acceptance / Conformance Criteria - Stormwater Structures Backfill granular material shall be compacted to MDD of 95%.
d1c7cb98-8641-5341-994b-ea4470308fdd | note | Standard / Specification - PS 16.32.3
75e64ac6-029b-5e7e-ab2f-6d62438d5624 | note | Verifying Document - NDM Results
6f6b8403-ddb8-5d40-adf1-d4cc9f2ef858 | note | Frequency - 1 per backfill layer per structure
296e6018-bc51-5a85-a578-f14fc5cc21f8 | note | Verification Activity: Activity - I
15cce95e-fa47-5c7b-9032-921bd70bd231 | note | Verification Activity: By - SE
c39c3e78-c1aa-5dca-a3f5-3c587c96df60 | checkpoint | 3.04.4 - Subgrade Clay
ae0091af-8c0c-52cc-b75d-a35fa3f76837 | note | Acceptance / Conformance Criteria - If clay is present at subgrade level, then this should be supplemented with soaked CBR laboratory testing.
1db22515-8d3a-56b7-9dd8-77f0a46019d5 | note | Standard / Specification - PS 16.32.3
77029148-a510-56dc-88d6-c28059422f6b | note | Verifying Document - Soaked CBR
36143a61-3eec-534e-99a7-55ac2d9cbd59 | note | Frequency - Each Occurrence
eb3dbda9-3677-5a19-b28d-7e491ed5f611 | note | Verification Activity: Activity - I
a881e587-2b20-553b-9123-49e3bdebae1b | note | Verification Activity: By - SE
772516f7-046e-5c6f-aac8-fb5becb92a72 | checkpoint | 3.04.5 - Culvert CBR Approval
3c258f69-f678-52f7-9913-42fb49154f2e | note | Acceptance / Conformance Criteria - The contractor is to provide CBR testing of trench subgrade prior to placement of bedding and laying of culverts.
0c978519-93f2-565e-aad6-832f7c252596 | note | Standard / Specification - PS 16.38
f26024b5-c24c-542e-9adc-b46f6a06d840 | note | Verifying Document - CBR
414b1fad-73e1-5bc8-9d59-9cbde223fa67 | note | Frequency - Each culvert prior to bedding
8a7c2686-1478-51dd-8a5f-b6ead3cfc667 | note | Verification Activity: Activity - W
b311b341-d8a7-57cf-9f2a-03a65b60768f | note | Verification Activity: By - ENG
2b11378f-fb1e-5ce9-90ee-5cf3efd04f03 | section | 3.05 Catchpits (Structure)
31ff3eb2-aa65-5635-a88d-3fd640cbd3bf | checkpoint | 3.05.1 - Catchpits Base
7c12f643-54cd-5642-b419-a60cb10f0a3d | note | Acceptance / Conformance Criteria - Catchpits shall be constructed on a compacted, on top of a 150mm layer of compacted AP65 or GAP100 granular material.
4d7a6880-94e2-5dd5-87c5-acf5d37d6788 | note | Standard / Specification - PS 16.10.2
cfd7a3fa-c030-5be5-902f-e19786facbfe | note | Verifying Document - Site Records
3b50728b-9859-55b4-a133-214b3d0fd973 | note | Frequency - Each Catchpit
eb439e00-b472-5d4e-b1b9-909647a050e9 | note | Verification Activity: Activity - I
b97ed336-e7f3-586a-b7a9-76d5e23c013a | note | Verification Activity: By - SE
ec26eee7-2ffc-5274-9a64-37128cd44b24 | checkpoint | 3.05.2 - Precast Catchpit Sealant
caca2619-e854-52de-8466-ceb7c1b17f08 | note | Acceptance / Conformance Criteria - All joints between segments of precast catchpit risers shall be sealed with ‘Black Butyl Mastic Sealant – Hynds (MSR)’ or similar and approved.
5662f1dc-68c0-57c4-96a2-ab8b3cf29981 | note | Standard / Specification - PS 16.10.2
e3491805-ebf4-5a7d-9d6a-768e20f967dc | note | Verifying Document - Site Records
c1b760af-fdbc-54d1-ac9d-473503e15ed1 | note | Frequency - Each Catchpit
74fda00c-9175-57e9-9e72-c326c6f42529 | note | Verification Activity: Activity - I
5b4fd898-b0e4-573a-8f1c-5faacd3f59fd | note | Verification Activity: By - SE
feb0a3cc-ec88-5255-a059-11b948c8cfc2 | checkpoint | 3.05.3 - Catchpits Grates
f3063c57-e226-5f54-b6f3-63ee891fca10 | note | Acceptance / Conformance Criteria - Cast-iron grates and frames shall be set no more than 30mm lower than, but parallel to the cross fall and grade of the surrounding, finished pavement surface level. All grates and frames shall be haunched to lids.
afa108f9-36ee-549b-bee0-84858cac3fcb | note | Standard / Specification - PS 16.10.2
b9715cd7-3ddd-56a3-84b7-03434604bcda | note | Verifying Document - Site Records
db7af4b0-2966-5b17-8edb-d0fce08bab3b | note | Frequency - Each Catchpit
833ad2d4-0f3d-5158-98a3-cef60fb2b875 | note | Verification Activity: Activity - I
2a0daae5-4037-56fd-bb23-56fb57cd2535 | note | Verification Activity: By - SE
20499adb-cd8d-52ad-9503-f7ac36d5126e | checkpoint | 3.05.4 - Catchpits Sumps
82783ac0-0a33-54c7-926b-fb0accf22531 | note | Acceptance / Conformance Criteria - Catchpits must have sumps at least 450mm deep (below the invert of the outlet pipe level)
f07874f5-809f-5857-9ca1-dde377bad4d0 | note | Standard / Specification - PS 16.10
9811e13a-60c2-55cf-a626-05c28b8da90c | note | Verifying Document - Site Records
ba27d4c4-4877-5b94-adc6-c5dec1860b9e | note | Frequency - Each Catchpit
1cb8192a-31f2-5be6-afba-3ce6e4f421b0 | note | Verification Activity: Activity - I
09a245a3-b6ff-5b78-92c9-f795fb912fe6 | note | Verification Activity: By - SE
38a69e92-eb03-5781-babf-63bafa6f0463 | checkpoint | 3.05.5 - Catchpits Inlets
8fc438ca-6594-5b52-84ee-1bbf3c7d5221 | note | Acceptance / Conformance Criteria - All catchpits receiving stormwater from the highway shall be constructed with a back-entry inlet.
19206e38-5252-55d9-b766-ed46b3f4d212 | note | Standard / Specification - PS 16.10
617f5fe4-08cd-56a5-a9ed-2e6d64437fc2 | note | Verifying Document - Site Records
60babfde-8a7b-5821-876e-365eb6628c75 | note | Frequency - Each Catchpit
e16b2f58-8955-55e7-b3f8-a0bf1c481028 | note | Verification Activity: Activity - I
783f76e9-2b93-5db0-845f-1e21c8d64c5c | note | Verification Activity: By - SE
fbfd030e-e726-5b00-b683-815353d7d8ec | section | 3.06 Manholes (Including Catchpit Manholes)
4ea6a7a4-33ae-5695-82f6-c7b9a7aa7caf | checkpoint | 3.06.1 - Manholes Base
3a9e6f0e-79b8-5d80-afa4-286e1327281d | note | Acceptance / Conformance Criteria - Manholes shall be constructed on a compacted, on top of a 150mm layer of compacted AP65 or GAP100 granular material
f493d2b6-4b01-51c7-b4bd-b7b5abee8966 | note | Standard / Specification - PS 16.15.2
dec3f19d-bd7b-5bc5-98a6-18340d74e6bb | note | Verifying Document - Site Records
8c10f297-d8b6-58b1-b0cc-b291908bb792 | note | Frequency - Each Manhole
4e07cb12-774d-5d74-a75c-a7a17318ca90 | note | Verification Activity: Activity - I
acae7bce-bc0e-5278-b5d3-4c2c81856ed9 | note | Verification Activity: By - SE
830ba5c3-5241-5f8c-9d26-aee2aa04121a | checkpoint | 3.06.2 - Manholes Sealant
1d507ef0-acca-5a43-88c4-d1acd676ce68 | note | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
4e2dce2e-e2b4-5031-8fb5-21ac1c0128fa | note | Standard / Specification - PS 16.15.2
c412922a-19eb-5c79-8071-400b7df951fd | note | Verifying Document - Site Records
c51f6de7-834a-56e4-aa11-a45cf597f87d | note | Frequency - Each Catchpit
89e41216-5fc5-5a4d-ac7b-b6e80627fabe | note | Verification Activity: Activity - I
fc8b90cb-5fbb-5cad-8ac4-af7ffe5f9e7b | note | Verification Activity: By - SE
65a61540-a274-5c95-993e-1bca70d687a4 | checkpoint | 3.06.3 - Benching
f95c7681-49b8-5df2-b050-183c6406024a | note | Acceptance / Conformance Criteria - Benching is required in all manhole structures unless noted otherwise on Drawings. Benching shall be 20MPa concrete and to a F4 finish. Manhole benching shall accommodate pavement subsoil drain connections where required.
1d794a62-7c5d-58c5-9714-015fe298b28c | note | Standard / Specification - PS 16.15.2
3347e862-c03a-52ab-9d9c-2a79228848a4 | note | Verifying Document - Site Records
f42162ea-77b6-5c48-9a5b-721d72594dc3 | note | Frequency - Each Catchpit
f2fe82f9-8dbd-5b31-ab79-7f8fb6e8871b | note | Verification Activity: Activity - I
f60e390e-e985-5b3e-8d40-dac7c9c4ecff | note | Verification Activity: By - SE
1b2b7647-ea00-550b-94b6-c3eb86c1e5af | checkpoint | 3.06.4 - Benching Fall
0cac811e-75f9-532a-b09c-a44cad9229f8 | note | Acceptance / Conformance Criteria - All side benching shall be formed with a fall towards the channel unless otherwise stated.
1097b43a-3ffe-57df-8568-ead8070fa6a4 | note | Standard / Specification - PS 16.15.2
74262943-c30c-56a4-bafb-64db4aae0de9 | note | Verifying Document - Site Records
b34fb4dc-ca10-5c46-a515-a7a0d16dec8e | note | Frequency - Each Manhole
f813fdc6-8eaf-51ae-b92e-d3902ff8bcf9 | note | Verification Activity: Activity - I
0360d584-5bab-5633-8f8f-c65954b27c4b | note | Verification Activity: By - SE
e2634fcd-64bd-5c88-986a-591133456f83 | checkpoint | 3.06.5 - Sealant
21cb44f5-1153-5b62-90ee-b4948ae6730a | note | Acceptance / Conformance Criteria - All pipe work penetrations through manhole walls shall be sealed using Epoxy Mortar or an approved equivalent type of permanent sealant.
3cc3eb22-7813-530f-8aa5-6ae338830655 | note | Standard / Specification - PS 16.15.2
59ebae16-ebd8-56f7-aa02-b87e2ef8cba1 | note | Verifying Document - Site Records
58e9733d-3a89-5204-ae3f-36a29763d73e | note | Frequency - Each Manhole
7e94f9b2-5165-5c4a-9957-f9bb127a161b | note | Verification Activity: Activity - I
7a9c04a4-d06b-559d-97ec-c27fb6692cc1 | note | Verification Activity: By - SE
011d016c-aafb-54b9-b1eb-bc32a59107a7 | checkpoint | 3.06.6 - Lids
7aa78c8f-122b-5ccc-917d-ff44c192c11c | note | Acceptance / Conformance Criteria - All solid cast-iron covers and frames shall be set flush with the cross fall and grade of the surrounding finished surfaces. All grates and frames shall be haunched to lids.
46ea94c0-a704-5d95-8387-8698484f51c9 | note | Standard / Specification - PS 16.15.2
1f3bc0d6-5be8-5873-a9e9-c6544a416ebe | note | Verifying Document - Site Records
f608c04d-9e1c-5bfc-a52c-999da51bef95 | note | Frequency - Each Manhole
7aa68f92-8526-588d-ab62-c690abfab4e3 | note | Verification Activity: Activity - I
f5d7d1b6-2b8d-579b-933c-8545e4c06196 | note | Verification Activity: By - SE
f97987d2-2d57-5b5c-a4fd-287d395bce0e | checkpoint | 3.06.7 - raised cover levels
df0a6082-b5e9-573c-a1eb-4417756b2a91 | note | Acceptance / Conformance Criteria - For new or existing manholes with raised cover levels, the height of the manhole access shaft (throat) shall be no greater than 600mm where access is required (all non-catchpit manholes). The shaft and any subsequent extensions to the shaft shall be constructed using either:
ef266951-f763-5fac-9123-b81939b21d05 | note | Standard / Specification - PS 16.15.2
82e191ee-3427-5ad3-a704-000251cc0625 | note | Verifying Document - Site Records
1cd684fd-7259-59b4-a745-bc1f6cf2f01f | note | Frequency - Each Manhole
ff52b000-0775-509f-9955-80514ffdb205 | note | Verification Activity: Activity - I
64c3f6d9-b360-539d-9a0f-8f406ab46004 | note | Verification Activity: By - SE
137e9184-dbbb-5055-85de-4e13f31d3b5e | checkpoint | 3.06.8 - Adjust Manhole Service Lid Covers
391775e4-fd9b-56c6-9f3f-159ce096b096 | note | Acceptance / Conformance Criteria - Following adjustment, the service cover shall be firmly held in place and shall not be 5mm higher or 0mm lower than the adjoining surface. The item shall cover adjustments + or – 300mm from the original height. Any adjustments exceeding these measurements shall be treated as a variation.
04334fc2-b281-51f3-8aa9-0a76cf293552 | note | Standard / Specification - PS 16.12.1
57287e33-c31e-55c1-a5d0-8ae74216966d | note | Verifying Document - Site Records
f5b7ab8b-269a-54a7-bfc3-75ff06b220c5 | note | Frequency - Each Lid
ccc852a1-41d3-5d1b-90e4-f782f972d478 | note | Verification Activity: Activity - I
963627e5-207a-51ad-9868-852410b6cc08 | note | Verification Activity: By - SE
2a566367-4568-59ef-8af5-b33af6cd82fd | checkpoint | 3.06.9 - Visual inspection of all Manholes
3e9bb3c2-f553-5292-961f-29cdcd544bae | note | Acceptance / Conformance Criteria - 3-6 months following construction, Each manhole shall be inspected. No evidence of identifiable flow infiltration, settlement and riser displacement or cracking shall be present
867b6da2-0105-570c-9e45-1e84db38098a | note | Standard / Specification - PS 16.34
c7293857-6920-5d24-95cc-56b8befaa828 | note | Verifying Document - Inspection Record
a0f5bb33-714b-5902-87e6-be5fdf9607a1 | note | Frequency - Each Manhole 3-6 months after Construction
d8c8ada0-1f73-5c3b-ad64-707803459d6d | note | Verification Activity: Activity - W
505eb47b-c74b-5bcb-985d-8f81b9bac215 | note | Verification Activity: By - ENG
27774e0c-99d7-5289-8467-16e09dd355ec | section | 3.07 Headwalls and Wingwalls (Structure)
a282b859-9ba8-5309-ac5f-cce9472c84c2 | checkpoint | 3.07.1 - Headwall Bedding
2bab5ccb-3cbf-57f6-8710-b2459902c1f5 | note | Acceptance / Conformance Criteria - Headwall aprons shall be constructed on a compacted, 75mm bedding sand underlay by 150mm layer of AP65 (or similar material as approved by the Engineer) granular material and compacted to a MDD of 95%.
91063004-0b29-50ff-b05e-821158bec0e8 | note | Standard / Specification - PS 16.13.2
82b3bf69-61dc-5cf6-bca7-7e387c6379ff | note | Verifying Document - NDM Results
b73fe472-3c42-5813-8fba-89f17bab39ba | note | Frequency - 1 Per Apron
8881594f-1fb1-5b9f-afa7-d37ce5091875 | note | Verification Activity: Activity - I
94340d61-1416-52e1-b978-f8650ee0935b | note | Verification Activity: By - SE
07fc3567-164c-5618-a44d-5368bfd158b2 | checkpoint | 3.07.2 - Precast and Cast in-situ Headwall and Wingwall tolerance
21f8fae2-c3f3-5adf-86e0-7393a663a12e | note | Acceptance / Conformance Criteria - +/- 10mm variance to vertical design set-out
5a5687cc-6e9a-5bce-93d6-38d9dd154e4f | note | ○ +/- 10mm variance to horizontal design set-out (values in accordance with NZS 3109: 1997)
86b8dbec-1541-5da5-8190-ed28920688b4 | note | Standard / Specification - PS 16.34
208c6c08-ec71-5a1d-9d54-701f09fcccae | note | Verifying Document - Survey Records
dc7f4cf0-5888-52fd-b014-035b78fea0ba | note | Frequency - Every Unit
e0a4a3b7-1c85-546d-80f0-d3d5193a7762 | note | Verification Activity: Activity - I
0f5c6158-e8c4-56c2-ada6-733e98d3831c | note | Verification Activity: By - SV
8068364e-520f-5fd0-991b-16023b2271ec | section | 3.08 Stormwater Concrete Capping (Pre Pour)
bd69386d-659e-5519-93df-1bd1697fd818 | checkpoint | 3.08.1 - Construction Joint Locations
5f47460c-17f6-5a16-82a0-d5da69d96d71 | note | Acceptance / Conformance Criteria - Proposed location of construction joints to be submitted to the engineer for review prior to concrete pour.
bcdb9380-87ba-5b77-b134-cff7009c664a | note | Standard / Specification - Downer
7fcaf1be-2e8f-59fa-94fc-5a7bc498d040 | note | Verifying Document - Approval
f2cbab80-916f-5bf8-8fcd-14e744ff2e5e | note | Frequency - Prior to Pour
592d2188-3269-5697-a6c3-acbbf70737b1 | note | Verification Activity: Activity - HP
8b4c3044-7670-510a-9877-2fb346213beb | note | Verification Activity: By - ENG
1885b19b-fd69-523f-9265-6ecd08f19429 | signoff | AUTHORITY HOLDPOINT
f50d5944-adee-5c53-805f-e43deb1cbcd6 | checkpoint | 3.08.2 - Dry Pack Mortar
bc415a1b-696b-5a55-8143-ab5c161a66d0 | note | Acceptance / Conformance Criteria - Dry pack mortar where specified on the drawings shall be places as per the manufactures instructions.
3497142d-f243-5a8d-9be2-ce7568b448bc | note | Standard / Specification - Downer
f99c52e3-5888-5a4b-9bce-7354556879ec | note | Verifying Document - Pre pour
4c63d7de-d2f6-5dcd-a6c9-650d45058db5 | note | Frequency - Before Works
0a914d3b-42c3-54b9-9825-3359f3ae4990 | note | Verification Activity: Activity - R
53ee03dd-1ade-5cad-b017-c44bc5b48127 | note | Verification Activity: By - PE
7ddf1616-1eae-54b1-afaf-a7dbaf19d051 | checkpoint | 3.08.3 - Reinforcement Pre Pour Inspection
42a17dd3-d295-5d6b-b380-447c658db28e | note | Acceptance / Conformance Criteria - Handling, Fabrication, Placing and Fixing shall be inspected prior to pouring concrete.
2af99b23-dbfe-5ed0-87c8-ce749b036717 | note | Standard / Specification - Downer
9affa3d5-1486-542b-a9d2-ee8d51017ec7 | note | Verifying Document - Pre pour
3e50e346-575b-5748-b476-67754d8ebc63 | note | Frequency - Each Pour
0a3b6477-fa0a-57c6-9aa7-d4438541a7ae | note | Verification Activity: Activity - R
2384d2d0-d928-537a-bf85-fd5f2a402d49 | note | Verification Activity: By - PE
49afaa9c-fcb3-541e-a838-fe0a90e77ca3 | checkpoint | 3.08.4 - Pre-Pour Inspection
0c8f35e6-f474-5ea8-aed5-1ded1a659a16 | note | Acceptance / Conformance Criteria - Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area.
070abcb2-7bf3-5d84-9c6f-33dcd92c65fb | note | Standard / Specification - Downer
66acced7-8b9f-5989-9f56-a0091a8b6302 | note | Verifying Document - Signed Pre-Pour
7b32fc0c-01de-5596-9243-19fd69a3df18 | note | Frequency - 48 Hours Notice Prior to Each Occurrence
e788a677-e575-56ea-983a-c85f93bb281d | note | Verification Activity: Activity - HP
43366cc7-9dd2-5ad0-9fe0-3fca307e02b1 | note | Verification Activity: By - ENG
bc0f02e9-b1ca-53bc-ac57-244188125592 | signoff | AUTHORITY HOLDPOINT
bbd94df5-4b0f-53f6-ae1b-aa72bd251ca6 | checkpoint | 3.08.5 - Delivery Dockets
02b4606a-efbc-5629-abaa-968be95213fb | note | Acceptance / Conformance Criteria - The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size.
631c12cb-2d6f-508e-ad19-e9a7ce9788ae | note | Standard / Specification - Downer
3b998771-c19d-5c84-8f0b-40cc49fe060a | note | Verifying Document - Dockets
7fb6e36c-ba86-57a3-bf57-d0765b07e8eb | note | Frequency - Each Pour
4395b7f3-7ead-58ed-82e6-d5fb8519306b | note | Verification Activity: Activity - R
425eee7d-b0ef-505b-8ff7-088d243ed20b | note | Verification Activity: By - PE
4279327e-59cf-5451-83b7-3515969e2984 | section | 3.09 Stormwater Concrete Capping (Post Pour)
033f68b5-19da-576d-ab6c-0e1322ff0d66 | checkpoint | 3.09.1 - Post Pour Inspection
40c46004-a0d2-55b3-a8b8-8c3b33037ae3 | note | Acceptance / Conformance Criteria - Following the concrete pour, the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
411daf79-3c25-57cf-ae76-78628629977e | note | Standard / Specification - Downer
a3e75254-9229-55f5-9653-09df3c558c89 | note | Verifying Document - Post Pour
78ab019f-3d34-52c5-b593-b4913cf5aa03 | note | Frequency - Each Pour
fb8ec1e5-57ab-53d6-b80e-f7c853b534f4 | note | Verification Activity: Activity - R
ed99a297-8f95-516f-8e5f-18f02a31ff66 | note | Verification Activity: By - PE
4f83fc6d-7c13-5e0c-8101-fc7d013048d1 | checkpoint | 3.09.2 - Construction joints
3eef2fc6-cb15-5b10-8ec5-92adcf30affc | note | Acceptance / Conformance Criteria - Construction joints shall be placed as per the drawings / agreement.
c4fe7329-89d1-5b92-97fb-946425b4de35 | note | Standard / Specification - Downer
8c200ebd-8252-5998-a899-76c41ab70a2e | note | Verifying Document - Post Pour
7109bee6-d043-51e5-9868-872c9082099d | note | Frequency - Each Pour
bbcc0d1b-9163-541c-8742-77a41ffea878 | note | Verification Activity: Activity - R
0e00c0a9-2e62-57ed-90f3-3b3db0efe016 | note | Verification Activity: By - PE
7bf1ae95-4187-5f9c-ad6a-07e234d10d2b | checkpoint | 3.09.3 - Defective Concrete Finishes
a826d68e-d3e9-5374-b462-7f774e9b20f6 | note | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
79d88ba9-d28a-5aa0-8420-589301486a67 | note | Standard / Specification - NZS 3114
51411ba0-df15-5afa-9058-69a514ce4bff | note | Verifying Document - NCR
5178402c-3803-58ae-9609-e3477c92a417 | note | Frequency - Prior to non Minor Repair
0c46167d-50f4-5af7-81da-627189c701b5 | note | Verification Activity: Activity - V
fab78af2-0726-52ba-b6d3-5e0ca7dceb51 | note | Verification Activity: By - SE
9677155b-1567-5603-9058-10b8155b0cfb | section | 3.10 16.35 CCTV Inspections
148112e0-6cfb-504e-8565-c9c49eeea73b | checkpoint | 3.10.1 - CCTV stormwater pipe
9b110b3d-b14a-500b-9f70-6bfee2d47466 | note | Acceptance / Conformance Criteria - Every stormwater pipeline 300mm and greater shall be inspected by means of CCTV camera at the completion of each pipe trench backfill and compaction and at the completion of Earthworks operations (or at a time otherwise agreed with the Engineer).
33ba4a54-0d0b-549a-803e-2113e2b980a5 | note | Standard / Specification - PS 16.34, PS 16.35.1
a10ba199-9940-51e5-bd48-fcffc08e0e56 | note | Verifying Document - CCTV Video and Report
e7ec6065-f0ef-5743-8684-aa5761cd04e3 | note | Frequency - At completion of pipes laying, backfilling but prior to final surfacing (Pavements, etc.)
c4d739e9-d404-5135-9f86-101444ebec1c | note | Verification Activity: Activity - I
6da0e0e0-2b67-5a23-be2f-a5acbdabd9f5 | note | Verification Activity: By - PE
1bb8f0ef-71a1-5083-bde8-eddaaedae0da | checkpoint | 3.10.2 - Pavement Construction CCTV Review
856f1831-3c20-5a03-ade3-5bb0c01dbeba | note | Acceptance / Conformance Criteria - Prior to pavement construction, The Contractor shall submit the pipe condition inspection report to the Engineer for acceptance. The pipe condition inspection report is to be based on CCTV for all pipes upon completion of backfilling the trench.
29ebfdb2-81c5-5080-8628-ddd2129a1380 | note | Standard / Specification - PS 16.37
b096192c-aecf-5fcf-9c3b-abf79330ef6c | note | Verifying Document - Engineers Acceptance
227d49f2-89ee-5142-aed3-b693f5bc28e4 | note | Frequency - Prior to pavement construction above Stormwater pipelines
da035812-d13b-5178-b416-e457d43c05cc | note | Verification Activity: Activity - HP
587f0ad7-ea70-570a-b2ad-7682d65e9ec1 | note | Verification Activity: By - ENG
c99c9d00-0420-58fe-b549-3dcfcc6d3958 | signoff | AUTHORITY HOLDPOINT
d25444e5-96eb-541b-becc-59f2adbdde88 | section | 3.11 As Built Records
2424709a-58b3-5a56-8303-6a65e7fc6226 | checkpoint | 3.11.1 - Survey Requirements - Stormwater Systems - Underground:
c597a341-c1b0-5fb6-bd9b-1b8e6bc1c3d0 | note | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings.: Trench invert. Pipe/structure bedding and backfill compaction. Pipe/structure size, class, alignment, and level. Manhole and catchpit position, levels (lid and inverts). Outlet structures including position, levels, erosion provisions and fish passages.
178957d6-1815-56b9-8eec-b2ed2bbe4cff | note | Standard / Specification - PS 16.33
a470446c-240f-5e87-a0bc-9a7dfe0076f2 | note | Verifying Document - Survey
85b7f2fc-fca9-5599-954d-88a20587b9a6 | note | Frequency - All underground Stormwater Systems
297aa355-398b-5be0-87c3-36edee67c577 | note | Verification Activity: Activity - I
c1bef070-6ad4-58dc-b8ed-62f707bf1462 | note | Verification Activity: By - SV
d9c444fd-5ffe-5265-81e4-16abd7347357 | checkpoint | 3.11.2 - Survey Requirements - Stormwater Systems – Above ground:
54850b2d-ac5d-5b3b-8ff5-cfa01879fe43 | note | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings: Treatment swales, wetlands, basin’s location, profile and grade. Diversion Drain location, profile, and grade. Trench excavation and invert. Line, levels and grade of kerb and channels. Rodding eye locations.
cf027f9f-d387-570b-80d6-c9c7a1996470 | note | Standard / Specification - PS 16.33
ce1e0489-3673-55e7-ab1c-47486e9ecb0c | note | Verifying Document - Survey
bba38cb5-4871-5fa6-829b-1af2c5118f4f | note | Frequency - All above ground Stormwater Systems
4f3331d3-fc36-58e6-aefb-4483ee8174ec | note | Verification Activity: Activity - I
d6f5d537-2878-5e6a-be62-f8c7ba769148 | note | Verification Activity: By - SV
20e6bebd-4ed2-4b81-839d-21280f9a0ea7 | section | 3.12 HDPE Pipe Materials
dda286d8-7d29-4296-a053-3ae99972251b | checkpoint | 3.12.01 - PE Pipe
48142e24-955e-5812-a7d4-eeba26ac1609 | note | Acceptance / Conformance Criteria - PE pipe is required to comply with AS/NZS 4130 and be PE100 or PE80B plain wall with an SDR as shown on the drawings, but no greater than SDR17.
72ebd30c-71c8-512a-a2f7-f8c2d6d975e7 | note | Standard / Specification - PS 16.28.3
85bbb74f-7654-5b39-b167-ed4e1d06eb61 | note | Verifying Document - Datasheet
77cd10b7-8a31-55d4-937e-711721f69800 | note | Frequency - Prior to use
f45a456f-a9c2-53eb-a690-6f2c0c6a7353 | note | Verification Activity: Activity - R
0559749c-9d09-5af2-9995-8fcdffa7541c | note | Verification Activity: By - SE
5d2c3207-3642-4da4-9d6a-b2c967e76321 | checkpoint | 3.12.02 - PE Fittings
9cd725b5-dffe-5131-b899-b1d34846c103 | note | Acceptance / Conformance Criteria - PE fittings must be manufactured in accordance with AS/NZS 4129 and be the same class and pipe material as the main pipe.
3e8bbb5a-274e-5d58-b2e4-bccf1a22e578 | note | Standard / Specification - PS 16.28.3
ce1f4f2e-1743-5406-bd33-1382fd3a8f7c | note | Verifying Document - Datasheet
d2635d51-6322-5ed5-9615-ee57affc6e84 | note | Frequency - Prior to use
43ba9033-0ed1-591e-8c28-b3ff6641dd04 | note | Verification Activity: Activity - R
7446ddbf-bb49-5564-a85a-ffad3eea2bb5 | note | Verification Activity: By - SE
6c0461bc-535e-4384-b6f0-939a6ee680f6 | checkpoint | 3.12.03 - Electrofusion Couplers
fc3dd1b2-8f15-5a51-94d0-470efad07c7b | note | Acceptance / Conformance Criteria - Electrofusion couplers must comply with AS/NZS 4129 and be minimum PN16 pressure rating.
add93445-f15b-5893-bf4b-6663950f7f03 | note | Standard / Specification - PS 16.28.3
c56d4a20-c3df-543a-b97c-c58384c5d5fb | note | Verifying Document - Datasheet
8cec3378-88b4-5520-bfbf-e98030ff5b08 | note | Frequency - Prior to use
8a31ed8d-ef47-5777-98e0-d935d8ae2d44 | note | Verification Activity: Activity - R
63bd3cc5-1d76-5c72-9daa-3e37efb173b4 | note | Verification Activity: By - SE
16690a25-3ea7-4f53-8077-a2095f402ffb | checkpoint | 3.12.04 - PE Fitting Flanges
924b351f-0f4f-5dbd-9179-75ed300f6661 | note | Acceptance / Conformance Criteria - Flanged connections between PE pipe and metal fittings (e.g. cast or ductile iron flanges on valves, spools, bends, etc) are to be made using PE stub flanges, full face gaskets (Tessnit or Klinger or equivalent approved by the Engineer), 316 grade stainless steel backing rings, and 316 grade stainless steel bolts and nuts.
753344c4-4b5f-59ef-8c60-0059e6066394 | note | Standard / Specification - T-EES: 04311 - 2.3
b7dbc142-beb3-5c15-b20d-395d1cca4b0f | note | Verifying Document - Datasheet
af08fc65-73c2-5832-8be3-412c1dfebd8f | note | Frequency - Prior to use
7a54005b-8250-5c9b-89eb-5fadcd759254 | note | Verification Activity: Activity - R
3a3e6a00-7ec4-57f3-862b-5a6c06454fba | note | Verification Activity: By - SE
31cecad0-628d-4eaa-ac6d-e5bf9f9c1b3e | checkpoint | 3.12.05 - Denso Tape
ffb98532-3fa2-5553-88e8-cd667b267637 | note | Acceptance / Conformance Criteria - Denso Tape (or equivalent) shall be used on buried flanged fittings
10980ff2-89ea-5340-9546-ac73c8b54bc2 | note | Standard / Specification - T-EES: 04311 - 2.3
d2f4c04e-b723-54b0-9c44-ad5a93896402 | note | Verifying Document - Datasheet
2df8d43b-b30b-5a0d-bbd7-7a9dcc4b4dd1 | note | Frequency - Prior to use
3c56dac3-444a-5f8d-b98a-bcd358f81e10 | note | Verification Activity: Activity - R
c922ed41-2417-5ab3-82a0-77b90e861f66 | note | Verification Activity: By - SE
4dadab66-1c4e-4122-bcbd-c216b0fc14eb | checkpoint | 3.12.06 - Grout
354c0029-dd0a-5540-8571-d643b013402e | note | Acceptance / Conformance Criteria - Grout must be 1.5 MPa flowable concrete. The grout must be compatible with the pipe material and must have a service life matching the new pipe.
21ce0b5b-a0b5-5563-926d-a5b663c43bf1 | note | Standard / Specification - PS 16.28.6
6452e849-5730-5a05-b88a-00898c8eb6e5 | note | Verifying Document - Datasheet
7a11676a-9d0c-5f20-bb5d-711364675e3b | note | Frequency - Prior to use
6fd48873-1f73-56ca-8733-813d24658667 | note | Verification Activity: Activity - R
b2831d4c-433d-5574-882a-4d4f3b316bfd | note | Verification Activity: By - SE
| checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
| textbox | Contractor's Rep Name:
| textbox | Engineer's Rep. Name:
| date | Date:
| signoff | Add Signature