## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | DN1210-012 ITP Utilities Rev 1 | itp | DN1210-012 ITP Utilities Rev 1
8e916c0c-5850-4ca0-aad3-d295c9619403 | section | 1. PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 1.1 GENERAL
4a66bb89-4063-48d7-ba64-2c8f3122a315 | checkpoint | 1.1.1 - Trench Profile
0bcb6d66-7e1e-522d-ba87-be9b0db6f981 | note | Detail - Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes.
67dc9f3e-9171-50cf-b1b6-87fec1d0c3a6 | note | Acceptance / Conformance Criteria - Survey Set out
dd78f3e2-e03d-5227-a645-a1acee11c522 | note | Standard / Specification - PS 25.13.2 a (1)
40ba78fc-9e73-52b2-a54a-f9029e66caf3 | note | Verifying Document - Survey Data
20d912dd-83fb-52e2-b2fc-f85bf0271bb6 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
9abec1dd-c417-52ff-a7dd-f5c2e029111e | note | Verification Activity - H
f2dfcbc7-c870-5849-aeca-006cd2d2d0c7 | note | By - ENG
d7f561a4-3e32-4b1a-9982-23753a93830f | signoff | AUTHORITY HOLDPOINT
25425128-8231-4e6d-aa60-7136a71593a6 | checkpoint | 1.1.2 - Underground Services
283dd870-0601-52e4-855c-ca1a319e14fe | note | Detail - Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer.
e9093ccf-6692-5b86-aa60-478a2d8764e6 | note | Acceptance / Conformance Criteria - Survey Data/Existing utilities Drawings
c178e828-e156-5366-98fb-7c2b3ee5879b | note | Standard / Specification - Appendix V
afa0302e-7ad5-5f89-980f-717933ab154f | note | Verifying Document - Survey Data
999d0726-1342-5992-bf08-3221e0b8ecb8 | note | Testing Quantity Required (based from schedule qtys) - Prior to Construction Review existing service location drawing supplied by WSP.
5195c12a-66bf-5ab3-be01-01228c27e530 | note | Verification Activity - H
917c7757-35c5-53a4-b610-1d5f602e77cd | note | By - PE/SE
af7a8933-9e5a-48a0-a05a-129fd15c5cc9 | signoff | AUTHORITY HOLDPOINT
39a6b05e-30a2-4740-ac86-41f6215e698b | section | 2. MATERIAL, PERSONNEL & THIRD PARTY APPROVAL - 2.1 MATERIAL TESTING
486cc648-29a7-46e8-87c0-82a4976fb1ca | checkpoint | 2.1.1 - Bedding and Overlay Material: Clean Imported Sand or SAP 7
4c6a5b85-12dc-57af-9f84-eb844b1a72b4 | note | Detail - Material grading:PSD
81d99318-3953-50b0-87a3-553626258b67 | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
842b2c18-b12a-55f1-ac5d-21652cdca29f | note | Standard / Specification - PS 25.13.2 g) & h)
110948ae-0e2c-51af-a67d-1197efab1263 | note | Verifying Document - Delivery Dockets/Material Certification
6d35a092-9e71-53f3-8366-f69dd71548b1 | note | Testing Quantity Required (based from schedule qtys) - NA
5b73eeea-f3c1-562c-addc-9e13da30056b | note | Verification Activity - HP
9a700353-5f28-57db-a746-62af3930586e | note | By - ENG
b1e0dc8e-de0b-4e74-a9aa-38a5ebc23b8a | signoff | AUTHORITY HOLDPOINT
44d83bac-76f3-42c4-8c5e-39b2257c0cec | checkpoint | 2.1.2 - Materials: GAP65-Backfill Material
23b3c69e-61c3-5c8d-b7c9-27e3a083e564 | note | Detail - Material grading:PSD
69982c10-640a-5c1d-b2c2-6349b69f27c9 | note | Acceptance / Conformance Criteria - Stockpile size over 4000m3 PS- 16.5.11 for GAP65
0d2e1224-6bdf-544e-8baa-647e3abc8c29 | note | Standard / Specification - PS-21.7.2 Table 21.9
89926f4d-431c-5a36-a4e7-5be287cc0f9a | note | Verifying Document - Lab Test Report NZS 4407.3.8.1
538f58d9-8e96-5832-bd96-e69312922f9f | note | Testing Quantity Required (based from schedule qtys) - 1 Test per 1000m3
582b6634-6b50-520c-8e89-1d5f35c4e7b7 | note | Verification Activity - HP
9569ed76-8c8e-598b-ac62-26995c7de055 | note | By - ENG
63d81330-269f-4298-9075-db67765b857e | signoff | AUTHORITY HOLDPOINT
0b6e92e6-b517-4dab-b57d-d9abacf69d0b | checkpoint | 2.1.3 - Materials: GAP65-Backfill Material
dead2c3d-8425-5ced-9f1d-c49fef0cedf6 | note | Detail - Weathering index:
10ac7968-b8ea-5b19-8b95-0f9febb656a2 | note | Acceptance / Conformance Criteria - AA to CA
f554ac44-d467-5ccc-847c-8f1390459f01 | note | Standard / Specification - PS-21.7.2 Table 21.9
987d8f4e-3f75-5e58-83e8-8420be2644fd | note | Verifying Document - Lab Test Report NZS 4407.3.11
8b7fa9c2-a910-5cc0-bdd6-f7af3e21259d | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
89b237ec-4d43-5544-857e-dccdc5cffbda | note | Verification Activity - HP
5eaf02df-d9ca-5f5a-8fa5-c343b8ec9cfc | note | By - ENG
464c66bc-6468-4260-b978-70b3310b1037 | signoff | AUTHORITY HOLDPOINT
09ef89c4-2afa-4d83-9697-447334c2113f | checkpoint | 2.1.4 - Materials: GAP65-Backfill Material
67aaf769-fcec-552c-9ed7-bf1a39112466 | note | Detail - Crushing Resistance
ffc49956-2e6a-5dd3-a304-40ece59ef931 | note | Acceptance / Conformance Criteria - >100KN
f76a0622-fd6e-5455-847e-d508fcacedbc | note | Standard / Specification - PS-21.7.2 Table 21.9
1a5aa289-6eaf-59a0-9437-a111b759d478 | note | Verifying Document - Lab Test Report NZS 4407.3.10
92ed5aba-43ea-56b8-a774-1a2293235f5c | note | Testing Quantity Required (based from schedule qtys) - 2 test per source
b14c597e-8b01-5272-8ddb-301b10feb6bb | note | Verification Activity - HP
b5d26f2d-714e-521b-9a61-469d0abb98d8 | note | By - ENG
006c000e-da74-49b5-97af-9a1160001773 | signoff | AUTHORITY HOLDPOINT
0e80def9-0026-4998-a4ca-cde2b81a47e9 | checkpoint | 2.1.5 - Materials Approvals
a56af989-ca4e-5c53-a433-cd450e47f5e5 | note | Detail - All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements
8895bb7e-c427-5901-a5aa-07751a808d3a | note | Acceptance / Conformance Criteria - Prior to Commencement and throughout construction
fdbe7567-dbbc-519b-80f5-59a9d0d58c39 | note | Standard / Specification - Project Specifications
5c389606-b39f-5d8e-8d26-163bf0f5146f | note | Verifying Document - Utilities Providers Approval/Material Certification /Delivery Dockets
3ddf2253-d8cc-5de2-81a4-28ced242fc94 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
ef51aec0-3acf-5b8c-814d-5627875e5648 | note | Verification Activity - H
1af29b68-624c-5b9b-b62a-c702c9fce0fe | note | By - SE
4ece6099-0f01-4b16-bde4-65c5945709fa | signoff | AUTHORITY HOLDPOINT
83f97cbe-b43e-4cbc-bc3b-729ae9f6c33e | section | 2.2 MATERIAL DELIVERY
ee48925a-b035-46ef-97b4-087f4ef5eabb | checkpoint | 2.2.1 - Pipe and fittings. Ducts
7db8345a-ba3e-58a1-ae6b-4d5f1a4d4028 | note | Detail - Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC or High-Density Polyethylene (HDPE). Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines.
333fbb3f-f90e-5faa-ae0e-3ca9b54ed4ef | note | Acceptance / Conformance Criteria - Comply with Project Specifications
625baae0-854c-5ffd-9828-2611affb4ecb | note | Standard / Specification - PS 25.13.6 b)
51f875eb-7058-5199-9123-ccc9ee657e66 | note | Verifying Document - Delivery Dockets/Material Certification
497e2f66-3f6d-5599-b0d5-be28065d2a77 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
5aa16fdc-5187-5a70-a7e8-62d24fd18fa9 | note | Verification Activity - H
78bc25dd-85bf-5421-be72-73f158f43e7c | note | By - SE
f97a8dfd-6853-5b80-b674-22bd03bdd93b | note | Comments / Closeout Details - Duct details will be instructed by service providers.
30b72118-4b36-4dd5-91c9-00414bc65ae7 | signoff | AUTHORITY HOLDPOINT
95fc4281-439d-4b9a-bfa7-e0f188d3b25a | checkpoint | 2.2.2 - Bedding material
349f055c-40d5-51ac-b330-812b78a35726 | note | Detail - Clean Imported Sand or SAP 7
52d5971e-85d0-5bd6-a4bf-6ae513e08feb | note | Acceptance / Conformance Criteria - Free of larger sharp particles conforming to GAP 7
ac7553e4-090f-598d-93fd-a88a790432ad | note | Standard / Specification - PS 25.13.2 g) & h) & 25.13.7 b) ii
c7246019-cc11-595a-a5c5-ed534863d820 | note | Verifying Document - Delivery Dockets/Material Certification
da3558cd-d367-5395-806d-f6d08fba0c9f | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
13520fea-8f9a-58bd-94f0-b9d17b4cee98 | note | Verification Activity - H
bd332cbf-5d6b-5170-a45e-98515475dc80 | note | By - SE
e29ceea3-5f67-41be-9f64-7ba1ea194895 | signoff | AUTHORITY HOLDPOINT
d5398cc0-f040-422b-8e23-1339dfa1e2a1 | checkpoint | 2.2.3 - Backfill Material
775a8ca9-30b0-5457-92f9-21908aa5712d | note | Detail - Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs
b2e368c6-bc23-5da4-a48d-978978955761 | note | Acceptance / Conformance Criteria - Comply with Project Specifications
dc270cb9-cd17-59bd-803a-59e13c5cd7f6 | note | Standard / Specification - PS 25.13.2 h) i to iii & 25.13.4 a)
05583998-e4ea-505c-906c-b3681ae0bfd5 | note | Verifying Document - Delivery Dockets/Lab Test reports
b3465e16-1c11-5103-b922-723dc70f41a1 | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
1524ee9f-d13e-5e50-87c6-a5e81f8459d0 | note | Verification Activity - H
9ba41559-439e-5d84-8fd8-cd22bd752862 | note | By - SE
7245ad1a-3400-43c7-aa67-5b628124c14c | signoff | AUTHORITY HOLDPOINT
a4d7cdb7-b059-4497-a17f-f892ba5d8756 | checkpoint | 2.2.4 - Pits Covers
b54dfeb9-8272-5c6a-9c91-dbe596f03cfd | note | Detail - Jointing and pulling pits shall have slip resistant surfaces.
6e129f47-6b34-5471-a0c8-52ff04f7831c | note | Acceptance / Conformance Criteria - Class A-10Kn. Class B- 80Kn. Class C- 150Kn. Class D-120KN.
f10b6ad6-3c89-5058-ba2a-5ab374cde17a | note | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1- 1993.
febba2d3-986d-5831-b1b0-a89896aa2976 | note | Verifying Document - Material Certifications. Delivery Dockets
8632adbf-8bac-5027-840e-de9d33e4f89b | note | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
b523dd59-d9ee-5824-bcb7-d9730aa34ecf | note | Verification Activity - H
3c22d34c-297b-55df-9dc8-1e84a24caef9 | note | By - SE
12320b3f-a7f1-48e9-acfe-43a50c1746ea | signoff | AUTHORITY HOLDPOINT
2e80cf9e-cce2-4de5-a526-19b5f0b1c990 | section | 3. CONSTRUCTION ACTIVITY - 3.1
4473bcd7-a7bd-4e0a-b8c6-5007ed250edc | checkpoint | 3.1.1 - Trench Excavation
881014cb-a527-53b7-bee5-f8672fe67d26 | note | Detail - To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time.
3e77300b-24e3-57d9-8d0c-54d09709df76 | note | Acceptance / Conformance Criteria - #ERROR!
12365ca8-56e6-5f1a-acee-ef8499fd5229 | note | Standard / Specification - PS 25.13.2 a) i
e5d1fb7e-67ac-59a5-9234-fe1d48f36ff3 | note | Verifying Document - Survey
39daa345-e591-50a6-9823-ea6a4c1e5c31 | note | Testing Quantity Required (based from schedule qtys) - Every time
6b035129-a403-50e6-a124-eafc4b6f86b9 | note | Verification Activity - M
b8e83467-db66-5745-9ff7-de536dd190a8 | note | By - SE
c560f64e-3631-49b4-b19d-a3becd6f68a3 | checkpoint | 3.1.2 - Unsuitable Materials
788da501-45e1-5204-b133-312faf493b0b | note | Detail - All confirmed unsuitable material shall be excavated down to suitable materials.
3b5a9fdc-7571-5cb9-8c38-a2295f4015fa | note | Acceptance / Conformance Criteria - Dig Down to Get Suitable Materials or get Engineers Approval.
8d8e26ee-a00d-5e92-ad99-5ebf580c87e6 | note | Standard / Specification - PS 25.13.2 b) ii
a32f42d3-0de8-5a1a-a4e0-0f297dd3fd71 | note | Verifying Document - Visual
eacc48f2-a624-5251-8847-87e6cddcb3cb | note | Testing Quantity Required (based from schedule qtys) - Every time
9d2893a1-8ed0-54ea-a3ad-ea1451cc7677 | note | Verification Activity - M
50c89cc8-28e1-5b9a-8865-40337e15e174 | note | By - SE
4a681e24-b46a-4441-9bd6-7e42252ebb01 | checkpoint | 3.1.3 - Foundation Compliance
9f3f9957-5265-56a7-8e28-baf2e6f1f334 | note | Detail - It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence
b4f5bf4b-5651-5370-9694-0525360b32f1 | note | Acceptance / Conformance Criteria - 50mm granular layer shall be laid and compacted before the bedding layer is laid.
70967d19-82ff-5029-93ac-e78b1e927194 | note | Standard / Specification - PS 25.13.2 c) and g)
bb29f6e5-6443-5910-892c-ab0fdd680881 | note | Verifying Document - Visual Inspection
d7b30555-ed23-54f5-971d-8f7663e42d70 | note | Testing Quantity Required (based from schedule qtys) - Every time
7f197952-ec14-51dd-a602-b43e97854998 | note | Verification Activity - M
f2e6e66d-882f-50c4-8a0e-428f0e065146 | note | By - SE
49179d62-20cd-451d-9cc5-4bdc9f49dc68 | checkpoint | 3.1.4 - Bedding
8614c5cc-5665-5fa3-ab79-3f8940785aa5 | note | Detail - The floor of the trench shall be clear of any obstacles and shall be as flat as possible.
0736aece-5d03-503d-8bd2-dc15e71dfe33 | note | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
119d2e5e-a84d-5440-9563-82cc8c9de3ac | note | Standard / Specification - PS 25.13.2 g)
f566dbf0-0c84-5db8-aa23-db97f0e0357e | note | Verifying Document - Visual Inspection
95c8247d-bef3-517d-afe5-71c62c023bcb | note | Testing Quantity Required (based from schedule qtys) - Every time
cf88f922-c00b-5c77-94ae-58ea7117c49b | note | Verification Activity - M
7af9af8b-6269-5b6b-9749-5e37f31ca339 | note | By - SE
78830cf9-10a2-4c5e-8550-200be233c777 | checkpoint | 3.1.5 - Bedding (Encased in concrete)
e2a882fc-91f0-5b73-ac67-4727ea84b5b1 | note | Detail - Concrete Bedding to be placed. Compressive strength of concrete used no less than 20MPa
e92735c5-112e-5f6a-ab41-56137c2c3ed8 | note | Acceptance / Conformance Criteria - 50mm
c925fb4c-df71-59d9-8612-f84c6aee1fad | note | Standard / Specification - PS 25.13.7 c)
aa502856-7f55-501a-8b7a-1cc391135779 | note | Verifying Document - Visual Inspection
15aa5f42-8a9c-5efd-8d93-0ae20c77a890 | note | Testing Quantity Required (based from schedule qtys) - Every time
99a33773-5ba8-5074-9c2e-001402773f08 | note | Verification Activity - M
b3c964ab-9694-5169-83b2-96437b72a933 | note | By - SE
dfc31b15-66cf-447e-b61f-2a1b0891b1c2 | checkpoint | 3.1.6 - Installation of Ducts
5b79e591-f8e5-5827-adaa-be34a18a3b89 | note | Detail - If more than 2 ducts are being placed.
a223bcd1-0b1c-5e32-beba-bb2d6eb87ff5 | note | Acceptance / Conformance Criteria - Must have 50 mm bedding material between the two ducts.
deeb4f1c-8275-5660-ad84-a68effb8da42 | note | Standard / Specification - PS 25.13.7 b) iii
d86431aa-c70a-50be-a1cf-a63445223e1f | note | Verifying Document - Visual Inspection
24b5f92a-0d49-5a68-85cd-e4c7a023a435 | note | Testing Quantity Required (based from schedule qtys) - Everytime
4d7275e2-defa-5308-9cdc-0c13ffff8e33 | note | Verification Activity - M
4c27abcb-e832-5ed4-8489-e71afe910f15 | note | By - SE
a05dd518-a7e7-4a26-9f83-a8f2a44879cd | checkpoint | 3.1.7 - Draw Wires
5edb7e75-29a5-5246-b153-3b8dadcbedb7 | note | Detail - A draw wire shall be installed in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
9d659fb7-8cb7-5a1b-be14-7d781f814ada | note | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
5c218fd5-e8d2-540a-9a00-2af658da7a07 | note | Standard / Specification - PS 25.13.7 e) ii to iv
f066a145-aaea-5c8d-a3ab-5f5869ec9dda | note | Verifying Document - Visual Inspection
8f57c5b6-de05-5c56-a867-4cffa95efeb7 | note | Testing Quantity Required (based from schedule qtys) - Every time
752d02da-2b6f-5438-b36b-7effcef8df65 | note | Verification Activity - M
d77a631e-2c4a-503f-aae3-306c4c26277e | note | By - SE
9d07cbba-54d9-488f-aaaa-b8959d513f76 | checkpoint | 3.1.8 - Caps
1bfdfd82-7fe6-5e68-9de7-b048819822ff | note | Detail - All duct ends shall be capped
ae5add1e-5d83-53f5-8d27-724134035025 | note | Acceptance / Conformance Criteria - Capped ducts
a3d7f628-012e-5ea4-b7c4-6f7f0f8c09e4 | note | Standard / Specification - PS 25.13.7 e) v
1b0dc8a4-1927-5f71-b1f5-72771fe7de73 | note | Verifying Document - Visual Inspection
387d27f1-087e-5ca4-aeaf-1624f5a7c315 | note | Testing Quantity Required (based from schedule qtys) - Every time
393cf3ed-7340-5bb4-9068-e6e079e4f5c2 | note | Verification Activity - M
57c7c6ec-efd8-5ea6-bda5-8e472b70ed9f | note | By - SE
b17ea8f5-9cdb-4403-a4d8-4c5f65d3300c | checkpoint | 3.1.9 - Warning Tape
fffcaef5-8628-5f0b-974b-849c726c921d | note | Detail - Warning tape to be placed above services.
51439d3b-16f0-5217-8a6f-2a24ba22fa89 | note | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the duct
e9c43411-659c-5c77-b569-388644d1a8ed | note | Standard / Specification - PS 25.13.7 b) iii & f)
fe08ade8-e822-5587-8394-f5dcc7688f8f | note | Verifying Document - Visual Inspection
00f192cc-e9dd-52d7-a66c-f6a410d5c154 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
66839ed7-44f6-50fe-a63f-4fcd43402bea | note | Verification Activity - M
5924d14b-7652-5653-ab92-1041568205ed | note | By - SE
e306fc1c-d395-46d7-a477-4d04ef77d232 | checkpoint | 3.1.10 - Overlay
c96c786d-a3ac-538f-bd2f-f7a7a9396209 | note | Detail - Clean Imported Sand or SAP 7 to be placed and compacted
bc7ad0de-793b-56a0-b539-d517e3b9bc52 | note | Acceptance / Conformance Criteria - 100mm thick Clean Imported Sand or SAP 7
a891bdad-70a0-52b3-aacc-ffe42aceab7b | note | Standard / Specification - PS 25.13.7 b) ii
1dd21f08-8d27-5bfb-b9e8-6a9f25e00417 | note | Verifying Document - Visual Inspection
127845bd-db3a-5def-b2b7-0a3acf4b4686 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
d556104c-2e88-5f64-9ae2-9701f3e1b8a3 | note | Verification Activity - M
b9d5c2fd-2a2a-5863-8989-b22e6624b3e7 | note | By - SE
3f3429b5-7132-4adb-b746-c9a7683a7539 | checkpoint | 3.1.11 - Overlay (Concrete Encased Ducts)
1f4429d8-f8a2-5bac-a86d-0813b9fde853 | note | Detail - Overlay and surroundings to be placed with concrete.
0b70a8f8-2690-5c27-8c4c-3c4c4fd010c2 | note | Acceptance / Conformance Criteria - 100mm thick on top of Ducts 50mm thick side of the Ducts
f9675d8c-79e1-56da-a27d-b43646e236b3 | note | Standard / Specification - PS 25.13.7 c)
010b256a-1588-58ba-9c39-62df9f4f7179 | note | Verifying Document - Visual Inspection
b34dbc84-d497-5c86-b2ce-8799a8d0f168 | note | Testing Quantity Required (based from schedule qtys) - Every time
d597156a-ed6b-5674-85c6-119be7aa2d64 | note | Verification Activity - M
236de8df-23be-5469-b74e-c361c55f82d8 | note | By - SE
0bae926a-9ce6-4858-9d51-9b2f9caa194c | checkpoint | 3.1.12 - Overlay Testing (Concrete Encased)
35e54c37-e0b1-598a-be0e-b1e2bb10136f | note | Detail - Placed Concrete needs to meet the strength Criteria
b074a358-5034-527a-bf77-2f7fbd297b7a | note | Acceptance / Conformance Criteria - >20 MPA
fa29de66-7375-50c6-8352-5c130ce9b7b3 | note | Standard / Specification - PS 25.13.7 c)
b0012925-f4cc-5a23-b915-ab5034f37dbe | note | Verifying Document - Concrete Dockets
91ed986f-a827-54fe-9a6b-7600723d8aa7 | note | Testing Quantity Required (based from schedule qtys) - Every time
9aacd20f-1f0f-508c-b1b7-468d26f1adbc | note | Verification Activity - H
90a5508c-f605-5494-9626-9395b1c0b5a6 | note | By - SE
0491c173-2aab-4592-86c2-67fcbec243f9 | signoff | AUTHORITY HOLDPOINT
5b6c2158-a99a-4448-ab3e-92552e8438d9 | checkpoint | 3.1.13 - Backfill
5bf88ea3-a40c-5c85-9bc5-bd9bc4a1e4e6 | note | Detail - GAP65 to be used if site material is not approved. NDM Testing to be carried out.
d007f31b-e980-5f51-b330-b26ba3ad43ae | note | Acceptance / Conformance Criteria - NDM Test every 250mm compacted layer Min 92% compaction rate and Average of 95%.
d72fe4f3-f5d8-5c87-ba13-19390696dae7 | note | Standard / Specification - PS 25.13.10 a) modified
b5333357-30a1-5679-9e39-f6a426589629 | note | Verifying Document - Lab report.
053515aa-9b3b-50c0-bfb4-56f808ca9c52 | note | Testing Quantity Required (based from schedule qtys) - Every Lift
682f58e3-a6cd-56d3-ae35-8208fb6bbe45 | note | Verification Activity - H
3e64b478-e791-5aab-9131-020ba8bddd83 | note | By - SE
f4cf8649-25a9-4847-814e-28f6d264bf5b | signoff | AUTHORITY HOLDPOINT
aee89273-de10-42e4-89e7-889fa4ef10d3 | checkpoint | 3.1.14 - Pit Installation Location
78c4648b-49e0-5f28-8583-31e1f07bcca5 | note | Detail - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid .
bfb37dbb-602a-54ce-865a-5f9bc9a9edc0 | note | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
1835a7c4-faa8-5498-b21a-52a635aa2845 | note | Standard / Specification - PS 25.13.8 a)
0708013d-51a8-535c-bd10-3d6f229329d2 | note | Verifying Document - Visual Inspection
950eab39-7f6f-598c-b4bc-b438a93cd9a9 | note | Testing Quantity Required (based from schedule qtys) - Every time
7c294134-4f12-5c05-a658-a9c7c627ad90 | note | Verification Activity - H
3f51bcd6-f532-5373-99ff-edace48712db | note | By - SE
b17ed789-fce9-5f0b-af6a-f65804704759 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
b30154a2-27cf-4399-9ebd-8961bb518b47 | signoff | AUTHORITY HOLDPOINT
4fede5a1-b426-4107-93fe-fbd3a4824ffd | checkpoint | 3.1.15 - Pit Installation Bedding
4ba50b52-7982-5304-a05b-b5ece97d1dda | note | Detail - Bedding with 150mm compacted GAP20 covered with 20mm compacted sand
f714ef28-6d1a-5fe8-b6e0-c8594a9f683b | note | Acceptance / Conformance Criteria - 150mm GAP20 covered with 20mm Sand
88a7d06c-e1cd-5f91-b95c-78a49a4d9b81 | note | Standard / Specification - PS 25.13.8 d)
f3588442-3583-5377-886f-1334bf1a0099 | note | Verifying Document - Visual Inspection
4a69ed86-2acf-5fb1-ba3b-a28f9a65b3be | note | Testing Quantity Required (based from schedule qtys) - Every time
9f492a93-7b7f-5b2c-bb98-924386c86df8 | note | Verification Activity - H
a4bd4db7-0e1e-51c1-b511-0cf4fb01e48f | note | By - SE
cdd9bd87-4c5e-595c-bae4-1b37f5494cab | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
0bd6e6a0-05f2-41ed-8cf5-802339320a6a | signoff | AUTHORITY HOLDPOINT
fe4a52eb-50ec-46b2-829a-261874d7888e | checkpoint | 3.1.16 - Pit Installation Backfilling
7d489dc7-5bbc-5fb4-9b31-a0f8163f708e | note | Detail - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts.
500e8173-6802-5b17-a562-f5da50056f90 | note | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
ef7d94e5-4ee1-5d47-89e9-4f90d2138b3b | note | Standard / Specification - PS 25.13.10 a) modified
3e39b019-1e19-5ace-9f61-521efd6d31db | note | Verifying Document - Visual Inspection
72261735-3e57-5fe8-98e5-1f9fe9c01b44 | note | Testing Quantity Required (based from schedule qtys) - Every time
b747e77b-8f12-5546-96fd-5bdbf812d01f | note | Verification Activity - H
301bcfe1-402b-5b92-bc23-86c8a3fb4796 | note | By - SE
effe1658-db19-571c-b1eb-3597f1a6ecb6 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
81bc6170-8c9c-45f0-b620-12e1089e96ca | signoff | AUTHORITY HOLDPOINT
a1333581-120a-45d8-9b00-bb9c191658e9 | checkpoint | 3.1.17 - Pit Installation Clean up
cea66dc3-485e-5822-8e9f-c030703f0300 | note | Detail - Clean out all pit after completion of the work
ba3186df-c924-5b82-ac04-b2f5eae40ea4 | note | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
4a67d1d0-2cf3-5de9-aca4-16a4e0882ed1 | note | Standard / Specification - PS 25.13.8 e)
42dd3885-0376-5ec5-9b6d-c0db556cf49d | note | Verifying Document - Visual Inspection
bcdb6a29-93e7-5635-ac42-4cf1cfdf82ef | note | Testing Quantity Required (based from schedule qtys) - Every time
01606bd5-cb4b-5683-ba2d-65dbe816a496 | note | Verification Activity - M
c7db4af7-46f8-560c-8b92-e1d42d0b4448 | note | By - SE
4b3f379c-f817-5f86-b89e-9105a8b52a80 | note | Comments / Closeout Details - If pits are installed by utility service providers, service owners/operator will clean the pit.
c508a466-171c-4f79-875c-c23e6a410c2f | checkpoint | 3.1.18 - Survey As Built
f986c5ac-7748-5e6b-b32b-c2a181dade03 | note | Detail - As Built every ducts joint before backfill
f9fbcc29-98d5-562e-84e9-57d1f7357dcf | note | Acceptance / Conformance Criteria - Completed as per drawings
108777ac-97dd-5670-b2fd-aa1ebb5ff775 | note | Standard / Specification - Standard Practise
c091fbf0-ef67-52e4-a28d-f14313c9f7ef | note | Verifying Document - Survey
449f69b7-8db5-5180-9127-5cd276569e69 | note | Testing Quantity Required (based from schedule qtys) - on going
0542d6c1-82c9-55fd-9307-73923cbeb027 | note | By - PE
8684bf06-73a7-4869-a78a-feab8acbd2f0 | section | 4. POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 4.1 AS-BUILTS
2af294bc-bf87-484b-989f-db926cf70510 | checkpoint | 4.1.1 - Survey As-Builts
53cf4a25-16e2-5051-b5db-eb5ec3759817 | note | Detail - Quality Check on New Works based on the tolerances in RITS
83de8240-0fb0-5adb-8cdb-1750f0103661 | note | Acceptance / Conformance Criteria - Meets spec and thickness requirements as per drawings
b9ffad88-9cb4-57f8-b1b9-5dedfdde3f02 | note | Standard / Specification - PS-21.7.7
bbed9c01-fa35-530b-ab40-200efdd164d8 | note | Verifying Document - Red pen markup only
313a5680-5efb-513d-9f2e-dcdbdfe71f03 | note | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
e4c858d1-5129-5530-baed-d20d31d20be2 | note | Verification Activity - H
9394f156-0b56-5a84-8b84-7ffc7787352e | note | By - SE
a072cf05-9802-47ac-9772-7070c5ba6526 | signoff | AUTHORITY HOLDPOINT
| checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
| textbox | Contractor's Rep Name:
| textbox | Engineer's Rep. Name:
| date | Date:
| signoff | Add Signature