## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Add Photos |  | Photos: | c2b9f5f5-2b86-49a5-80f3-38190f852ab7
| section | Details
| checkpoint | Please upload all relevant photos and press PASS
| checklist | T3084984 - Wiri RAP Interface Returns - ITP Rev03 | itp | T3084984 - Wiri RAP Interface Returns - ITP Rev03 | 26d5c926-22b6-4b66-a692-bf3c6a53a00e
| section | T3084984 - Wiri RAP Interface Returns
| checkpoint | 1 - Issued For Construction Drawings
d2d3d592-1220-5184-8225-0c99609f38d4 | note | SPECIFICATION REFERENCE - IFC Drawings Issued by Client/Engineer
0465e994-184f-55ac-bd8f-8c5a0db96f43 | note | ACCEPTANCE CRITERIA - Issued For Construction Drawings Available
3f3c3605-106c-562b-9192-9eeb0363ad5a | note | DATE/SIGN - Contractor Rep - H
| signoff | HOLD POINT
| checkpoint | 2 - Underground Services Confirmation
a37a942c-d0bd-5791-a67c-1ab3b1c67752 | note | SPECIFICATION REFERENCE - CTS Permit to Work
fc916314-fd16-5f1d-9214-0fe3c5a3e7df | note | ACCEPTANCE CRITERIA - Underground Services Drawings to accompany permit and marked out onsite where excavation is to be undertaken
347dc77a-1cbf-59a2-b295-e0fcf482667d | note | DATE/SIGN - Contractor Rep - P
62e04558-f065-507f-89a8-f62ccbf9b36a | note | ○ CTS Civil Inspector - R
| checkpoint | 3 - Survey & Setout
cbd1f752-33b5-506d-bd63-5950a89130ae | note | SPECIFICATION REFERENCE - IFC Drawings
d4afb149-9778-5015-ad61-0b1384e31b21 | note | ○ CTS General Civil Construction Spec
8d848bd8-1b34-548c-93e6-57817b672559 | note | ○ CTS Excavation Works Spec
441da9a3-7842-59bb-95a0-74356e398b21 | note | ACCEPTANCE CRITERIA - Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing.
| checkpoint | 4 - Waste Management & Disposal
e02d9587-b526-51be-85de-fe2425abeeec | note | SPECIFICATION REFERENCE - CTS General Civil Construction Spec
bf830f9a-d36c-5b18-9b6b-adff7b739734 | note | ○ CTS Excavation Works Spec
a9324c03-a16a-5841-94a5-ed10144effea | note | ○ CTS Contaminated Environmental Ground Soil Managenet Plan RW-231
d698d631-2ff6-5f24-83ab-17fb30363a60 | note | ACCEPTANCE CRITERIA - Waste management plan prepared and followed. Supporting documents available on request.
f0310620-c07d-5436-98da-b69e98f8615c | note | DATE/SIGN - Contractor Rep - P
de13c16d-6b02-5894-8f64-eb82212db644 | note | ○ CTS Civil Inspector - R
| checkpoint | P1185A - Demolition
96b42369-db5a-579d-bf20-091c72d9e2ec | note | SPECIFICATION REFERENCE - IFC Drawings
eef97807-ab81-5a7c-a03a-69791c11bed7 | note | ACCEPTANCE CRITERIA - Existing pedestal removed at ground level. Concrete removed to approved landfill.
fb8f982b-4ec4-5a9a-9bbf-5834fc0dd2de | note | DATE/SIGN - Contractor Rep - P
59ae458c-7aa8-51b8-bbab-07a5eec50860 | note | ○ CTS Civil Inspector - R
| checkpoint | P1185A - Position of Pump Pedestal Setout
89cff21c-7ee8-5e29-8174-f912077176e4 | note | SPECIFICATION REFERENCE - IFC Drawings
ae395ee4-f086-5c04-85ca-bd101547a3e2 | note | ACCEPTANCE CRITERIA - Setout as per IFC Drawings
2b9c23da-03a6-58b9-bafe-96ae93208701 | note | DATE/SIGN - Contractor Rep - P
ed9c69d5-e306-5d77-9399-ecfd97861ad1 | note | ○ CTS Civil Inspector - R
| checkpoint | P1185A - Pump pedestal location Cleaned & Scabbled
0f2417d3-6a20-5461-9706-b6b46bd7416d | note | SPECIFICATION REFERENCE - IFC Drawings
75d0af9b-1d71-5eb7-807b-1c3745e4fc23 | note | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
362aea47-8e7b-53e6-b8d1-781178f90abc | note | DATE/SIGN - Contractor Rep - P
16c4daea-76ce-5da0-9209-3cff325fae35 | note | ○ CTS Civil Inspector - R
| checkpoint | P1185A - Cast in Items - Bolts & Nuts
4848d4f8-7a8d-57b0-b6d6-1018971fbe03 | note | SPECIFICATION REFERENCE - IFC Drawings
14721145-e2f1-53a9-9854-794ff645c8bf | note | ○ CTS General Civil Construction Specification
8561f67c-adae-5aba-a12b-ab748d2f0240 | note | ○ CTS Epoxy Grouting of Anchor Bolts
bcad05b1-160d-5008-80fb-cec11a3beeda | note | ○ Manufacturers Documentation
8b3b2537-3e7c-5e16-a079-d101bceb13bf | note | ○ Inspection Records
98410c91-1eee-57a7-900a-da056a0f0bba | note | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
7e185da0-cf3a-55a6-b141-f2f0fa9cc071 | note | ○ Drilled holes for Anchors shall be inspected
dd3baf8c-b7e5-5ee2-a2b3-b4c01e8cc006 | note | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
254ceb82-770a-50a8-91e4-eec25878f291 | note | DATE/SIGN - Contractor Rep - P
40705005-1af2-51f8-a72f-5b951e4db7e2 | note | ○ CTS Civil Inspector - R
| checkpoint | P1185A - Formwork, Reinforcing & Concrete
18e550aa-0b92-5a54-a458-54a48cb00654 | note | SPECIFICATION REFERENCE - IFC Drawings
66fed2f5-2f83-56df-8a06-68b89404b4d0 | note | ○ CTS General Civil Construction Specification NZS3109/3112
f484051a-abc1-598e-a33a-9b9e8dc7eb6d | note | ○ Manufacturers Documentation
a4163e98-9e5f-52fa-a81e-3eadc936a8e5 | note | ○ Inspection Records
2172f7ca-f0e9-5136-aefd-a2fe0391c161 | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
3824b303-50b5-588a-9d26-6a4d74bf77ea | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
68cf3d62-48e2-5f99-bf11-a619a44d4258 | note | ○ All reinforcing and formwork to comply with IFC drawings
8cfb73bd-5e0a-5d2b-a4f6-3ad7d06b1f57 | note | ○ Concrete to be min 30MPa at 28 days
56299576-6561-52b4-9a56-6c56bbd9bef5 | note | ○ Testing of concrete per CTS Specifications
47d7ea3c-08e7-5c98-ab99-9cabea7bb4e4 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
d45ceaa6-d0f2-5f2f-b6db-0d476925877c | note | DATE/SIGN - Contractor Rep - P
97c3507e-4d0a-5f57-b9c2-03ee99a8e1d7 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | P1185A - Grouting of Baseplate
c2bee6e0-8ff0-582b-8d2a-5b631f90f095 | note | SPECIFICATION REFERENCE - IFC Drawings
ac92b210-8160-5f86-819c-02734b4a8891 | note | ○ CTS General Civil Construction Specification
4b9918ae-6458-5bbf-9f16-5ed7aa67df56 | note | ○ Manufacturers Documentation
d570c04a-72f4-59c8-a7be-d11f05744010 | note | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
83eedfab-311b-5edb-9850-fdcad87a6104 | note | DATE/SIGN - Contractor Rep - P
cb737adc-c4bb-5166-ab05-2424ebc2494a | note | ○ CTS Civil Inspector - W
| checkpoint | P1185B - Demolition
a63e5b12-77b4-59e3-ad4f-3acd51bc99f7 | note | SPECIFICATION REFERENCE - IFC Drawings
cc5db4ef-5929-5fb9-b398-b547d649986e | note | ACCEPTANCE CRITERIA - Existing pedestal removed at ground level
b2e50c35-aeaf-521a-9886-47bf77620337 | note | DATE/SIGN - Contractor Rep - P
c088ba33-f410-574f-92b4-0a08926187ad | note | ○ CTS Civil Inspector - R
| checkpoint | P1185B - Position of Pump Pedestal Setout
e6595284-d317-51dd-bfbc-61cb0aa8e34c | note | SPECIFICATION REFERENCE - IFC Drawings
a775dcc3-b644-566b-a9ca-aa6808e9bedb | note | ACCEPTANCE CRITERIA - Setout as per drawings
6bc182b2-dd70-5117-bf84-3d3e16e21c8b | note | DATE/SIGN - Contractor Rep - P
1c267ad4-2ea5-500c-99f5-f23e05a988ac | note | ○ CTS Civil Inspector - R
| checkpoint | P1185B - Pump Pedestal Location Cleaned & Scabbled
2d58e169-696d-58ed-acc6-1acd36cd7f6e | note | SPECIFICATION REFERENCE - IFC Drawings
60bbba16-5046-532e-9866-ab90cc17c02e | note | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
7ced8917-799b-5b8c-9afd-4a8704b10328 | note | DATE/SIGN - Contractor Rep - P
71015ac4-85e4-5ddf-a600-3644a17efc9c | note | ○ CTS Civil Inspector - R
| checkpoint | P1185B - Cast in Items - Bolts & Nuts
f33c8c71-1435-5c23-9ab7-b6e530d096a7 | note | SPECIFICATION REFERENCE - IFC Drawings
9f4720c2-f78c-5498-95ed-c8cee1b1414e | note | ○ CTS General Civil Construction Specification
2d1409e3-36cc-586b-a430-1e04c8a8c015 | note | ○ CTS Epoxy Grouting of Anchor Bolts
ce4e18c2-5954-5a92-a4a4-0f347976f75e | note | ○ Manufacturers Documentation
7bc5e43a-7b2d-5026-98bf-db6cf0c8c08e | note | ○ Inspection Records
3185565c-6633-527a-a255-cd8283246da4 | note | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
4dc3c6a7-d654-50ee-a18a-06bd25a3cbeb | note | ○ Drilled holes for Anchors shall be inspected
385b557e-3bce-5fe7-8379-560dd65601ad | note | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
766a0a41-21b5-5f9a-88c4-4219f7df6016 | note | DATE/SIGN - Contractor Rep - P
298eb471-7af3-5bbd-b9f6-32f333f41e0f | note | ○ CTS Civil Inspector - R
| checkpoint | P1185B - Formwork, Reinforcing & Concrete
e7ce2ef2-1e6d-587d-b836-986cd5dc56ce | note | SPECIFICATION REFERENCE - IFC Drawings
b4512d25-bd96-59c1-a2d9-aad0c0580fee | note | ○ CTS General Civil Construction Specification NZS3109/3112
c575ee6e-3758-5369-b2ff-064cb798cc25 | note | ○ Manufacturers Documentation
c8b705f6-eecf-5c16-9f87-e76d129bcc52 | note | ○ Inspection Records
cce93493-9c13-5c7e-8e7b-3fdb04b518f2 | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
b7aa9ff6-0ab3-56a3-a4ac-6460da61db33 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
5be56634-d8a2-5869-ab67-7e0ed7190984 | note | ○ All reinforcing and formwork to comply with IFC drawings
40e26f16-f26d-5e04-9cd3-aca246d05ce9 | note | ○ Concrete to be min 30MPa at 28 days
32f1e969-dd61-55e7-bbda-ba38e357e3e1 | note | ○ Testing of concrete per CTS Specifications
15590b35-9a95-5944-8340-8a74076039e8 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
88277227-f293-586c-a5f3-7c0910497c90 | note | DATE/SIGN - Contractor Rep - P
63ec835d-a6d0-55f1-8df9-797385f63d65 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | P1185B - Grouting of Baseplate
3fde85df-eaa2-5aed-9bdd-030de7b8232f | note | SPECIFICATION REFERENCE - IFC Drawings
780cd39b-90c7-568e-9c2d-0f8ac2665d6e | note | ○ CTS General Civil Construction Specification
8d2a1f0c-30fa-5980-9a93-7b0a71b135df | note | ○ Manufacturers Documentation
351a9352-da88-581b-bf25-e474eef39855 | note | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
7346fc9d-7031-5468-b7a7-921b7f18ffdf | note | DATE/SIGN - Contractor Rep - P
8b0cc0b7-6784-513b-b81a-f42b63eb63e2 | note | ○ CTS Civil Inspector - W
| checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Setout of Pipe Sleeper
d89868fc-629c-5924-9cab-f7df2fcc6cef | note | SPECIFICATION REFERENCE - IFC Drawings
3faf2d3e-d040-5285-bb3f-ed119c3c564b | note | ACCEPTANCE CRITERIA - Comply with setout in drawings
3948583a-13a1-58dd-9a8e-f54c96ba3f5e | note | DATE/SIGN - Contractor Rep - P
a297606c-645f-5665-b9e6-b761ac60ca82 | note | ○ CTS Civil Inspector - R
| checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Excavation & Foundation Preparation inc Site Concrete
5edb43d0-6a81-53f8-8d91-5ac64928bd1d | note | SPECIFICATION REFERENCE - IFC Drawings
69a6c6d5-55fe-59d7-acde-33a3148dc8bb | note | ○ CTS Excavation Works Specification
d6252ef3-310c-575a-8d59-31e682571520 | note | ○ CTS General Civil Construction Specification
89927cff-3151-5fc7-9231-4a91c6cb933a | note | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
5f3225c8-72d5-5774-b783-1e7cb2b95cc3 | note | DATE/SIGN - Contractor Rep - P
2a54887f-5e9f-5d7c-98db-0f72e51d6174 | note | ○ CTS Civil Inspector - W
| checkpoint | PSS3259/PSS3263/PSS3264/PSS3282 - Formwork, Reinforcing & Concrete
05cad429-3d8e-5e38-85b4-5082d899a4d2 | note | SPECIFICATION REFERENCE - IFC Drawings
351b37ab-0aa4-56e7-a8a8-f7f8d4742abe | note | ○ CTS General Civil Construction Specification NZS3109/3112
3bc355e5-d9fe-56f4-b306-d74e13959e99 | note | ○ Manufacturers Documentation
c50e4bb4-d451-5bcc-8cfd-3e5b6a3ff89f | note | ○ Inspection Records
2e23418a-5b50-52a8-8457-c0124d980a7a | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
17e59dc2-4c22-5822-88c4-8de2cc997b00 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
05900b9d-9af8-5518-b597-25f0c3c49316 | note | ○ All reinforcing and formwork to comply with IFC drawings
e62839a6-017a-57a6-82a4-b21f6facc292 | note | ○ Concrete to be min 30MPa at 28 days
56d6c6fa-79e8-5a22-ab3e-73f2637f8b6e | note | ○ Testing of concrete per CTS Specifications
c5898c84-a2c6-5b7c-a05e-85555a483764 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
fc172450-8b3c-516f-9ebc-d2c9c48dbd79 | note | DATE/SIGN - Contractor Rep - P
92058a5c-5bbd-587e-bc66-29af3d705584 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | PSS3268/PSS3269 - Position of Slab Extension Setout
bac641da-c053-57dc-9404-02b01a8ed07b | note | SPECIFICATION REFERENCE - IFC Drawings
3bd40c11-0274-5563-970d-24e61e47d5c4 | note | ACCEPTANCE CRITERIA - Setout as per drawings
c3a40300-467e-55ed-9218-da08056f5bd0 | note | DATE/SIGN - Contractor Rep - P
a4466e46-41a5-5b7a-bb31-a05281db594b | note | ○ CTS Civil Inspector - R
| checkpoint | PSS3268/PSS3269 - Excavation & Foundation Preparation inc Site Concrete
fa5e9d38-168f-587b-9acc-075c158f8aa4 | note | SPECIFICATION REFERENCE - IFC Drawings
bbba09ea-5915-5b76-a03a-d540403b1fbc | note | ○ CTS Excavation Works Specification
67741041-31a4-5ee4-ac9d-6e01cecd2610 | note | ○ CTS General Civil Construction Specification
cdf66b29-2322-525a-9376-c8d0f9412361 | note | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
634c1b05-a8ca-58ce-9ba5-03f48371a1c3 | note | DATE/SIGN - Contractor Rep - P
8a39c3a8-9389-5bf3-95e9-0f122aa92c75 | note | ○ CTS Civil Inspector - W
| checkpoint | PSS3268/PSS3269 - Formwork, Reinforcing & Concrete
48a1b742-417c-571c-b647-da69d5301e4c | note | SPECIFICATION REFERENCE - IFC Drawings
38176a7e-d536-55d3-8392-24f4800aa208 | note | ○ CTS General Civil Construction Specification NZS3109/3112
de0dc8e6-dbf3-5c20-963a-bb02fe0e65fe | note | ○ Manufacturers Documentation
245f8c25-43cd-5223-8749-4a6dc2ca8269 | note | ○ Inspection Records
4b84c154-1a64-534f-b0bc-f0effa8585df | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
dd239b03-829f-5ac9-b5aa-f9853098dd82 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
21b4b8f6-329c-55fa-9a1c-93ab0467207c | note | ○ All reinforcing and formwork to comply with IFC drawings
84a012aa-e85d-514a-bb2f-5cd073f8159e | note | ○ Concrete to be min 30MPa at 28 days
0e606058-8076-5ea1-9d8d-fc28dff3dd1c | note | ○ Testing of concrete per CTS Specifications
a6571016-19ea-5a7a-8779-a6ed00717d83 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
2bae2e87-3f4b-5436-be88-87dc7c317937 | note | DATE/SIGN - Contractor Rep - P
49aea235-4cd4-5bce-ad2a-f22428c1cecf | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | PSS3272/PSS3273 - Position of Slab Extension Setout
f9bfe1a6-fa9c-516f-ab78-35d1c67434ea | note | SPECIFICATION REFERENCE - IFC Drawings
5d8b1b87-d641-5fe7-b7da-8268f57cf488 | note | ACCEPTANCE CRITERIA - Setout as per drawings
0beec65f-83a7-5989-acf0-906afc500079 | note | DATE/SIGN - Contractor Rep - P
77ff334f-8a4e-579c-8c82-d3478daf2870 | note | ○ CTS Civil Inspector - R
| checkpoint | PSS3272/PSS3273 - Excavation & Foundation Preparation inc Site Concrete
02f0a22d-34f1-59df-8c32-ca56bd11b86a | note | SPECIFICATION REFERENCE - IFC Drawings
81a042c8-3131-598c-9422-1e40c18c86ba | note | ○ CTS Excavation Works Specification
22166bda-4d06-5226-8293-6f0ccbea0cfd | note | ○ CTS General Civil Construction Specification
f00587a4-d1b1-5231-9e81-fd9800caab38 | note | ACCEPTANCE CRITERIA - Excavated as per IFC drawings to line and levels shown. Foundation compaction Inspection Record completed.
720fa2da-f935-5b72-9327-256b0b8c2575 | note | DATE/SIGN - Contractor Rep - P
f28cfa22-062c-5f17-87fc-ef6fa5673fe6 | note | ○ CTS Civil Inspector - W
| checkpoint | PSS3272/PSS3273 - Formwork, Reinforcing & Concrete
0c302280-4007-5d75-9bb2-99ab35b3a6df | note | SPECIFICATION REFERENCE - IFC Drawings
674573bc-2ce7-52b1-ae14-1b8285164d42 | note | ○ CTS General Civil Construction Specification NZS3109/3112
31cc02c0-9c0a-54ae-8e33-1bdbfaf5ccd6 | note | ○ Manufacturers Documentation
7131412d-070f-5941-801a-b6de5dc5583e | note | ○ Inspection Records
6e427401-3833-56f4-820a-942f8b2f1785 | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
ccb1a1f9-8d68-51d5-9624-dc08aee94497 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
ba89c926-8785-5703-abff-c56c267a46ea | note | ○ All reinforcing and formwork to comply with IFC drawings
0169c798-e9e9-5ef5-a588-d4e6368bf0ca | note | ○ Concrete to be min 30MPa at 28 days
84fdc905-63ea-5dbb-acd4-1f0ec515bbc3 | note | ○ Testing of concrete per CTS Specifications
90fdab7c-8d2a-564b-ba3a-19c80b03258f | note | ○ Prepour Inspection Record Filled out Prior to Concrete
07586369-e35f-5a45-a895-43c57ab739d0 | note | DATE/SIGN - Contractor Rep - P
cbcb71aa-f403-50b7-8442-a3448ae92d52 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | P3658 - Position of Pump Pedestal Setout
dca692a0-8d2e-5358-ab62-8ccd8262ac4e | note | SPECIFICATION REFERENCE - IFC Drawings
76c8936c-a171-5560-8e60-0c5c79530366 | note | ACCEPTANCE CRITERIA - Setout as per drawings
5e9ebe18-b431-53b9-8c66-3e72e764f647 | note | DATE/SIGN - Contractor Rep - P
336576db-396b-537b-9eb7-8024fdd3a571 | note | ○ CTS Civil Inspector - R
| checkpoint | P3658 - Pump Pedestal Location Cleaned & Scabbled
b8042d7a-01ff-56c6-b7bb-9715c1d0b060 | note | SPECIFICATION REFERENCE - IFC Drawings
6f224088-92c3-5b88-a355-8f519e796de6 | note | ACCEPTANCE CRITERIA - Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
abfc77b6-f077-5ada-8672-c6af97365120 | note | DATE/SIGN - Contractor Rep - P
8354199c-2d87-5989-a261-20d163152c38 | note | ○ CTS Civil Inspector - R
| checkpoint | P3658 - Cast in Items - Bolts & Nuts
8cdeac5b-b037-50f0-b96b-266bc316d381 | note | SPECIFICATION REFERENCE - IFC Drawings
0753049c-5b1b-58f9-b7ca-15fcbf410f50 | note | ○ CTS General Civil Construction Specification
f73576e0-7a5a-5386-a36f-de0e37066152 | note | ○ CTS Epoxy Grouting of Anchor Bolts
8c64c512-c171-57f0-b710-452852487221 | note | ○ Manufacturers Documentation
753a4ac0-c97a-561b-80f0-4eb229262734 | note | ○ Inspection Records
dbd1962b-5d87-547c-bc1a-6402360ce3f2 | note | ACCEPTANCE CRITERIA - If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
238ac032-af71-50da-9a71-a3788fbcb3c4 | note | ○ Drilled holes for Anchors shall be inspected
44417a48-5c5b-5221-a9ab-d867ee6c1c61 | note | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
462e0ba2-27a6-55c1-b39a-714196d16f8d | note | DATE/SIGN - Contractor Rep - P
5fc9839b-88b7-5761-99c7-fec82686e95e | note | ○ CTS Civil Inspector - R
| checkpoint | P3658 - Formwork, Reinforcing & Concrete
12016907-362e-5a07-b9d2-89b299dfe862 | note | SPECIFICATION REFERENCE - IFC Drawings
a26f2db7-1c03-5d93-b85a-9c2a5dc4e403 | note | ○ CTS General Civil Construction Specification NZS3109/3112
120b3767-12a0-50cd-9f36-b5d23c902ac0 | note | ○ Manufacturers Documentation
20ee2e1e-7ead-55f2-adbb-ab12cf4f5fae | note | ○ Inspection Records
935c42a8-99e3-5c67-989b-19c4691fbfa6 | note | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
2509e191-6d3f-58a6-bbbc-f38d441cda3e | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
fc67347e-b845-530f-85c2-3c7f1adffa66 | note | ○ All reinforcing and formwork to comply with IFC drawings
a416a89b-6a1e-54dc-ac66-95c8d2f309ff | note | ○ Concrete to be min 30MPa at 28 days
22172ea6-8e4e-5d43-b5f4-c1e30150ed6b | note | ○ Testing of concrete per CTS Specifications
4b0ad07a-5f61-52d6-bac4-09ccebfe68b0 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
352190d1-46e9-5059-977d-6c57df34c6e0 | note | DATE/SIGN - Contractor Rep - P
9d684929-aba3-5546-b700-9d51329717ed | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | P3658 - Grouting of Baseplate
3bfded69-5e77-591e-a69b-903853346a54 | note | SPECIFICATION REFERENCE - IFC Drawings
c8b23e27-869a-529d-982f-dce027ffa759 | note | ○ CTS General Civil Construction Specification
56c5af78-52d1-50f0-99da-cc64212520c0 | note | ○ Manufacturers Documentation
598d85bc-57e5-5b21-b917-78545c0f9b69 | note | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
18ba2e0e-6dd8-5bef-ae87-0b6f6c1657e4 | note | DATE/SIGN - Contractor Rep - P
a3865cc4-8eb5-5970-9f13-0e8fd496b63f | note | ○ CTS Civil Inspector - W
| checkpoint | 5 - Other
3b4e709d-651e-5630-a64d-05b0219647ac | note | SPECIFICATION REFERENCE - Other
994ae909-4c5e-556d-8b19-a110fcde2d8b | note | ACCEPTANCE CRITERIA - Other
acf89e30-6a7e-5272-a810-e9035b5c98bf | note | DATE/SIGN - Contractor Rep - H
24201690-e02c-553e-823e-45d27ad8a2fb | note | ○ Project/Construction Engineer - H
| signoff | HOLD POINT
| checkpoint | 6 - Complete final Civil Inspection and close off ITP
9623f555-435d-55ed-b6ea-b2da8421242e | note | SPECIFICATION REFERENCE - IFC Drawings
643e4692-9b03-5515-a00e-573d912039cd | note | ○ CTS General Civil Construction Specification
6a76b2a9-72f1-5a0d-962c-b8a01ff175af | note | ○ Manufacturers Specification
89c85df7-d8c5-550d-bc51-47c300277289 | note | ACCEPTANCE CRITERIA - ITP/QC has been completed; all steps & hold points signed byrelevant party.
ec83da9a-0325-5644-868a-c779a769b4c8 | note | ○ All work completed as per work pack, and any field instructions issued during construction compiled
77bba869-7ca3-5303-ad29-5d4f1fa7b0a7 | note | DATE/SIGN - Contractor Rep - P
ceb98418-f4ea-52f6-ab60-341c094dbda5 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 7 - Non-Conformance Reporting
5d2e0205-35ce-525a-8af4-8e7e65a41920 | note | SPECIFICATION REFERENCE - UCC Internal NCR and or Lucidity event NCR
fb14026d-d691-581f-8c60-428c6368d834 | note | ○ QC Requirements for Civil Works
e776f05f-9afd-5582-a3bd-25ce8e1aa501 | note | ACCEPTANCE CRITERIA - All Non-Conformance reports and Investigations are attached and closed out
6fd5ffa1-463b-5f3a-95b0-aa9925d9f3c6 | note | DATE/SIGN - Contractor Rep - R
| checkpoint | 8 - As Built & Final Design Documentation
46fa36d5-816a-5309-a01b-b77fd539a331 | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
ca14c6eb-b2b1-5be8-9c2c-7d587c3e9f93 | note | DATE/SIGN - Contractor Rep - P
| checkpoint | 9 - Reference Info, Specifications
98e6eabc-afb7-5be5-a266-fb371ce36651 | note | ACCEPTANCE CRITERIA - All Reference Information and relevant Product Specifications
| checkpoint | 10 - Punch Listing
e0f0fb42-7d0f-5438-af26-58a312305dae | note | SPECIFICATION REFERENCE - CTS QC Requirments for Civil Work
309c5f9e-fb78-589e-88ec-e4ea1afc67ff | note | ACCEPTANCE CRITERIA - All punch list items are closed out in the relevant timeframe to the required standard
11283e89-5ebf-5bd4-ae4e-d3d80f0fd73b | note | DATE/SIGN - Contractor Rep - P
0aa1e3f5-4140-5554-9505-623cb6b13b89 | note | ○ Project/Construction Engineer - R
| checkpoint | 11 - Compilation of ITP
9d847bd3-b030-5272-8840-ec7136b88a04 | note | ACCEPTANCE CRITERIA - ITP Completed and Signed off
c1eccc4c-cf6d-56a5-a77b-e7150dc0eb62 | note | DATE/SIGN - Contractor Rep - H
331d23de-39a0-5e72-a4a0-49268f2746a6 | note | Project/Construction Engineer - H
| signoff | HOLD POINT
| checklist | W25 Wiri RAP Interface ITP | itp | W25 Wiri RAP Interface ITP | eee20048-8037-42bb-85a5-211fe3f8605a
| section | Details
| checkpoint | 1 - Issued For Construction Drawings
14e560e1-e462-5822-9ef7-bfb47765a793 | note | SPECIFICATION REFERENCE: IFC Drawings Issued by Client/Engineer
468ea300-0531-5d42-802a-c97b0c452e38 | note | ACCEPTANCE CRITERIA: Issued For Construction Drawings Available
e1fb5811-2352-58ff-a9a8-1c4e213b001e | note | DATE/SIGN: Contractor Rep - H
| signoff | HOLD POINT
| checkpoint | 2 - Underground Services Confirmation
e4393529-e18e-515f-8143-b2f8416059a0 | note | SPECIFICATION REFERENCE: CTS Permit to Work
98dc5e73-06b9-5037-9761-40fe188eb1e4 | note | ACCEPTANCE CRITERIA: Underground Services Drawings to accompany permit and marked out onsite where excavation is to be undertaken
721a346e-2504-56ca-af3e-36a9d3e1c1cd | note | DATE/SIGN: Contractor Rep - P
3aaf4a53-eef7-5063-a8bf-f7bafb5ef9f4 | note | ○ CTS Civil Inspector - R
| checkpoint | 3 - Survey & Setout
44700001-d822-54a7-9581-ed17aa8d2da8 | note | SPECIFICATION REFERENCE: IFC Drawings
5626be32-5086-51db-ae78-0eb5b638bea2 | note | ○ CTS General Civil Construction Spec
0020406b-98d5-5a67-bf14-38c33676700b | note | ○ CTS Excavation Works Spec
5583ac0b-ab89-5d29-a05f-45c52d9ed749 | note | ACCEPTANCE CRITERIA: Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing.
0e36f685-a029-5a4e-bf13-dfa447d561ce | note | DATE/SIGN: Contractor Rep - P
| checkpoint | 4 - Waste Management & Disposal
97e0785c-2c79-52a0-a125-a6b222b7790b | note | SPECIFICATION REFERENCE: CTS General Civil Construction Spec
5113ea89-293e-580e-87b7-0cd9952b48de | note | ○ CTS Excavation Works Spec
a958e955-b8e6-5e61-b32a-09f41857db7f | note | ○ CTS Contaminated Environmental Ground Soil Managenet Plan RW-231
4f1713a1-a69f-56d5-a614-e2c465186600 | note | ACCEPTANCE CRITERIA: Waste management plan prepared and followed. Supporting documents available on request
652514ef-12e0-518b-b07e-7798bd7434c1 | note | DATE/SIGN: Contractor Rep - P
5a80dbf3-5ebb-5b06-8ca5-49373d423a26 | note | ○ CTS Civil Inspector - R
| checkpoint | 5A - Demolition
0896c0f7-9fc3-5c57-9aa9-cb07866dbbcd | note | SPECIFICATION REFERENCE: IFC Drawings
cb80c843-5038-5bd4-8aec-01530a8c4026 | note | ACCEPTANCE CRITERIA: Existing pedestal removed at ground level
166bad3d-f6ff-53b9-9526-7307b612e2b0 | note | ○ Concrete removed to approved landfill
c121a744-9235-5af3-abd9-c2a6cec9522e | note | DATE/SIGN: Contractor Rep - P
95239fec-10c4-5e23-9396-d72997b24440 | note | ○ CTS Civil Inspector - R
| checkpoint | 5B - Position of Pump Pedestal Setout
2c9d9d9b-d617-5a6b-90fc-a81cf981e9c9 | note | SPECIFICATION REFERENCE: IFC Drawings
7db8fb62-f099-5944-a68e-7b434d42f1e5 | note | ACCEPTANCE CRITERIA: Setout as per IFC Drawings
f362729c-2dc3-51c8-8c57-3d59fd2542d1 | note | DATE/SIGN: Contractor Rep - P
ee9a611f-5e82-5ca7-afb8-8c32adbb5124 | note | ○ CTS Civil Inspector - R
| checkpoint | 5C - Pump pedestal location Cleaned & Scabbled
4c7b2ede-4a02-59d6-b99f-bd2e227dc2d2 | note | SPECIFICATION REFERENCE: IFC Drawings
e2f95c6d-067c-5c43-b5c0-b48654effbfa | note | ACCEPTANCE CRITERIA: Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
e78a5186-5455-5c9a-8412-994daea7c2b2 | note | DATE/SIGN: Contractor Rep - P
6ccb5418-d312-53c9-93e9-584991ffc614 | note | ○ CTS Civil Inspector - R
| checkpoint | 5D - Cast in Items - Bolts & Nuts
fd0500fb-ea20-5fd5-aa8c-8c1c7e80dfa8 | note | SPECIFICATION REFERENCE: IFC Drawings
516ea30d-0249-5c9a-b082-ff6c04d21050 | note | ○ CTS General Civil Construction Specification
5b51cdde-f82e-5586-9804-20a45cefdd7d | note | ○ CTS Epoxy Grouting of Anchor Bolts
a5995309-ec0c-59f1-ac52-b320dfea8f2d | note | ○ Manufacturers Documentation
ce19b1a7-e3c3-5de1-8b2e-d10164b71617 | note | ○ Inspection Records
825b30e4-a02e-51cc-87e7-9ad4fe0f1eec | note | ACCEPTANCE CRITERIA: If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
0713b261-a2be-58df-8dd2-5e78a09d2518 | note | ○ Drilled holes for Anchors shall be inspected
b7f20fbc-1c79-5331-8eae-1398aa24986d | note | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
e519a704-14e0-5435-9cd0-a19a73e12d2d | note | DATE/SIGN: Contractor Rep - P
59067b11-c40c-5bef-bae0-134044ce4bc1 | note | ○ CTS Civil Inspector - R
| checkpoint | 5E - Formwork, Reinforcing & Concrete
3bce4f58-6017-5f28-95e1-36da7599bbe7 | note | SPECIFICATION REFERENCE: IFC Drawings
ef24c0aa-97b8-5b9b-aefe-ee2723537ede | note | ○ CTS General Civil Construction Specification
f05e6526-b0ca-57d5-a340-e231fb120698 | note | ○ NZS3109/3112
07004e69-bfe3-5058-864f-b60c0249c886 | note | ○ Manufacturers Documentation
4c761a38-aa3a-5f33-a1a9-c1026520dfa4 | note | ○ Inspection Records
b21452db-5f6c-5887-a1de-28cdba4aa2b2 | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
6b1e4f02-525c-5d7c-9282-5d9f39e8154b | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
9578af37-733e-5e4b-9426-80c1fd91dd1a | note | ○ All reinforcing and formwork to comply with IFC drawings
05fbe7ef-d807-5675-a05e-292e6a65315d | note | ○ Concrete to be min 30MPa at 28 days
cf14c741-3da0-5cd7-ac7e-8667c14dc34c | note | ○ Testing of concrete per CTS Specifications
ffb56e24-fb0d-5c96-931f-5763d1242ca0 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
28111e96-4951-592d-97bb-b4aac03fbb4d | note | DATE/SIGN: Contractor Rep - P
ba64b285-ed3f-59b7-8e7e-4e402769f56f | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 5F - Grouting of Baseplate
9f1a3564-9666-53d7-ac62-cd4bb5f78cd0 | note | SPECIFICATION REFERENCE: IFC Drawings
05677506-4adb-591c-80b7-e3a853c55b59 | note | ○ CTS General Civil Construction Specification
caec6071-9cb3-5a63-b5be-6797c3ca56da | note | ○ Manufacturers Documentation
1aec489a-688c-5978-a2ac-0f701bdf6e76 | note | ACCEPTANCE CRITERIA: Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
d173e079-d339-5975-861d-5a5ffd103d68 | note | DATE/SIGN: Contractor Rep - P
5baf711a-e76f-5464-8f3a-963e999f63e3 | note | ○ CTS Civil Inspector - W
| checkpoint | 6A - Demolition
761da63b-a1a8-5f37-9f5a-0cec9b6e43a9 | note | SPECIFICATION REFERENCE: IFC Drawings
ac18e0b4-d4db-5868-9f0f-e4bb315e48c8 | note | ACCEPTANCE CRITERIA: Existing pedestal removed at ground level
a7dc4c7c-16a7-58a9-b485-e88d453c85a5 | note | DATE/SIGN: Contractor Rep - P
fdd41716-64ec-5ece-b04e-f4186b6a4838 | note | ○ CTS Civil Inspector - R
| checkpoint | 6B - Position of Pump Pedestal Setout
3ad2afbc-632b-5950-854e-64a7fd197376 | note | SPECIFICATION REFERENCE: IFC Drawings
9481dd41-bb84-53c9-8f12-5e4bcad32c2a | note | ACCEPTANCE CRITERIA: Setout as per drawings
b1f7e5ea-ba00-5b48-a571-55b312131584 | note | DATE/SIGN: Contractor Rep - P
fdd270bd-744c-58a4-89b6-abf755425d7a | note | ○ CTS Civil Inspector - R
| checkpoint | 6C - Pump Pedestal Location Cleaned & Scabbled
1d5a68be-e702-5178-8e9a-6352db2d8090 | note | SPECIFICATION REFERENCE: IFC Drawings
06e814cb-5acd-5627-9156-964d66ab3307 | note | ACCEPTANCE CRITERIA: Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour
44fe54f5-edf6-5f83-b437-a7ca80a54a98 | note | DATE/SIGN: Contractor Rep - P
ecc32e14-094f-58b4-9dd9-96e1617ac11c | note | ○ CTS Civil Inspector - R
| checkpoint | 6D - Cast in Items - Bolts & Nuts
a42b9470-1de7-5dbe-9886-cb91a08a5da4 | note | SPECIFICATION REFERENCE: IFC Drawings
a4ff2d4a-8e76-59cf-9635-afabffa8248d | note | ○ CTS General Civil Construction Specification
dcd9374d-4b00-5f90-b287-30b128b0d85a | note | ○ CTS Epoxy Grouting of Anchor Bolts
67967c49-14c9-5642-a90f-7e0500063ca1 | note | ○ Manufacturers Documentation
b4b01dbf-a3e7-535f-9779-00af0432dad8 | note | ○ Inspection Records
b59e4260-afda-5111-8413-0547d51bb717 | note | ACCEPTANCE CRITERIA: If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings
5b019f9f-0269-5e8f-a130-cd21bb4c33f6 | note | ○ Drilled holes for Anchors shall be inspected
1893ccf0-b0a9-5ad8-976d-23ab09e5e892 | note | ○ Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings
3ba1910c-cdcf-5f7f-9f13-0a499131d151 | note | DATE/SIGN: Contractor Rep - P
1fe459e1-9272-5bc0-b73d-415ac1d5fe6d | note | ○ CTS Civil Inspector - R
| checkpoint | 6E - Formwork, Reinforcing & Concrete
ef15eee4-1c51-584a-9457-3610ae4d6c27 | note | SPECIFICATION REFERENCE: IFC Drawings
5761dd29-ef59-5d01-9ef0-3ac317991477 | note | ○ CTS General Civil Construction Specification
2f852e19-1f93-51b7-8069-142a653a6fd7 | note | ○ NZS3109/3112
97e43c32-18e9-53e3-8b71-b0ac885840fc | note | ○ Manufacturers Documentation
e1bc7cdb-d20b-5bfb-9e34-664823ae4b59 | note | ○ Inspection Records
1be8ac9f-bde5-5217-a99b-9add801ad4f5 | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
d16ebe42-6827-5951-83e9-17ae4e79c48f | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
a30cfdf5-cb16-5fa4-a89b-662e781b96da | note | ○ All reinforcing and formwork to comply with IFC drawings
5b499405-cf4f-5d89-afea-867c2289a50f | note | ○ Concrete to be min 30MPa at 28 days
e9f65d37-8ce9-51d1-9ccf-139231c8e439 | note | ○ Testing of concrete per CTS Specifications
227fdd9e-c7f8-5775-bfa7-a8d67a1ca2a3 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
635de7f4-d637-5e1d-b668-694189f6df4f | note | DATE/SIGN: Contractor Rep - P
5820d878-b238-57cd-baa0-b0f65d5d8eb8 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 6F - Grouting of Baseplate
e58ba7fb-0bc8-5191-81cc-712cb0956ae8 | note | SPECIFICATION REFERENCE: IFC Drawings
e0ca1210-9ec7-5068-9700-5e1229ad034e | note | ○ CTS General Civil Construction Specification
c3df7bc7-b12e-50b4-b559-f84430b02e84 | note | ○ Manufacturers Documentation
61b33721-f0a1-5295-92c9-4ad420d2c08c | note | ACCEPTANCE CRITERIA: Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
ccac55dc-faf8-5441-8e32-53699dfbb62f | note | DATE/SIGN: Contractor Rep - P
3d20f4d0-9524-5edf-9aee-7620fb3402f0 | note | ○ CTS Civil Inspector - W
| checkpoint | 7A - Setout of Pipe Sleeper
6e0ecc0d-6071-59e1-89eb-13d3083d72e4 | note | SPECIFICATION REFERENCE: IFC Drawings
51cf838a-7d6f-5942-991d-5b8eb3d70e76 | note | ACCEPTANCE CRITERIA: Comply with setout in drawings
f81e1182-c264-59d3-bc8d-5f9779689ee0 | note | DATE/SIGN: Contractor Rep - P
921dd59f-a68a-5202-ad3c-b2cc0923c1a0 | note | ○ CTS Civil Inspector - R
| checkpoint | 7B - Excavation & Foundation Preparation inc Site Concrete
03bd86fb-7848-5513-91b2-ccbe88c3388a | note | SPECIFICATION REFERENCE: IFC Drawings
c81abbc8-c6a5-525e-863c-fdbac8fd7ed7 | note | ○ CTS Excavation Works Specification
13aaea2f-8f5b-5e40-8661-bcbc51affac1 | note | ○ CTS General Civil Construction Specification
11ac930d-db4a-5553-b57b-8b900dac4d5e | note | ACCEPTANCE CRITERIA: Excavated as per IFC drawings to line and levels shown
d070c471-b6b7-5ba9-8207-212b60965b74 | note | ○ Foundation compaction Inspection Record completed
91c04762-2395-5b90-9466-206d19234db0 | note | DATE/SIGN: Contractor Rep - P
43cc0ae5-7efb-550f-8a6e-fe2a9a0ed499 | note | ○ CTS Civil Inspector - W
| checkpoint | 7C - Formwork, Reinforcing & Concrete
73730a53-1ee8-5069-b151-241f6270c18c | note | SPECIFICATION REFERENCE: IFC Drawings
5bd114fe-015c-5e97-8a63-c8b8c0b3d5ec | note | ○ CTS General Civil Construction Specification
a179dd76-5275-5680-b27b-198c319e5c9b | note | ○ NZS3109/3112
e6cb0121-36c9-53d7-ba03-42bf65962353 | note | ○ Manufacturers Documentation
e7c1aba3-22da-50e3-bff5-bfd0b1abdd9e | note | ○ Inspection Records
c50085fd-734a-5480-a87d-806c63a19e77 | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
09497384-c249-52cf-931d-6923dce989e1 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
72eec2c4-b0e6-5f7b-95ea-548662e830df | note | ○ All reinforcing and formwork to comply with IFC drawings
d705247c-b7ad-5957-8ff9-1eb8d26f78f2 | note | ○ Concrete to be min 30MPa at 28 days
34392d43-2244-535f-a235-d7bcc8a4f148 | note | ○ Testing of concrete per CTS Specifications
a722ca94-5069-5758-a1d7-aec98c97545a | note | ○ Prepour Inspection Record Filled out Prior to Concrete
d412e189-8e8d-5432-b273-efbed17f6dfc | note | DATE/SIGN: Contractor Rep - P
7ef845bb-cd14-565f-abd5-41e02da3e714 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 8A - Position of Pump Pedestal Setout
6fc5f9f5-06bc-525c-8989-b8969e60bce4 | note | SPECIFICATION REFERENCE: IFC Drawings
5354e3e4-8ce1-5552-8b33-e84bcd89b7a7 | note | ACCEPTANCE CRITERIA: Setout as per drawings
f30a7b57-8b32-5d39-ac78-d347d948cd28 | note | DATE/SIGN: Contractor Rep - P
83e62704-337a-55a3-b903-a39d551d0d9a | note | ○ CTS Civil Inspector - R
| checkpoint | 8B - Excavation & Foundation Preparation inc Site Concrete
95c771e9-61f1-5763-b856-e82364c36cc0 | note | SPECIFICATION REFERENCE: IFC Drawings
6d73a70a-3c49-59cc-b948-90f5a4df3280 | note | ○ CTS Excavation Works Specification
1f79658e-32bc-5eb1-8605-8b178605f003 | note | ○ CTS General Civil Construction Specification
c4595fdf-3cdb-503f-8ad6-3b938e503846 | note | ACCEPTANCE CRITERIA: Excavated as per IFC drawings to line and levels shown
3eb2e2f9-1507-53c2-86df-7e87815bfbd0 | note | ○ Foundation compaction Inspection Record completed
9faafceb-26bd-5f05-ad03-dd668e675793 | note | DATE/SIGN: Contractor Rep - P
c2e4746f-ff31-5843-bec6-520523e84adf | note | ○ CTS Civil Inspector - W
| checkpoint | 8C - Formwork, Reinforcing & Concrete
97100f36-1c03-5a0d-b07c-b7847a327ace | note | SPECIFICATION REFERENCE: IFC Drawings
195d7b1a-cc50-5e48-827d-d1ad57c7e0de | note | ○ CTS General Civil Construction Specification
03078014-0499-511f-bd0a-8d4e857d753a | note | ○ NZS3109/3112
a23d43a2-7ef3-543f-95e3-179f4ae8cd3c | note | ○ Manufacturers Documentation
6cbd6517-7002-5031-a2ea-cfbe119f8454 | note | ○ Inspection Records
a71fed5a-f071-5a9b-86aa-089c155c74ed | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
768331b6-361b-5665-8ba1-9e01fd1a1e2b | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
89d6fc31-9064-5065-a113-511e6c4ec5d3 | note | ○ All reinforcing and formwork to comply with IFC drawings
9822f7a2-9a6b-59b0-8645-27acd234aac4 | note | ○ Concrete to be min 30MPa at 28 days
5c397737-5f52-523a-8443-e35331f82848 | note | ○ Testing of concrete per CTS Specifications
8984d014-768e-5963-9e18-42712a4d194c | note | ○ Prepour Inspection Record Filled out Prior to Concrete
8cda9e98-30a9-53ec-97e9-ab681be73fbb | note | DATE/SIGN: Contractor Rep - P
586b7e30-fb24-5893-9e9c-5e7182e994b1 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 9A - Position of Slab Extension Setout
2212b1d4-be07-5007-8221-f495aa32a17e | note | SPECIFICATION REFERENCE: IFC Drawings
7812d237-fa72-53ea-9907-40d8db16daa1 | note | ACCEPTANCE CRITERIA: Setout as per drawings
d9e1ea7a-bf6a-5667-b194-7931d2ca5305 | note | DATE/SIGN: Contractor Rep - P
aae0bc18-a83e-5979-821e-ba71e23da7ba | note | ○ CTS Civil Inspector - R
| checkpoint | 9B - Excavation & Foundation Preparation inc Site Concrete
affeaa09-3819-5423-bfc2-8e9c4a59fd7c | note | SPECIFICATION REFERENCE: IFC Drawings
51f4e0a3-bb6f-586c-a9d8-1abd3277ac0a | note | ○ CTS Excavation Works Specification
03667025-54d7-5810-a501-21cda3cc64b5 | note | ○ CTS General Civil Construction Specification
4a0cbdb7-7dfe-5d8b-80a5-b16b7b91e7cf | note | ACCEPTANCE CRITERIA: Excavated as per IFC drawings to line and levels shown
f2216c29-7e2a-58b3-bab3-0593bdad13f1 | note | ○ Foundation compaction Inspection Record completed
e904b868-51ca-5a27-b860-e8d93f19b5aa | note | DATE/SIGN: Contractor Rep - P
cfe40430-7ba3-5065-8886-838beb7f6335 | note | ○ CTS Civil Inspector - W
| checkpoint | 9C - Formwork, Reinforcing & Concrete
33af660b-a477-5715-ac85-1295102c18d0 | note | SPECIFICATION REFERENCE: IFC Drawings
9a0d11c7-5f51-5077-bbf2-c0519d3967bc | note | ○ CTS General Civil Construction Specification
06b73b4a-efe7-576a-b7c6-a448c7afe72c | note | ○ NZS3109/3112
1e995f95-fb56-5722-a366-329a9631e0a3 | note | ○ Manufacturers Documentation
0cc224ad-eee2-55d5-9190-565817c48875 | note | ○ Inspection Records
22ddf9c2-7547-592f-8a90-a0de454de92d | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
1d42735e-9abc-5608-88f3-002804ca41b4 | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
d82337dc-4955-52ee-9ad1-3f6d51aae21f | note | ○ All reinforcing and formwork to comply with IFC drawings
5978997c-9bad-593d-a303-f42f66d9c1b8 | note | ○ Concrete to be min 30MPa at 28 days
a9fd78a9-f6e9-51cd-b728-9efc8b22607f | note | ○ Testing of concrete per CTS Specifications
29c4d6ec-58b2-5629-8a51-2c9d38e3b7dc | note | ○ Prepour Inspection Record Filled out Prior to Concrete
831b69b4-0c14-553e-910e-36ddec90f56b | note | DATE/SIGN: Contractor Rep - P
e7e28e51-3359-5e8a-9481-c7941f93435a | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 10A - Position of Slab Extension Setout
a6c70885-1237-5e3a-9d80-7e54a44443f8 | note | SPECIFICATION REFERENCE: IFC Drawings
29a57d79-fd38-58ee-a6ed-409b94c799b9 | note | ACCEPTANCE CRITERIA: Setout as per drawings
a8966890-33d6-503a-b122-6e5a03e63fa6 | note | DATE/SIGN: Contractor Rep - P
835abeb1-6570-588b-a28e-c07066d077e2 | note | ○ CTS Civil Inspector - R
| checkpoint | 10B - Excavation & Foundation Preparation inc Site Concrete
0c59225d-426b-5eb9-ae7e-9edc33031b73 | note | SPECIFICATION REFERENCE: IFC Drawings
35d19600-4bf2-5e3b-a1ba-9e6e2e51074b | note | ○ CTS Excavation Works Specification
9f14793f-04c6-5c34-ae7b-0318fe0517a1 | note | ○ CTS General Civil Construction Specification
690f7240-1b50-59bd-b8de-4e2fab30b22b | note | ACCEPTANCE CRITERIA: Excavated as per IFC drawings to line and levels shown
30223d43-b313-5568-9b48-022946a1aeb7 | note | ○ Foundation compaction Inspection Record completed
0c0f7e27-eb5a-5a3b-9c83-4efb689468f9 | note | DATE/SIGN: Contractor Rep - P
ea2c5c60-c401-574d-8763-9570b69c7b72 | note | ○ CTS Civil Inspector - W
| checkpoint | 10C - Formwork, Reinforcing & Concrete
4f0e142e-4945-5a25-b17f-49abb3cd647e | note | SPECIFICATION REFERENCE: IFC Drawings
29a8d6ec-f352-5fb5-b30c-094349eb44c2 | note | ○ CTS General Civil Construction Specification
7ea3d663-e0a9-560f-925f-35aa14f2f167 | note | ○ NZS3109/3112
23003765-e2cc-5cbf-b713-7a0eca545e69 | note | ○ Manufacturers Documentation
138a5209-af39-50e8-a344-283076bc0961 | note | ○ Inspection Records
d974fd5b-e525-5aa5-8a5f-f8de93890c38 | note | ACCEPTANCE CRITERIA: All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's.
d630ed08-283b-546a-a58e-e17e724525dd | note | ○ All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted.
fbd6e0ef-3c46-5fc8-9cb5-8fb88275467f | note | ○ All reinforcing and formwork to comply with IFC drawings
7c062043-7ada-5de9-836a-887b76e30859 | note | ○ Concrete to be min 30MPa at 28 days
69f703dc-ff31-503c-a4b8-97869dab5692 | note | ○ Testing of concrete per CTS Specifications
40c46186-e210-55f3-abb2-c1c71af5cbb5 | note | ○ Prepour Inspection Record Filled out Prior to Concrete
f22ee24b-7f1e-5061-a610-20a5b27250ee | note | DATE/SIGN: Contractor Rep - P
58933062-0ea3-5b71-9be7-03312bf6f723 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 11 - Complete final Civil Inspection and close off ITP
66c14816-65ca-58ac-8888-cba232f498f3 | note | SPECIFICATION REFERENCE: IFC Drawings
b71df2a6-7f9b-570f-8495-bf5497863770 | note | ○ CTS General Civil Construction Specification
0d453ec2-f050-508a-bbdd-0f4e0f8ddcc9 | note | ○ Manufacturers Specification
9a2dd5b8-959c-597f-874d-712ecd5f8973 | note | ACCEPTANCE CRITERIA: ITP/QC has been completed; all steps & hold points signed byrelevant party.
594e5a3d-f787-51c2-b981-b37a17b1f5f4 | note | ○ All work completed as per work pack, and any field instructions issued during construction compiled
ff62b707-b324-5c89-8b5f-02028973c6c3 | note | DATE/SIGN: Contractor Rep - P
859e308d-4afd-5754-ba03-4512b3dbe1e8 | note | ○ CTS Civil Inspector - H
| signoff | HOLD POINT
| checkpoint | 12 - Non-Conformance Reporting
5ffbb2cd-32e1-5f8f-8bf3-52c6adc1bfd4 | note | SPECIFICATION REFERENCE: UCC Internal NCR and or Lucidity event NCR
fcd8f443-4710-59f5-89cc-f0a4874e8789 | note | ○ QC Requirements for Civil Works
c702d77f-f278-5548-8cc4-d1ec227384de | note | ACCEPTANCE CRITERIA: All Non-Conformance reports and Investigations are attached and closed out
f9822a94-bb06-5e2f-b355-e91091e9a173 | note | DATE/SIGN: Contractor Rep - R
| checkpoint | 13 - As Built & Final Design Documentation
e59f8b8e-a15b-50f9-863d-f33dc925e698 | note | ACCEPTANCE CRITERIA: Confirmation From Engineer on as built records & redline mark ups
3400d94f-c590-5556-97d8-f02b0109d68e | note | DATE/SIGN: Contractor Rep - P
| checkpoint | 14 - Reference Info, Specifications
74408157-1fb1-572b-80ae-c9db22b85b9d | note | ACCEPTANCE CRITERIA: All Reference Information and relevant Product Specifications
528c98b0-965a-52bc-984c-a7da35a863c8 | note | DATE/SIGN:
| checkpoint | 15 - Punch Listing
0963cbbb-e9b0-5b5d-87dd-a62360b70442 | note | SPECIFICATION REFERENCE: CTS QC Requirments for Civil Work
b171023d-4b16-5075-8c2b-8f5734211755 | note | ACCEPTANCE CRITERIA: All punch list items are closed out in the relevant timeframe to the required standard
5a210d89-74f5-5dfd-a31d-f20124920c58 | note | DATE/SIGN: Contractor Rep - P
ca2a679d-3bc0-5416-a954-f182b1464e98 | note | ○ Project/Construction Engineer - R
| checkpoint | 16 - Compilation of ITP
7c8bfb5e-8e25-58b0-a4f4-5f2beef2fef4 | note | ACCEPTANCE CRITERIA: ITP Completed and Signed off
4dc37894-7258-57d7-9387-666d76b42912 | note | DATE/SIGN: Contractor Rep - H
faf5d619-7aa8-535d-821b-f5c168bc43f3 | note | ○ Project/Construction Engineer - H
| signoff | HOLD POINT