## Table 1
Item | Process Description in Sequence | Quality Control Activity | Acceptance Criteria |  |  | Verification | Inspection Activity
|  |  | Acceptance Criteria | Reference Standard |  | Recording Document | Activity | Activity
1 | Corrosion protection prior to new steel going to site. | — | — |  | — | — | — | —
1.1 | Degrease and clean | Degrease using degreaser and two rag method | All surfaces free from oil, grease and other contaminants |  | Paint Manufacturers specification And AS 1627.1 | Paint QA Sheet | P | W
1.2 | Atmospheric conditions checked for blasting | Relative humidity should not exceed 85% and difference between steel temperature and dew point to be 3 and above | Work protected from unfavourable weather conditions and no work commenced within dew point conditions |  | Paint Manufacturers specification And AS 1627.4 | Paint QA Sheet | P | M / R
1.3 | Abrasive blast with non metallic media to Sa2.5 blast with a profile between 35 and 75 microns | Dry Abrasive blast using best practice to Sa2.5 cleanliness with a profile of 35 – 75 microns | Visual inspection to Sa2.5 standard. Profile measurement using Testex tape to between 35 and 75 microns |  | Paint Manufacturers specification And AS 1627.4 And AS 3894.5 | Paint QA Sheet | P | H / R
1.4 | Check Abrasive Blast profile | Profile to be in range of 35 to 75 microns. Use Testex tape or profile gauge to measure profile. Record to Daily inspection sheet | Surface profile to measure between 35 and 75 microns |  | Paint Manufacturers Specification | Paint QA Sheet | P | D/M/R
1.5 | Atmospheric conditions checked prior to applying the first coat of coating system | Relative humidity should not exceed 85% and difference between steel temperature and dew point to be 3 and above. | Work protected from unfavourable weather conditions and no work commenced within dew point conditions |  | Paint Manufacturers Specifications and AS 3894.7 And AS 3894.10 | Paint QA Sheet | P | D/ M / R
1.6 | Application of Coat #1 | Applied within 4 hours of last abrasive blast and before any discolouration of the prepared surface occurs | To reblast if there are changes to the prepared blasted surface |  | — | — | P | M
1.7 | Mix paint as per manufacturers recommendations | Coatings to be mixed by power mixer or paddle. Allow induction time as per manufacturers recommendations. Record batch numbers | Record of Batch numbers |  | — | Paint QA Sheet | P | M/R
1.8 | Stripe Coat all edges (except those being welded), welds, bolt holes, inaccessible areas, etc | Brush apply stripe coat to areas as required. Record paint quantity used | All edges, welds, etc are coating |  | — | Paint QA Sheet | P | —
1.9 | Apply full spray coat of the first coat to all surfaces | WFT measurement by wet film comb as per AS 3894.3 Appendix 3. Record paint quantity used | 50% overlap with no misses or runs. WFT as specified and checked by painter regularly using a wet film comb |  | AS3894.3 | Paint QA Sheet | P | M
1.1 | Cure time of first coat | As per Manufacturers specifications and product datasheet | Coating to be cured to recoat and hard |  | Coating to be cured hard for either recoat if required and for transportation | — | P | M
1.11 | Dry film thickness check of first coat | DFT as per manufacturers specification and as per AS 3894.3 | Coating to be at correct film thickness as per manufacturers specification |  | AS 3894.3 | Paint QA Sheet | P | T / R
1.12 | Repair defects as per repair specification – increase coating to low thickness areas | DFT acceptance criteria as per AS 3894.3 | Coating conforms to the DFT requirements |  | AS 3894.3 | — | P | H
1.13 | Repeat Tasks 1.7, 1.9 – 1.12 for atmospheric checks, mixing and application of the subsequent coat | Refer Tasks 1.7, 1.9 – 1.12 | As per Tasks 1.7, 1.9 – 1.12 |  | As per Tasks 1.7, 1.9 – 1.12 | Paint QA Sheet | P | —
1.14 | Final inspection prior to handing over to transportation | DFT acceptance criteria as per AS 3894.3 Coatings conforms to the DFT requirements. | Coating conforms to the requirements |  | Paint manufacturers specification And AS 3894.3 | Paint QA Sheet | P | H
2 | Complete final inspection documentation for presentation to the client | — | — |  | AS 3894.12 | Final report | — | —