## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | 8.1B - Stormwater Drainage Checklist |  | 8.1B Stormwater Drainage Checklist | 31019e13-fb18-46df-9706-18c64a073780
| checkpoint | Stormwater Drainage Inspection Report Details:
a518a3d8-fa2b-515d-8b27-e19692a4d2c5 | textbox | Spec No.:
78df9ed2-6975-5795-a426-4ed7501bc7a2 | textbox | Drawing & Revision no.:
2dd7837e-1ca5-532d-b182-c0db4f7aad71 | textbox | Shop Drawings no:
442468af-2993-5c7c-9adc-8642b9f9aee4 | textbox | Starting IL established:
| checkpoint | Pipes and fittings comply with relevant Authority and Specification
d5db6557-0b2c-58fa-86f1-f0e43eff5022 | note | Spec#: AS3500 and Project Specification
b84c2db7-6d56-57dd-88bb-7a004d1277de | textbox | Materials used, Size and Class:
5d37cd03-ef3d-5ac5-ac55-972687038104 | button | Approved by Principal | Yes,No
| checkpoint | Pipe Lines
69a33f73-40a1-5196-bf45-23b6d692ba84 | textbox | Date started:
93b7a854-6d82-5422-b87c-fdf737460dbf | textbox | Drainage Line Number:
10ae2433-de59-5db1-8935-31a419603811 | button | Pipe Damaged? | Yes,No
03ff89f5-e6af-5965-86d8-dfeff5a5c63e | textbox | Jointing Required
a702c9dd-ef8e-5f33-a612-817477dabdbe | button | Bedding and Haunching | Yes,No
| checkpoint | Bedding material, placement and compaction meets specification.
d91c8973-d477-5810-b6f7-7715ee597a09 | note | Spec#: AS3500 and Project Specification
845850d1-c235-51bb-9c51-2bd91422b8c7 | textbox | Material used:
aeb97833-4f95-5a06-b8c7-dab204cd6ed3 | textbox | Docket #:
27ef9937-6c12-58be-aaee-2902d5a859e1 | textbox | GPL - Initial/Date
10babc41-54d1-5891-8d32-deefd918eb4e | textbox | Builder - Initial/Date
| checkpoint | Laying and jointing of pipes - RL and fall
c4c9db9b-38bd-5627-b5aa-f1dd2c7c4374 | textbox | Jointing Type:
3e2a1007-64bd-5473-9fae-3569956f0cab | textbox | Fall:
a7cab045-a361-5ddf-9fbe-40c7f5d30a7f | textbox | AS3500
324b5590-b8c0-5f90-a22b-b1ac380eecdb | textbox | RL's as installed
ea24c644-9f7d-5750-88d1-53a7a6ae877d | textbox | GPL - Initial/Date
edcf5743-e0e2-5a4b-88a3-7907faff774d | textbox | Builder - Initial/Date
| checkpoint | Backfill
25149430-9abf-5571-979a-2a28e2249ca2 | note | Spec#: AS3500 and Project Specification
a1fdc9ea-e225-5ea1-a9ab-5c4dd7616f84 | textbox | Material used:
7bb49017-c31f-58ed-b3d4-bac77ea8740f | textbox | Docket #:
| checkpoint | Pit Sign off: Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
a5253301-ce85-5a11-aa3a-f9ef7fe57ead | button | Geschke Group Signature Sign-Off added below | Yes,No
d7de7f2d-4733-553d-a5c1-0c99b04744c7 | button | Builder Representative Sign-Off added below | Yes,No
| checklist | 8.1F - Installation of Stormwater Pit Checklist |  | 8.1F - Installation of Stormwater Pit Checklist | aebf482a-1e63-429a-ab36-8c368226089a
| checkpoint | Stormwater Pit Installation Report Details:
4530b6f0-511d-5cac-b71f-a150a35bb2d3 | textbox | Pit Number:
8969db26-bf20-5072-8e79-d5c4a3886556 | textbox | Pit Type:
e70f9431-bad5-55bf-95e4-0c06edab0266 | textbox | Project Specification:
fddc1332-7a89-592d-86f6-5f95772aaa0e | textbox | Drawing & Revision no.:
9459c17e-e4ad-56ee-8b7a-9379a8410f5f | textbox | Shop Drawings no:
746ffff3-e3a3-5f75-a79a-ec65357aeee8 | textbox | RL of the bottom of the pit
| checkpoint | Bedding material, placement and compaction meets specification.
04c4f4fb-f8e2-576c-80aa-e27846fac6b5 | textbox | Spec#:
c310417b-977f-5e42-b877-75f5d549d81b | textbox | Material used:
| checkpoint | Pit installation
de201c90-8ca2-5d2d-bc7b-232d98f783aa | textbox | Date Installed:
f9d00011-c097-510f-a203-4138dfb7931e | textbox | Pit Base:
117d75e4-9f4f-58a1-83fe-c9762ccb7613 | textbox | Step Irons - GPL Initial/Date:
863d456f-01f9-5915-bed2-f2aeaaa95bc9 | textbox | Outlet IL
95116407-0787-50bc-b5a0-e9bd85817127 | button | Placement of cover | Yes, No
a89c6c3e-c164-5ef1-8808-a5f4d59ec00b | button | Concreting of cover | Yes,No
| checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
c9d3d3e7-74a5-5f0c-818c-dff309e1062f | button | Geschke Group Signature Sign-Off added below | Yes,No
bf881782-6d86-5ebf-a177-757ed33607b5 | button | Builder Representative Sign-Off added below | Yes,No
| checkpoint | Backfill
f945b33d-7f5d-5ff7-aedf-fff3be7b176c | textbox | Spec#: Project Specification
db692b20-8012-595f-a0d3-b2a54bf33250 | textbox | Material used:
| checkpoint | Hand-over Photos
| checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
42f96199-8cb8-5c3d-a965-f9c7dc412ea6 | button | Geschke Group Signature Sign-Off added below | Yes,No
3e0705ec-9a85-54b4-b2e4-67831318178f | button | Builder Group Signature Sign-Off added below | Yes,No
| checklist | Add Project Photos |  | Project Photos | 42db5763-09c3-49c7-bef0-debfcc0ddf2a
| checkpoint | Attach Photos and Comments
| checklist | Backflow Test Report |  | Backflow Test Report | a1d7c54e-7e9b-4814-9d89-527bfa6a7a69
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Description of property or vehicle
1af4966f-be03-57bb-b487-18edcd9b69a3 | note | The description must identify all land or vehicles covered in the application
35727210-b84c-5a45-835d-3fbbf6893fa0 | textbox | Street address (number, street, suburb and postcode)
2f5dc3d1-09e3-5a82-8f6f-48f3eb3376cd | textbox | Water authority property service / installation number
78dd17a4-c14d-5d33-a486-b081296d819f | textbox | Water meter number
| checkpoint | Type of test
11c447e3-d605-5521-8090-c80f7579aac7 | tickbox | Commissioning of new device
8b97ffe1-8369-5753-87a8-1d246f75f8bb | tickbox | Replacement
435f6d09-c382-53b7-ad63-02dd5b14d944 | tickbox | Annual
62318c17-2a6b-523a-af42-b56f39423c92 | tickbox | Repairs
821e82c6-8391-5935-ad30-286e39ada845 | tickbox | Decommission
| checkpoint | Backflow prevention device location
dd01ad59-061a-55ac-9a89-c8366b894f8a | textbox | Location of device (eg: Northwest side of building @ FHR external)
4879183b-24e9-5527-93c5-23c18296b3e2 | textbox | Mains pressure (kPa)
dbe3c427-f08c-5351-ae65-90556d1fd44d | textbox | Time and date of test
| checkpoint | Main device
a7b7bce9-6394-5db4-90ce-37d2a88fc3f5 | tickbox | RPZD (E)
a4d65809-4558-5af6-a8d4-8e2b46c7bd6f | tickbox | DCV (F)
a0ff65aa-eb56-5e44-9048-aca04dd003a4 | tickbox | SCVT (I)
f69c9a6d-fc5b-57b7-8f03-c1231e34fdfd | tickbox | Containment
767d8bfb-1da2-57b8-b6c3-7647de2964bc | tickbox | Zone
c90c8f75-0ada-5a98-9049-dcd4b0954190 | tickbox | Individual
f5f5abfd-07e1-5026-b3b9-5fd1ef2116cb | textbox | Make
c88b37d1-7e3b-59fb-80d1-1949dc6b2c80 | textbox | Size mm
24b10d62-e38f-54d0-bf70-91d15ee20f3d | textbox | Model
f81c3e40-e902-5843-8211-24d7d74cb9be | textbox | Serial number
ab71ba88-7fa9-5fb7-a6c3-6a02e34f2930 | button | Cleaned strainer | Yes,No,N/A
480bd7ef-37d5-5b7a-867f-26e23d6d18fd | button | Upstream IV | Leaked,Tight
cd1d257b-0249-55b2-8dbb-77d302829b6d | button | Downstream IV | Leaked,Tight
23aa547c-f7ec-5024-bc60-cec0baa474fa | textbox | Check valve #1 (kPa)
4eefdd01-c50f-5246-af1b-727f1945686b | textbox | Check valve #2 (kPa)
642a69f1-3656-5fcc-81db-9652157e5f93 | textbox | Relief valve opened
| checkpoint | Device installation notes
13c7d253-c3a0-59d6-b8c3-b9fda6322d8f | button | Isolating padlocks installed | Yes,No
cff36285-85f3-5a5b-beaf-87b515b66c7e | button | Installation complies with AS/NZS 3500.1 | Yes,No
| checkpoint | Test kit
a8b3d96e-4c8d-505e-b3e5-145f2594da40 | textbox | Test kit serial number
c302aa58-f18b-5bde-bfa8-3b08f412ca5e | date | Date last calibrated
| checkpoint | Authorised testers details
75f362e0-7810-5f90-bddc-fde2b7e58845 | textbox | Testers name
844152ee-5ca0-569f-85de-3c5baa28a3b7 | textbox | Registration licence number
3c1862dc-49a8-5c69-83dd-c053189ab195 | textbox | Phone number
| checkpoint-no-value | Licence person
b18446b0-a31c-5ed6-b412-d4fadce02ed8 | note | Full company name - Geschke plumbing
261c0f6e-7685-5252-9e08-fb638798b0d7 | note | Licensed tester name – David Geschke
d83f9ae3-3775-5380-9f8c-3b96377b3a42 | note | Licence number -50043
| checkpoint | I hereby state that the information provided in this form is a true and accurate record. I have tested the above device/s in accordance with AS/NZS 2845.3:2020
2925c5e0-50f7-5b81-a4bd-f538b6eed895 | note | Note: Failed devices must be repaired and retested within 20 business days as per the Water (Estimation, Supply and Sewerage) Regulation 2014.
0eee7ac9-d021-5f60-a770-8eb79cbd7c16 | textbox | Signature licenced plumber
9ec203bd-e8e0-53f6-b639-d44f223f087c | date | Date
063813a1-8ba1-5e22-b59d-e49856282138 | textbox | Signature tester
5e6fe529-bee1-5a29-a12c-e7f77275af41 | date | Date
| checklist | ITP - Subsoil Sample |  | ITP - Subsoil Sample | 0f2dec3e-7882-4be4-954a-e5d7fc2bab89
| checkpoint | 1. Approve specialist subcontractor
9d4eb838-dc73-55bf-b69f-c9def836fd57 | note | STAGE / FREQUENCY: Prior to awarding subcontract
da6e934e-11e9-50eb-aafc-cf7d43313983 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
3828bc0d-05a7-5c3d-8b7a-7e232b6d0c0a | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
df637440-df77-5b80-bda8-ca27cd6c0396 | note | INSPECTION / TEST PROC: Document
907bdaa2-ae11-5fe7-9b4a-b8726c61cc84 | note | INSPECTOR / APPROVER:Subcontractors Authorised Representative. Geschke
009442fb-4d6f-5780-9dd0-e1d259c035b1 | note | HOLD OR WITNESS POINT: Hold Point
| signoff | hold point
| checkpoint | 2. Approve Samples
e0753a28-228e-5b33-9dba-1f2ef8737545 | note | STAGE / FREQUENCY: Prior to ordering materials
ed2c4902-525f-5084-83cb-3597d98e2b4a | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
c0924802-0d21-5273-893a-36a5e749e8ad | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
8d3a4a13-88ad-57f7-bd57-5569ee6bb812 | note | INSPECTION / TEST PROC: Document and Review
bb6eba40-717f-5c47-a5a4-f9c280ce59a9 | note | INSPECTOR / APPROVER: Engineer. Geschke
b89ccf68-12f6-572d-8e63-5c97722e8790 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 3. Approve technical details
fd160c9e-62e4-5bb6-b481-0cf089407b1f | note | STAGE / FREQUENCY: Prior to ordering equipment
4844bcc0-5510-5ea7-954d-5709d6e77639 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
8688973e-580c-521e-a2ef-ab63fd5d5227 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
bcb9c29c-4d10-58fe-9307-f7fb3cb80757 | note | INSPECTION / TEST PROC: Document and Review
650067d7-f4fd-51b4-b854-7a1c032537d0 | note | INSPECTOR / APPROVER: Engineer. Geschke
e435cb21-9254-5f72-8f6b-dd34ca67dd9b | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 4. Approve shop drawings
e745eb57-8603-559c-a4c8-0161dad852a7 | note | STAGE / FREQUENCY: Prior to commencement
7610d3ca-cefb-5da4-b772-f9b08eaa1ef8 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
0d000ef2-9abb-5855-acad-717d29720935 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
6c873f21-a11b-5fe2-8348-eb058d7a2b10 | note | INSPECTION / TEST PROC: Document and Review
04480fbd-5b24-5218-9ae0-41a1add9a686 | note | INSPECTOR / APPROVER: Engineer. Geschke
840e34bf-364b-55b0-853c-dbb09dc2b066 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 5.01. Check set out - Works by Delta
2f5d3c92-b74b-5a37-8791-2b7410bd4ade | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
4aef75fb-96f1-56e4-a30c-94d2366ef86d | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
896486f4-d9e0-589c-bfbd-ff59e938c842 | note | Height control point is marked within 40m of works area.
910ebd13-ef48-5195-b307-d22c12848672 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
80584e9f-b783-579a-bdbf-2d373956ff7d | note | INSPECTION / TEST PROC: Visual Inspection and Document
c9f3304a-3c33-5973-8975-2616504cf418 | note | INSPECTOR / APPROVER: Foreman. Delta
9ad7cf58-d4a5-5db8-940f-68975769d27e | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 5.02. Check excavations
31fae4e3-e09c-5061-9060-86d4ed0daa19 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
18382bba-eb68-52bb-9f70-b9de3e873c02 | note | RECORDS: 'Before' Photographs
5075a1a9-1580-5548-9343-0db42c4f4c21 | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
016f9252-71f9-5743-8531-0c0edce96d79 | note | Minimum falls
f47f7e19-4586-5d39-a733-9f6a253768d1 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
01fbf527-7206-5681-a244-1b6f59c3a7a4 | note | INSPECTION / TEST PROC: Visual Inspection
65e836c8-b615-5f9b-83b1-d0f9b5e3c02f | note | INSPECTOR / APPROVER: Foreman. LLB
a5e514d7-adb8-5b8e-a394-df6e6e372568 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
57bd8763-fd51-5070-8dbd-e9262baa04b7 | note | STAGE / FREQUENCY: Prior to commencement / Each TMP
aea906af-f26d-5f81-a1ee-1b30392f229b | note | RECORDS: Copy of Consent and Traffic Management Plan
a845e705-da73-5d36-9ed5-764c10af7bc9 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
08946a2c-eb10-5c8c-8cd0-14ff16e194b6 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
b4a32c14-779b-55e0-80ae-e31020b76fe2 | note | INSPECTION / TEST PROC: Document and Review
aa2b6ade-d039-5ed6-a124-dc0b69f55bf2 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
591e8f8c-978e-5af7-bfff-6f6f28f8ca68 | note | HOLD OR WITNESS POINT: Hold Point
| signoff | hold point
| checkpoint | 6. Check deliveries of materials
9d8a4093-5711-5eb3-b30a-82ec2309416c | note | STAGE / FREQUENCY: Each delivery
ddafe402-bf29-5e52-b6e8-92002eeb9866 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
55a02ce1-c761-5c8d-997b-7809e49d42e3 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
dfdcc1cd-2aab-5726-9c19-8cebf0825dea | note | Grade or class matches design
71d23c89-7dbb-5c18-83ea-76f954556b73 | note | Size and thickness matches design
9e1a1ba9-8427-5d9b-b242-3800df4375a3 | note | Supplied items are free of defect
86dcfe28-9be5-5a81-8866-6cc13cd393e9 | note | Marking, packaging and preservation is fit for storage / construction.
2e6802d8-89c9-5e57-b922-6504e966cc46 | note | INSPECTION / TEST PROC: Visual Inspection and Document
9dc8ff4e-5257-53de-b86c-2fa4ad32b710 | note | INSPECTOR / APPROVER: Foreman. Geschke
4d05ae0b-3ec3-50be-9af1-cdcd43203737 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 7.01. Check below ground pipework - pipes and fittings
6587e6f6-8857-58ce-a81e-e69a0d7f018e | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
51ff1b33-3f20-5c1b-946d-dfe5b18568dd | note | RECORDS: 'During' Photographs & As-built Survey by Delta
f63e3666-152a-53fe-a6b3-93c60acab6a4 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
11d98606-c4df-5995-9604-5b5d4a5065c2 | note | ACCEPTANCE CRITERIA: Joints, fittings and connections match design
19fc3ed7-2d4a-598e-b197-9e5525441206 | note | Alignment and position are as drawn
a9d3c499-2d16-5906-a2f6-2d40e1ab833e | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
f87725be-7882-5a46-839c-7d99fe66332b | note | INSPECTOR / APPROVER: Foreman. Geschke
63902c13-9d83-5cb0-8476-8552efa85cd8 | note | HOLD OR WITNESS POINT: Hold Point
| signoff | hold point
| checkpoint | 7.02. Check below ground pipework - high ends and flushing points
a23ebf66-8470-51c4-ad24-e68cff41e6bf | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
a5f06519-a097-5c0a-9438-394f9a11ff00 | note | ACCEPTANCE CRITERIA: Capped at surface level with hinged lid, cast iron box in concrete surround 300 x 300 x 150mm
d7d6e1b7-55fc-5b3d-9010-dbf2121c3186 | note | INSPECTION / TEST PROC: Visual Inspection
85aa3c7c-a514-53f4-a494-cd0d9424b2c1 | note | INSPECTOR / APPROVER: Foreman. Geschke
d859aba2-bb4e-5787-9ff8-f51eca18a00d | note | HOLD OR WITNESS POINT: Hold Point
| signoff | hold point
| checkpoint | 7.03. Check below ground pipework - haunching, surrounding and encasing
116b7a4d-b37b-5890-9c19-2ef492f2425a | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
ad62d472-435e-5bb3-814b-d16aae29631e | note | RECORDS: Photograph
46a79d42-7477-5de8-9968-d405dfe77cd8 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.19.3
c0fbbf83-66c2-59b7-ba63-11f2dd49fd9a | note | ACCEPTANCE CRITERIA: Free draining granular material
61b3c230-eedf-5c4c-ab90-9f05e93e2c39 | note | All faces of filter material in contact with topsoil or similar shall be covered in geotextile
ce343597-2b89-547e-adae-4bf2831ea165 | note | Material used is as specified and approved.
918be02e-b6a6-5a1a-9839-eb369acd7333 | note | INSPECTION / TEST PROC: Visual Inspection
d2767c7d-2d8d-5d33-bd5f-f4856228c8a9 | note | INSPECTOR / APPROVER: Foreman. Geschke
d74f6797-3c56-5c4d-8779-04c503ef3494 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 8. Check Completed Surface - Make Good
dce6dc94-4517-57ea-b403-733cfca67c81 | note | STAGE / FREQUENCY: Prior to practical completion
e3846798-21c4-50e2-940e-4efa5c61d919 | note | RECORDS: 'Upon completion' Photographs
9e0ec8ef-887d-5a06-a253-0d1424e803ed | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework less depth of works by others
1cc14c4a-453a-5a62-b1fc-462636b96b1d | note | INSPECTION / TEST PROC: Visual Inspection and Document
33e2b17a-1c55-56c4-9246-90f468242246 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
99c569b5-7437-5d5d-b0e6-884ae95e3856 | note | HOLD OR WITNESS POINT:
76009441-b406-5a2c-b191-3ae372055b22 | note | HOLD OR WITNESS POINT: Hold Point
| signoff | hold point
| checkpoint | 9. Obtain 'as built' documents - Works by Delta
93c52f42-ea40-521c-b108-a5f5e2cff2cb | note | STAGE / FREQUENCY: Prior to practical completion
8087767b-333f-5e05-9eb0-7043923ed488 | note | RECORDS: As built documents by Delta
723ca511-6a90-5520-b884-1220284158e5 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
07a79762-12e9-5e5c-9b4f-6af501b5b26e | note | INSPECTION / TEST PROC: Document and Review
6b1a0a76-d16e-511f-9238-c077e472a5a7 | note | INSPECTOR / APPROVER: Engineer. Delta
89918e03-93b9-50cf-9589-ffe0837930f3 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 10. Obtain operating and maintenance manuals
63efa2eb-fea7-582c-9919-aa2f8ceebea5 | note | STAGE / FREQUENCY: Prior to practical completion
de7d9af8-0442-5628-bcca-4f3d8d4daf8c | note | RECORDS: Manuals
a5d4f506-c0bf-511e-8f30-2ea093e4fea4 | note | INSPECTION / TEST PROC: Document and Review
6cfa71b0-06d6-5bd2-ac4e-59806bcedd44 | note | INSPECTOR / APPROVER: Engineer. Geschke
59e07c13-61cc-510b-81e0-f2db1f8b0938 | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 11. Obtain Guarantees
814f23f8-7599-53fa-995a-51f98f900fa4 | note | STAGE / FREQUENCY: Prior to practical completion
345d632d-1f3d-565d-b1ce-16d22c671d99 | note | RECORDS: Written guarantees
7728e5a2-8c4d-5c9c-8a38-f72b7aa1f7a4 | note | INSPECTION / TEST PROC: Document and Review
fa565cb3-984a-5bb4-8f59-55e1254fdfd8 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
d11330c1-db74-536f-8249-dcd3a19b564a | note | HOLD OR WITNESS POINT: Witness Point
| checkpoint | 12. Final commissioning & inspection
12376f84-d771-574e-aabc-7a1854862690 | note | STAGE / FREQUENCY: Prior to practical completion
a1830aad-a648-517b-95fd-6d5a7638c5dd | note | RECORDS: Final commissioning checklist
a716b483-bd9d-5d53-a3a8-c2e10802245f | note | INSPECTION / TEST PROC: Document and Review
adbdd134-9141-5c13-b0ee-710c899fc6f7 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
40201bcc-ad44-5507-b1d8-b31c30f5ba1c | note | HOLD OR WITNESS POINT: Witness Point
| checklist | QA 9 - Non-Conformance and Rectification Report |  | Non-Conformance and Rectification Report | b44362d0-376a-4e1e-ba62-cab8333be67d
| checkpoint | Non-Conformance and Rectification Report Details:
497480bc-16f9-57d1-a38d-b53f285ead12 | textbox | Drawing No./Rev:
6c7020c8-cb4b-5056-aedc-1eda68789ef9 | textbox | Zone or Grid:
c1b1944f-9e73-5dfc-85e7-ed80a4769931 | textbox | Issued To:
ec26a073-1fc2-5a02-a43e-1a4975f7246c | textbox | Item Not Conforming
0344f07b-d886-595d-ac05-a2e52a3647ab | textbox | Reason For Non-Conformance
6a8fe17b-aeec-5947-a7ad-703f786a7e75 | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
162acb0a-6221-5ed8-b32e-8bf9074941a4 | textbox | Action Required:
49bb3ead-9d10-58ba-b134-b5dc0c361c05 | textbox | Date:
41c65d3b-845e-51e2-b40e-83856850ea32 | textbox | Rectification:
b80c061a-a1e2-5ec9-a894-87917f2ade88 | textbox | Date:
2942d0e2-7101-5037-8548-4a3587576906 | note | Note: Non-conformance register to be updated
| checklist | QA 11 - Equipment Calibration Register |  | Equipment Calibration Register | b8d661de-740a-4725-bf6d-7cd96ba52dd5
| checkpoint | 1
b4d2c565-6cee-5beb-9f2a-9a346000f629 | textbox | Equipment Type:
be6ab2aa-d446-582d-a849-bfe836eb24eb | textbox | Manufacturer:
47593f44-3f6c-5547-84c2-26e0bbe47831 | textbox | Model and Type:
5941931a-1aa8-58e8-be93-967243c88d47 | textbox | Serial No.:
c86e3e82-4a80-595b-9779-716c2b19f620 | textbox | Next Service Due:
| checkpoint | 2
0306dcf0-68f3-549c-9016-f7af3b1c6ec3 | textbox | Equipment Type:
33c0b8b5-8807-5a36-8e57-78e3b2cffd0b | textbox | Manufacturer:
9bc41edb-c3df-5933-9cb9-88e19a0a352f | textbox | Model and Type:
95d17765-6174-52b6-af43-d2574c3cf7c2 | textbox | Serial No.:
974f94f4-32e3-5b07-b53e-96a207c4e5a9 | textbox | Next Service Due:
| checkpoint | 3
76a02e6d-6074-56d0-87c9-bedee5e2fd92 | textbox | Equipment Type:
191cf691-0333-562f-84d4-a19180c8c35e | textbox | Manufacturer:
f4614282-7975-5463-b1d2-174c3a96397e | textbox | Model and Type:
c30ae13d-364b-5dbc-b392-cb79271ea4f3 | textbox | Serial No.:
52bb628b-cc74-5d15-9174-7a2093a79f63 | textbox | Next Service Due:
| checkpoint | 4
3707671d-ca0d-57a3-adeb-787ad49847d6 | textbox | Equipment Type:
6b916005-e6be-5e93-abc6-40dfef2a82c7 | textbox | Manufacturer:
2ae7293d-67a1-55c5-8559-1f1c7f0191b0 | textbox | Model and Type:
2b5afd9c-bed7-563d-9fba-8740e3731118 | textbox | Serial No.:
b1afa72f-9aca-5386-9ef9-0af842e99e74 | textbox | Next Service Due:
| checkpoint | 5
069ace06-2f9e-5ec9-b970-a842724880ea | textbox | Equipment Type:
29c5bf83-58d0-556f-92ca-4404d9c3b2bf | textbox | Manufacturer:
3f11dbde-edf2-5bbd-8c1a-ca5495acda6f | textbox | Model and Type:
502d77c5-8f9b-582c-8fe8-11abd0c65c6f | textbox | Serial No.:
bd6fb2a4-219a-5322-ba03-0382fa934a03 | textbox | Next Service Due:
| checkpoint | 6
e8563fe9-3fbd-5210-841b-411bcfb2df35 | textbox | Equipment Type:
a2683913-abd9-5c90-9c8b-40899f0ea4c3 | textbox | Manufacturer:
8b366f34-db94-5c4d-a37b-98b8864a9024 | textbox | Model and Type:
556b2989-7730-5701-9d81-b0d8702a4a5b | textbox | Serial No.:
3bdbd6e4-a10e-5320-a32f-41e2025dab39 | textbox | Next Service Due:
| checkpoint | 7
d9b32f47-74f7-5c54-86e7-29b5eb68f311 | textbox | Equipment Type:
c25f1b07-ccd9-545d-bcf1-70f7de3772ae | textbox | Manufacturer:
557ae0af-ae79-52fe-ac32-5ae783bfbd24 | textbox | Model and Type:
da86f339-f33c-5594-ad94-a07efba683a0 | textbox | Serial No.:
34b3d541-2c85-5e93-8711-8208ef1ae94c | textbox | Next Service Due:
| checkpoint | 8
45af7411-27d7-5290-a4f3-e3c060b1732d | textbox | Equipment Type:
439911d9-6d5a-58b9-9d9a-e5fbb711d9e6 | textbox | Manufacturer:
fbc2bbb8-1c08-5ed5-b94a-64d9a782f33c | textbox | Model and Type:
ac8e6743-b058-5e6f-bfa5-336be58119a7 | textbox | Serial No.:
50731a42-0a37-550f-aacf-70906c6fcaa9 | textbox | Next Service Due:
| checkpoint | 9
1663dd13-3559-5831-919c-49102d9fec96 | textbox | Equipment Type:
c8f55def-8873-5711-ad58-9ea5462b3445 | textbox | Manufacturer:
fac8902a-ff44-5501-b258-36913a18b048 | textbox | Model and Type:
9e3de27c-9b55-5e59-bc48-2a233c014957 | textbox | Serial No.:
38356761-d8a1-5f92-89db-89d0b9e489a8 | textbox | Next Service Due:
| checkpoint | 10
f44f60a4-ad2e-59a7-83c3-f267d022f77d | textbox | Equipment Type:
f1ff474c-26e8-5ddf-909d-0cdb53b8d9dd | textbox | Manufacturer:
a001f1d9-90a7-5634-9641-fc9b22fc172d | textbox | Model and Type:
ca7d7f0c-915c-5e5b-9c73-6e0c60b161d6 | textbox | Serial No.:
caafb20b-52c7-5415-9dbe-4f70c7fc52a1 | textbox | Next Service Due:
| checklist | Safety Shower Functionality Audit |  | Safety Shower Functionality Audit | 5f22f409-936e-4e4b-a8d4-3c2665b771b1
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Accessibility
4236103e-0e45-54db-b989-da6d8b475dda | note | Is the location of the product in an accessible area, eg, no more than 10 seconds away from the hazard and has a clear path leading from the hazard to the safety product.
| checkpoint | Identification
b10d7e29-5ffd-5e20-ad55-69455eefb2d9 | note | Is the safety product clearly identified with appropriate signage visible from the hazardous area
| checkpoint | Support Brackets
268906f2-d6af-507f-bed5-d65de15b1782 | note | Is the safety product securely fixed with corrosion resistant anchors and brackets
| checkpoint | Installation details
64282624-58f5-5ef3-9420-c6eb3a5a8745 | note | Is the safety product installed at the appropriate height
| checkpoint | Exterior and operating instructions
6460c33c-25e2-580b-a9ee-43d9232a9095 | note | Is the safety product fitted with operational instructions and a test tag
| checkpoint | External Damage
e8deed0d-3ae8-5c49-b71e-6ee8919cc544 | note | Is the safety product free from visible damage
| checkpoint | External Corrosion
9f74bef6-c3ea-5952-88e7-e0aad24a78a9 | note | Is the safety product free from external corrosion
| checkpoint | Activation Points
fa09c7ae-1210-5a5d-9434-1b2f60a7eead | note | Are all activation points secure and in good working order
| checkpoint | Leak Test
f1f06e6b-8386-51f8-aaf4-68e134109b50 | button | Check that shower/eye/face wash has no leaks - shower rose. | Pass, Fail, N/A
fc1223fd-c01a-5880-98ce-ad840d47ff84 | button | eye/face outlets | Pass, Fail, N/A
e01851a3-8fbb-5900-82ed-6c0a4d4c41a4 | button | ball valves - shower 1" | Pass, Fail, N/A
e532184c-54e3-58b0-8c37-6e2c6e5b61bc | button | ball valves - eyewash 1/2" | Pass, Fail, N/A
| checkpoint | Dust Caps
2b1a2d9d-40d6-5460-b4e4-8919337ced3f | note | Are the dust caps correctly fitted and in good working order
| checkpoint-no-value | Flow details
1c965310-71dc-52e5-8fa4-7f7ecc54183a | note | What are the flow details from the safety eye wash outlet
379b0c07-ee4d-5638-b097-999428dab121 | button | Does the flow meet in the middle | Pass, Fail, N/A
42207971-7551-59fd-84ed-f2280ca5eb5a | note | what are the flow details from the safety product with all outlets flowing
4ec7d091-a0fd-5a1e-bb48-64b0a54d1fa0 | button | Litres per second | Pass, Fail, N/A
5ee90d15-92e7-5133-8fa5-1a5a907d046b | textbox | LPS
| checkpoint | Temperature Test
8df18c44-1e58-57fe-97cb-77bcfdc654e3 | note | Turn on shower, test temperature
2ade7017-c8b8-54bd-b836-9fc7c4edd081 | textbox | Temperature