## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP105 - Civil - Concrete Stairs | itp |  |  |  | Yes | ITP105 - Civil - Concrete Stairs | 127a8915-0f4e-4fe5-8960-7f3617b92efc
checkpoint-group |  |  | section | SECTION 1 – GENERAL DETAILS
checkpoint-no-status |  |  | checkpoint | GENERAL DETAILS
text | fba126c3-9d61-59a2-b2aa-bc0f1662fb61 |  | textbox | Project Name:
text | 716e76b5-f6dd-5abc-bd6c-c10eb553a20d |  | textbox | Project Number:
label | d5b93ae0-81bf-52e5-b177-30ead2d71178 |  | note | Client:
label | 4a8b4d80-04fc-523f-986d-f6e8a9c1064b |  | note | Contract Number:
label | bafd918f-3152-5be5-9a25-7b056836f02d |  | note | Lot Number / ID
text | e495d030-ceaa-5944-91aa-fb677810341a |  | textbox | ITP Number:
text | 6165f895-521a-5922-8dbc-a07960b5048a |  | textbox | Version:
label | fa7e5018-3145-5ec3-abca-133921a9779b |  | note | ITP Description: Concrete Stair Installation
text | b9c6941c-8b84-5ad3-9d58-21205068d976 |  | textbox | Prepared By:
date | 25693160-2816-52b9-8291-d0cd3117a200 |  | date | Revision Date
checkpoint-group |  |  | section | SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
checkpoint-no-status |  |  | checkpoint | ITP Close-Out by Vic Civil
text | 47e36a25-879a-5f8b-9e0e-0350e6e46a10 |  | textbox | Name:
date | 08e3e1c1-870d-50c1-b27d-56b0a7b45c53 |  | date | Date:
checkpoint-no-status |  |  | checkpoint | Client Close Out (If Req)
text | 00a8cbdd-24f4-55ff-bf3a-bd1d50843586 |  | textbox | Name:
date | c1d1269f-9e51-5022-a38e-458c2cb7ff1e |  | date | Date:
checkpoint-group |  |  | section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint-status |  |  | checkpoint | 3.1 - Survey / Set out
label | 987c620d-ffe3-587a-8339-af9119e55569 |  | note | Inspection Point: Quality Control Activity - Levels confirmed on site
label | 934376ec-04ff-5011-b20c-452587049c26 |  | note | Acceptance Criteria - Set out in accordance with design drawings or site conditions
label | c0074e3e-6fbc-5bb1-98e6-6e76df078a46 |  | note | Verifying Document - Visual Inspection / On Site Verification
label | cdcbe620-9818-5ca7-a289-addb20b8fdab |  | note | Key - I
label | 6f1e2e7c-0eb5-5030-9b31-70adb776985e |  | note | By - IP
checkpoint-group |  |  | section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint-status |  |  | checkpoint | 3.1 - Preparation of Subgrade/Rock Preparation
label | 1e9cddd2-1604-53aa-bc3b-b27859584b02 |  | note | Inspection Point: Quality Control Activity - Subgrade meets design requirements. FCR placed to specified thickness and compacted
label | 0f1f5715-2e27-5cf1-9874-7a0546c3f792 |  | note | Acceptance Criteria - No soft spots. Rock layer conforms to required thickness.
label | 1f09bb61-fc3c-5344-b417-c04801fa52c7 |  | note | Verifying Document - Visual Inspection. Geotech test if required.
label | 8060618f-21ce-5041-8913-7ec3d4cb3ccb |  | note | Key - W
label | 67c5fafd-a153-5e4f-a596-de0dde2cb158 |  | note | By - IP
checkpoint-status |  |  | checkpoint | 3.2 - Formwork
label | ce6ef79a-7963-5d02-bcf7-5e2253a9f24c |  | note | Inspection Point: Quality Control Activity - Installation of formwork to support stairs
label | 1411600c-bf9e-51ef-a178-47e377d2ca00 |  | note | Acceptance Criteria - As per temp design
label | 26703f24-1312-5dca-9f58-041d77c039c8 |  | note | Verifying Document - Visual Inspection
label | bfbcb866-40ad-5f78-9f88-ab8e0646aa28 |  | note | Key - H
label | 6cb48fc5-6752-5caf-9549-5b44e1dbf69c |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Steel Reinforcement
label | 004c0d6d-0af7-5e04-be01-9dc0442d7115 |  | note | Inspection Point: Quality Control Activity - Installation of steel mesh and or steel bar reinforcement as per drawings
label | a69620a1-01d1-5616-bb2b-a3bded3a8f89 |  | note | Acceptance Criteria - Reinforcement installed as required
label | 012f7c83-b84c-58ea-a7a6-83fa3f40f303 |  | note | Verifying Document - Visual Inspection
label | d4f0ce3d-bf96-5215-8f75-2982fef9e7ce |  | note | Key - H
label | 139b3a97-508b-5059-b8f1-9a856afe5304 |  | note | By - IP
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Concrete Pour
label | af3a8b79-4907-5bd3-abd4-6aeaefd31606 |  | note | Inspection Point: Quality Control Activity - Concrete is poured to required levels and strength
label | 2f9a6b00-4a3e-5d32-bd1a-3e4f0eaed8b8 |  | note | Acceptance Criteria - Strength and finish requirement met
label | 3d45c022-3426-5640-907d-b10a099dd796 |  | note | Verifying Document - Visual inspection only Strength Test
label | f80291c6-16af-50fd-99d9-51c660178cd0 |  | note | Key - I
label | bfda8009-be3e-577d-b5e7-98493cbe41a2 |  | note | By - IP
checkpoint-status |  |  | checkpoint | 3.5 - Stair edging or surface treatments
label | 4d157117-51cd-5a8c-bb0c-0e81e665bff6 |  | note | Inspection Point: Quality Control Activity - Stair treatments installed as required. (stair nosing’s, edge treatments, etc.)
label | bdf74d3f-5ea1-540e-bac4-5e97f1be7f12 |  | note | Acceptance Criteria - As per drawings
label | d83af1b2-0d15-5136-98a1-c44e563479ae |  | note | Verifying Document - Visual inspection
label | 4a1a8433-99da-5510-be97-739446033576 |  | note | Key - I
label | 75cec273-cbac-57f1-96bb-a6b8a24a3923 |  | note | By - IP
checkpoint-group |  |  | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint-status |  |  | checkpoint | 5.1 - Completions
label | 0a947470-b23c-56c8-aae2-fdaadef0b8ee |  | note | Inspection Point: Quality Control Activity - Inspection of works
label | 3463da35-6391-52bd-9948-f7672ec17022 |  | note | Acceptance Criteria - Works completed to the client requirements
label | 12578866-659a-5bd6-b58d-cd762f2be887 |  | note | Verifying Document - This document
label | 5cfc03b6-a120-5335-b65e-2cd27246e985 |  | note | Key - H
label | 36eba042-7e0b-5288-a697-b92ac9dc6973 |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | SECTION 6 – COMMENTS
checkpoint-no-status |  |  | checkpoint | Comments
checklist-sectioned |  |  | checklist | ITP007a-VC235-Structural Concrete Checklist | itp |  |  |  | Yes | ITP007a-VC235-Structural Concrete Checklist | 778602c4-8838-4f3d-94d6-056c77e78cb2
checkpoint-group |  |  | section | 4.0 CONSTRUCTION ACTIVITIES – PREPOUR
checkpoint-status |  |  | checkpoint | 4.1 - Incoming Inspection of Materials
label | d422a30e-0dfb-546e-b26a-76b869c22933 |  | note | Acceptance Criteria - All materials conform to IFC drawings and specs- ferrules, galvanised dowels, drainage conduits etc.
button | a4a11439-f37e-5559-85fc-d520dfa1df6a |  | button | Check Box | Yes,No,N/A
label | 9535782a-d44b-56d2-9838-780197e7423a |  | note | Verification Record - Delivery Dockets Compliance Certificates
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (1)
label | 6cc212e2-2060-5df9-abf7-a8397b09e5fe |  | note | Acceptance Criteria - Type, size, position, chairs, cover all as specified & within tolerance; laps and splices as specified; tack welds not undercut
button | 58791db6-4e5a-5609-8f88-0a66c23330db |  | button | Check Box | Yes,No
label | 644e0541-130a-59cf-96cd-8d3d17d42d0f |  | note | Verification Record - Reinforcement Schedule
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (2)
label | bc31cfeb-4ff1-58f2-879f-8c074435d029 |  | note | Acceptance Criteria - Ensure starter bars match precast stitch bars (if applicable)
button | 748f9438-dd8d-51d2-9d5e-fd7e9f6a1a7f |  | button | Check Box | Yes,No,N/A
label | 03bc39b5-90bd-5f76-91b8-dca826c8415c |  | note | Verification Record - Survey Report
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (3)
label | 84a46819-5a6f-5c9b-bf2e-7cff0c777619 |  | note | Acceptance Criteria - Placement, size and configuration as per drawings ± 5mm position.
button | 2b970c65-5ef2-576f-b750-158e0cec310c |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (4)
label | 2dd494ff-fc84-53fa-a987-03a52eedbba4 |  | note | Acceptance Criteria - Cover (including tire wire) specified in drawings 0mm, + 5mm. Cover checked to FSL.
button | e6115541-3ab7-549a-ab99-79e8b3caec06 |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (5)
label | 1fe7def0-a1fa-5e8e-87af-8e96391278e8 |  | note | Acceptance Criteria - Surface condition free from thick rust, grease, mud etc
button | 99f4e218-755c-59e6-9f03-7b190d9d2ed9 |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (6)
label | b7a6f027-cf10-5943-941e-038a5d348639 |  | note | Acceptance Criteria - Min lap lengths:
label | 2f8c9e27-a4ff-5817-9740-a2a8eae050fa |  | note | N12 – 300mm N24 – 1000mm N16 – 500mm
label | fc52e794-fe4f-52cc-8eaa-e855b33edd1b |  | note | N28 – 1250mm N20 – 750mm N32 – 1500mm
button | 8756d522-d1e6-5b17-9a6e-8ff99d51356c |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (7)
label | eae6105d-5fdd-59b1-b0b8-2231b56862ee |  | note | Acceptance Criteria - Tack Welding not within 50mm of bends
button | 93b3c713-5954-518d-b143-5fe9b43f6d06 |  | button | Check Box | Yes,No,N/A
checkpoint-status |  |  | checkpoint | 4.6 - Reinforcement (8)
label | 0ce6fee2-6c57-5a17-92f9-4005f39ac2eb |  | note | Acceptance Criteria - Mechanical splices (couplers or similar) fully engaged and installed as per manufacturers recommendations.
button | 603de40f-404e-5724-9da4-ae8a4038bd2c |  | button | Check Box | Yes,No,N/A
label | 09ac3e18-864c-5634-9890-dacff840140a |  | note | Verification Record - Coupler Delivery Docket, Compliance Certificates
checkpoint-status |  |  | checkpoint | 4.7 - Formwork/ falsework setup, alignment and integrity (1)
label | 0fb72bb1-eb94-5778-bc04-b32b5b698345 |  | note | Acceptance Criteria - Installed as per temp design; design confirmed by survey; forms clean & release agent/oil applied.
button | dc8468a1-3e64-506e-a1ca-64a6d7757629 |  | button | Check Box | Yes,No,N/A
checkpoint-status |  |  | checkpoint | 4.7 - Formwork/ falsework setup, alignment and integrity (2)
label | f7dc6bc3-7955-539b-bb13-1ca0550b0bfb |  | note | Acceptance Criteria - Falsework/formwork over 1m high has a temporary design
button | 09a2e6bc-bdd3-541d-b902-b7840ae0e3de |  | button | Check Box | Yes,No,N/A
label | b7fe5e67-0386-53aa-a3f5-e98a5313cdb3 |  | note | Verification Record - Temp Works Design
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 4.8 - Construction Joints
label | 293f264f-e141-5b2c-a6bd-db6882680982 |  | note | Acceptance Criteria - Concrete cast against concrete to be clean & free of laitance. Roughened and coarse aggregate exposed to depth of 3mm
button | 0ec26197-c1c6-5eea-a81a-c1aa24be9bf4 |  | button | Check Box | Yes,No,N/A
checkpoint-status |  |  | checkpoint | 4.11 - Cast-in items, void formers, block-outs and hold down bolts
label | b04cd4cb-8d4b-5cac-b421-9148d0e081f2 |  | note | Acceptance Criteria - Type, quantity and location as per design. Checked with survey and relevant stakeholder
button | 9f3e942b-4765-517e-9575-3a5d4dd8e302 |  | button | Check Box | Yes,No,N/A
label | 202b373e-0430-5b2c-83e1-056cc3333826 |  | note | Verification Record - Delivery Dockets
checkpoint-status |  |  | checkpoint | 4.12 - Installation of thermocouples
label | 6f92a0b7-208a-57fc-9f5a-b945e165460e |  | note | Acceptance Criteria - Thermocouples installed as per VR610.22
button | 83fbd972-9681-5c8c-988d-6bdc00c18fe0 |  | button | Check Box | Yes,No,N/A
label | 53ef0494-38f0-52f8-8ad6-246905408469 |  | note | Verification Record - Install Photos
checkpoint-no-status |  |  | checkpoint | HOLD POINT
label | 52d09c8e-7c97-5697-b463-59ba9979b03d |  | note | Concrete pre-pour checks completed in accordance with the applicable ITP, drawings, specifications and approved changes
text | 90450d8a-09f3-51d9-bf55-53ccffa77ed2 |  | textbox | PROJECT ENGINEER NAME (Vic Civil)
text | 3abaf3b3-a89e-5ac8-af47-17e5adcda9a3 |  | textbox | PROJECT ENGINEER NAME (Multiplex)
date | 02603f91-ac33-508d-b1f9-884433bc879a |  | date | Date:
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | 4.0 CONSTRUCTION ACTIVITIES – CONCRETE PLACEMENT
checkpoint-status |  |  | checkpoint | 4.13 - Concrete Supply & Concrete Testing – Slump Test (1)
label | 02b48ff9-9d56-5b49-83cd-252928f5473c |  | note | Acceptance Criteria - Concrete Mix on Docket Checked. Ensure delivery dockets. Tester onsite. Visual assessment of quality.
button | 320a13c0-26fb-546e-8531-d7a20d3ec90c |  | button | Check Box | Yes,No
label | 87b2f4d0-e26b-504d-b911-571a8549e29f |  | note | Verification Record - Concrete Delivery Dockets, Field Test Docket, Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.13 - Concrete Supply & Concrete Testing – Slump Test (2)
label | 0e074cca-1ce6-5b3c-a76b-86424781c47a |  | note | Acceptance Criteria - 1 slump test per strength test
label | 726c41b6-ecbd-50d4-aec5-499f990a6011 |  | note | ○ If mix contains superplasticiser, all batches shall be tested. If 5 consecutives batches comply, superintendent may reduce frequency to 1 per strength testing
label | 1f301f1a-1aaf-5e4c-9a24-7208acd5aea7 |  | note | ○ Test within 45 mins of adding cement to aggregates, or immediately prior to discharge when actual haul time is >45mins, or after addition of water. All other slumps to be estimated visually.
label | 18f62fd5-9edb-5415-9372-e997dc55e205 |  | note | VR Tolerances:
label | 668a59e4-f80d-554d-8088-f5451d354b65 |  | note | – – – – – – – – – – – – – – – – – – –
label | 1c6e0b51-73e9-5292-ab1a-47e5c09f1a13 |  | note | Specified slump, mm ¦¦ Tolerance, mm
label | 9aa70933-3e85-5360-b108-47d2c3437dda |  | note | – – – – – – – – – – – – – – – – – – –
label | 68e5448f-8cfd-5a3f-9255-4a68d0cf5386 |  | note | <60 ¦¦ ± 10mm
label | 5dc12ebf-2ed4-5c5c-8c8a-7827ff3a9a34 |  | note | ≥60mm to ≤80mm ¦¦ ± 15mm
label | 7b41bb6d-2fe8-5586-ad64-3a6d851cc5f8 |  | note | >80mm to ≤110mm ¦¦ ± 20mm
label | 9fc2df6b-14be-5647-92fc-82871aef0562 |  | note | >110mm to ≤150mm ¦¦ ± 30mm
label | 690d4c1a-7d14-5681-a956-a05c90b16c41 |  | note | >150mm ¦¦ ± 40m
label | 1a1472df-8e81-55fa-903d-eb4d5f04f768 |  | note | – – – – – – – – – – – – – – – – – – –
button | da86da32-cded-56b8-aeef-462a5c926899 |  | button | Check Box | Yes,No
label | a0bdc778-fb32-5fc4-ace0-9323548e0afb |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.14/4.15 - Discharge & Placement of Concrete (1)
label | 19d3c406-cc38-5465-8ade-caad5bc49ac0 |  | note | Acceptance Criteria - Each load placed within 60mins of batching, unless approved otherwise
button | 9184b312-5c6a-5430-be40-e93d510c2b0d |  | button | Check Box | Yes,No
label | 77298f5f-b734-57b2-8cf3-94e9e95c9938 |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.14/4.15 - Discharge & Placement of Concrete (2)
label | 1fd67231-726a-5d5e-b775-97db3903f598 |  | note | Acceptance Criteria - No water added once discharge commenced
button | b2de6355-01e1-5cda-bcec-603a4b970f40 |  | button | Check Box | Yes,No
label | 5def3580-7bdb-5383-8c42-8e6a308b6c05 |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.14/4.15 - Discharge & Placement of Concrete (3)
label | bdb62702-1800-5d15-8f7e-87200ec5057d |  | note | Acceptance Criteria - Max and min temps:
label | 3a55c61f-b97d-5389-8df6-b78c163a0d02 |  | note | – – – – – – – – – – – – – – – – – – –
label | 837806e1-06f4-5628-885b-f0dc69c9f248 |  | note | MIN (ºC) ¦¦ MAX (ºC)
label | 8a5ab9a0-7ca9-5d7f-a697-232d0b480d49 |  | note | – – – – – – – – – – – – – – – – – – –
label | cb5e24db-efd5-5b93-a8c1-e4a8dfdf3fb1 |  | note | AMBIENT: 5 ¦¦ 35
label | bee00bbb-09ed-5549-8574-02953a3d9d67 |  | note | CONCRETE: 10 ¦¦ 32
label | 65f08fea-039a-5555-9627-cd17feaf8761 |  | note | – – – – – – – – – – – – – – – – – – –
button | ffda436c-a4e8-5453-933e-89518fd23e91 |  | button | Check Box | Yes,No
label | ccc50014-8416-5000-8733-fa1372f908dc |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.14/4.15 - Discharge & Placement of Concrete (4)
label | aefabb2f-68fe-5369-8677-8938d97c1ee5 |  | note | Acceptance Criteria - Max. lag between trucks is <=25 mins. If > 25min aliphatic alcohol to be used. Interval between final discharge and start of discharge of next truck is <45 mins for a continuous pour.
button | 99327024-c786-5d62-9469-f82a8c311b3c |  | button | Check Box | Yes,No
label | 66c4840a-a3f3-5b0e-a26d-37e86eee6ef3 |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.14/4.15 - Discharge & Placement of Concrete (5)
label | 25890a6f-7335-55da-8860-494be1bfc827 |  | note | Acceptance Criteria - Vertical drop not exceeding 2.0m Placed in not more than 350mm layers.
button | 56e4307e-ffa8-5783-9ab9-2e4d406c11bf |  | button | Check Box | Yes,No
label | 4db55c9e-9e8a-5368-a40e-3cc2fcc4ff37 |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.16 - Concrete Testing – Compressive Strength
label | 7dc5bdb6-d480-5b25-a307-40d3391e7b05 |  | note | Acceptance Criteria - Compressive Strength Testing => 28 days post-pour
label | 2e017914-3c65-51a3-9de2-db27e95bb068 |  | note | ○ Refer VR 610
label | 463bbc10-d54c-5e3d-b5bc-5cc4cb7579fc |  | note | ○ 3 cylinders (1 x 7day, 2 x 28 Day) taken for each sample, minimum no. of samples:
label | 1023659e-d1a6-5c55-8580-5c9037b25b0a |  | note | – – – – – – – – – – – – – – – – – – –
label | 83eb77b3-d38d-5203-9aea-9ee3e5ad75f2 |  | note | Quantity, m3 ¦¦ # Samples
label | 3fb8236b-5f21-5c0b-9dba-eb8d0da951c7 |  | note | – – – – – – – – – – – – – – – – – – –
label | 6254dadb-b082-5c32-926e-22100e5a3e82 |  | note | 0-10 ¦¦ 1
label | 22287e8e-1f75-544d-94e8-20f143d0d444 |  | note | 10 to 25 ¦¦ 2
label | 005d7620-0fba-5e0e-bfab-18b3c099dda7 |  | note | 25 to 50 ¦¦ 3
label | 1c672396-6b6c-5402-903a-f36e5c01eb2d |  | note | 50 to 100 ¦¦ 4
label | 71f744e7-11c9-5ddb-b4e3-6a79d482afe1 |  | note | >100 ¦¦ 1 sample for each 50m3 >100
label | 5eb4d393-c2de-5edb-bb21-99c1c48abcc2 |  | note | – – – – – – – – – – – – – – – – – – –
button | b5c1fa4b-bd55-5c7d-aab0-7dbf87f3c0e3 |  | button | Check Box | Yes,No,N/A
label | 71cbaea4-1ced-50d3-bd95-96981aa8f61f |  | note | Verification Record - Concrete Pour Record (Refer pg 7)
checkpoint-status |  |  | checkpoint | 4.19 - Visual check on formwork
label | 88f14df2-75d3-50da-b357-de826375813b |  | note | Acceptance Criteria - Any significant deformation observed?
button | 40a1a082-fe4a-5017-990f-12ddb882b70a |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.20 - Surface Finish
label | 2c8bd451-fd32-55cf-8ea0-b1480f15252d |  | note | Acceptance Criteria - Surfaces finished to the class specified in the drawings.
button | 63893369-5734-5e11-8d8e-8fef8d280f80 |  | button | Check Box | Yes,No
checkpoint-status |  |  | checkpoint | 4.22 - Curing of exposed surfaces
label | 833ad6aa-5424-5066-89f0-007d301ff91e |  | note | Acceptance Criteria - Curing in accordance with BCRC report recommendations
button | 4cac8d17-a83b-5a83-ba45-aa083a058ecf |  | button | Check Box | Yes,No,N/A
label | 9de37994-eb3a-5f29-8022-5a56c70df25b |  | note | Verification Record - Curing Methodology or Compound: BCRC Report (attached)
checkpoint-status |  |  | checkpoint | 4.23 - Removal of falsework and stripping of formwork
label | 2c806fe5-4d56-5b64-b21e-dcc8278a1e72 |  | note | Acceptance Criteria - Falsework and formwork removed as per VR Table 610.251 (See Pg 5)
label | 327c3449-2d8e-5f61-81ad-8ba389c32138 |  | note | ○ If early removal or loading is required, relevant approvals and test results to be reviewed by design engineer
text | 168380ae-63f4-58d2-92b9-c2de96c8619d |  | textbox | Days since pour
button | ba68e0aa-be98-52f6-a71b-04e5e247ca1f |  | button | Check Box | Yes,No,N/A
text | 595498e2-1ad7-5b24-bf0e-0cb407f42132 |  | textbox | Verification Record - RFI Reference #: Maturity Report
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 4.23 - Inspection of stripped surface
label | 5a705904-d286-51a4-ba0b-dae37c6a6745 |  | note | Acceptance Criteria - Stripped surface finish has been achieve in accordance with specifications (VR610.31) and design drawings?
button | cf5c9d18-bb4b-5fe5-9f47-8186481fed7e |  | button | Check Box | Yes,No
text | 273e4948-ce7b-5fd2-91f0-2232dbb63276 |  | textbox | Verification Record - Surface Finish Class:
checkpoint-status |  |  | checkpoint | 4.25 - Patch Repair (where applicable)
label | 8944482f-d9a2-5aef-af83-b02a0962ba0a |  | note | Acceptance Criteria - Inactive crack and/or Patch repairs conducted as per approved procedure, where required
button | 224b67d3-d414-5a5e-89ed-fed3d409322e |  | button | Check Box | Yes,No,N/A
text | b7557751-ddcb-5ebb-bef7-3adbdb25b9d4 |  | textbox | Verification Record - Repair method approval- RFI-Repair Product TDS
checkpoint-status |  |  | checkpoint | 4.26 - Crack Repair & Monitoring (where applicable)
label | 6f5e6244-f81c-580b-9f29-87bf55efc2a0 |  | note | Acceptance Criteria - Cracks greater than acceptable widths as per VR Table 610.241 are mapped and repaired in accordance with VR 687 and approved methodology specific to location. Cracks requiring repairs monitored.
label | 3ca89efb-2c59-5c82-8479-209f1e0b1e63 |  | note | – – – – – – – – – – – – – – – – – – –
label | 9040fc34-cb27-581a-a0d4-b60d4f281e9d |  | note | Exposure Classification ¦¦ Maximum Acceptable Crack Widths (mm)
label | 5d360de5-65e0-5b49-be73-041c517b579e |  | note | – – – – – – – – – – – – – – – – – – –
label | dec78b6a-9780-5690-a105-7c7644c95939 |  | note | A ¦¦ 0.20
label | f9e5ba57-096b-5e13-ac0b-02443d94b31a |  | note | B1 ¦¦ 0.20
label | 4d81c0fe-384d-545c-994b-4284f5424470 |  | note | B2 ¦¦ 0.15
label | d180792a-7a10-5de4-be14-d6408086fe1d |  | note | C, U ¦¦ 0.10
label | 9618f963-1e3a-5024-bb2b-33a70338ed1e |  | note | – – – – – – – – – – – – – – – – – – –
button | 1d04ad14-9b78-50a3-a70b-a24911b80f8c |  | button | Check Box | Yes,No,N/A
text | 7cbd730d-ba96-52cb-9121-386c334b04cc |  | textbox | Verification Record - Repair method approval- RFI-Repair Product TDS
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-group |  |  | section | 5.0 TESTING AND COMMISSIONING REQUIREMENTS – POST POUR CHECK & TESTING
checkpoint-status |  |  | checkpoint | 5.1 - As Built survey complete
label | 273628f7-c645-54f3-8934-17fade6da9d5 |  | note | Acceptance Criteria - As-built survey is within tolerance when compared to Design & Specifications
button | 3c30e0d7-d76a-540b-b4c9-b4be0b4e7b0b |  | button | Check Box | Yes,No
label | cbd29be7-99a4-567b-a95d-a0f364eb29d6 |  | note | Verification Record - As-Built Record – conformance report
label | 6e30196f-4c69-5f4a-adf2-0b51142e02dc |  | note | Vic Civil - Site Engineer (R):
label | 30406111-6610-5e14-833f-fd13b0fc6524 |  | note | Multiplex - Site Engineer (R):
date | 992d21be-fe95-5eeb-ae68-6fb33306393f |  | date | Date:
checkpoint-status |  |  | checkpoint | 5.2 - Maturity Testing
label | 0fc8a9ac-60c6-51e9-add8-5e256736c522 |  | note | Acceptance Criteria - Concrete has achieved minimum strength prior to the removal of falsework/ formwork
button | 7f7e53a2-ef7e-5f5a-bdda-84dbf1c7c14a |  | button | Check Box | Yes,No,N/A
text | a8f003f5-5248-5554-99e1-720c8eab32c4 |  | textbox | Verification Record - Strength Achieved: Maturity Report
label | 3e9983d5-90e6-5107-bb51-62c4712bce64 |  | note | Vic Civil - Site Engineer (R):
label | f66c5cee-4355-5251-b626-935fd37a5d2c |  | note | Multiplex - Site Engineer (R):
date | 5913627b-0110-5bb9-abf2-df3345235357 |  | date | Date:
checkpoint-status |  |  | checkpoint | 5.3 - Concrete Cover
label | 05667fe7-784d-5e4b-9a14-826c9d225efe |  | note | Acceptance Criteria - For every 25m2 of exterior surface area a 3m2 ‘Test Area’ will be selected. Within this ‘Test Area’ 10 concrete cover checks will be conducted.
button | f60b359b-d188-5d9d-9a7c-6893c06cdc41 |  | button | Check Box | Yes,No
label | 4f06d249-2b6e-5524-8f36-2c4b12b78247 |  | note | Verification Record - Cover Checks Record (Refer pg 6)
label | 4fd78781-6e4d-572c-8c85-e719c4858b7c |  | note | Vic Civil - Site Engineer (R):
label | 9bda8ac9-6e33-585c-a177-d25ddeb54221 |  | note | Multiplex - Site Engineer (R):
date | c83b3424-81a0-591e-955f-69433a074326 |  | date | Date:
checkpoint-status |  |  | checkpoint | 5.4 - Temperature Monitoring (VR610.22)
label | 349dbd42-ab78-5f49-b8b6-75e26d366bb6 |  | note | Acceptance Criteria - Ensure temperature differential across the concrete member being constructed is < 20°C during the period of curing, and internal concrete temperature doesn’t exceed 75°C
button | 5a7787e7-25c2-56ad-beaa-7d93b4a75e55 |  | button | Check Box | Yes,No,N/A
label | 380ddc99-4d21-5626-8f33-3709e7393d74 |  | note | Verification Record - Temperature Monitoring Report
label | 73a6a875-d39f-56f2-8d25-d9a6cbaf4414 |  | note | Vic Civil - Site Engineer (R):
label | d8b58234-f138-51fd-bc47-b665b5ada39d |  | note | Multiplex - Site Engineer (R):
date | 30754ac1-7987-537f-a9c2-f261e967f505 |  | date | Date:
checkpoint-status |  |  | checkpoint | 5.5 - Compressive strength and slump results
label | c1ccb98b-5f74-523c-b006-6d4ea1a31090 |  | note | Acceptance Criteria - 7 and 28 day strength results achieve min requirements as per VR table 610.051. Slump tests with tolerances.
button | c6ad3e3a-9297-5e96-9799-15cf6ff530b2 |  | button | Check Box | Yes,No
label | 5bae42b4-9d6d-50d0-a684-dbd7a1916c27 |  | note | Verification Record - NATA Test Results
label | 83f51f07-9b30-56da-a56b-22b8dd638aab |  | note | Vic Civil - Site Engineer (R):
label | fbc91df4-675c-5183-8420-faa67a834650 |  | note | Multiplex - Site Engineer (R):
date | ef1d9d84-f8e2-50f9-b1a3-fd0a289eb116 |  | date | Date:
checkpoint-group |  |  | section | 6.0 SUB-LOT – COMPLETION REQUIREMENTS
checkpoint-status |  |  | checkpoint | 6.1 - Works Completion Inspection
label | a9daf44b-ea06-5744-9ebb-b2a5827fed15 |  | note | Acceptance Criteria - Ensure works completed in accordance with IFC Dwg & Specifications, Inspection completed & recorded prior to releasing activity
button | 64d7072a-68c9-5311-ac20-2fc06d22c41b |  | button | Check Box | Yes,No,N/A
label | 8ac96e71-a43a-598b-aa9d-1344b35343a7 |  | note | Verification Record - Punch List Items
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 6.2 - Close out NCR(s)
label | 9ddf8509-be09-570e-afd3-19562439bed1 |  | note | Acceptance Criteria - NCR(s) raised & closed formally, All out of tolerances notified via Site NCR reporting system
button | e6361521-32e7-5aa6-b64d-a3a42666b540 |  | button | Check Box | Yes,No,N/A
label | b2f928e9-dfd4-5694-b8e6-36f4fbd1b8dd |  | note | Verification Record - NCR/s related to lot:
holdpoint |  |  | signoff | Project Engineer (HP) / Quality Representative (HP)
checkpoint-status |  |  | checkpoint | 6.3 - RFI(s)
label | d374e4a5-b5ca-5fe9-9b0e-e5ad5866917d |  | note | Acceptance Criteria - All RFIs have been closed-out prior to work lot submission
button | 0de31e4b-7e8d-5cf6-8ffd-5a557df721dd |  | button | Check Box | Yes,No,N/A
label | e5ce040e-8b1f-5796-8966-9a58f052aeb7 |  | note | Verification Record - RFI & DCN Register relevant to sub-lot only
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-status |  |  | checkpoint | 6.4 - Red Line Mark Ups
label | 41b8f855-1dfb-5185-afb8-97ceb680c140 |  | note | Acceptance Criteria - Confirm redline drawings are being progressively marked up
button | 60f181c9-addf-5443-b11a-c4edea61f9c3 |  | button | Check Box | Yes,No,N/A
label | f187129d-e37b-5942-98c8-3e7199550a82 |  | note | Verification Record - Redline Drawings / Summary of Material Quantities
holdpoint |  |  | signoff | Project Engineer (HP)
checkpoint-no-status |  |  | checkpoint | Check List Close Out
label | 2aa78306-b51e-52c0-a079-64913852bbb9 |  | note | Concrete pre-pour checks completed in accordance with the applicable ITP, drawings, specifications and approved changes
text | c25f0b11-5ad7-5554-8dec-7e9c9800a9dc |  | textbox | PROJECT ENGINEER NAME (Vic Civil)
text | 3ffb369e-d51a-5704-b70a-8bb56dfbd284 |  | textbox | PROJECT ENGINEER NAME (Multiplex)
date | d0e8e1c0-760e-5f7b-9057-f5a576b76076 |  | date | Date:
holdpoint |  |  | signoff | SIGN
checklist-sectioned |  |  | checklist | ITP007a-VC235-Architectural Concrete Columns | itp |  |  |  | Yes | ITP007a-VC235-Architectural Concrete Columns Rev2 | 89a5bd9b-8099-4c70-b431-1c9460bc5953
checkpoint-group |  |  | section | 1.0 PRELIMINARIES - Prior To Commencement of Work
checkpoint-status |  |  | checkpoint | 1.1 - Work Lot Map
label | d01de0f7-08bd-5c9d-8c52-4d7acbdcbb57 |  | note | Specification Reference - N/A
label | 891c588b-8245-57fb-978f-0c957e5f2436 |  | note | Acceptance Criteria - Work Lot Map attached to Work Lot
label | 57ae36c9-fd8c-5333-83d9-86f6cc215f88 |  | note | Test / Inspection Method & Frequency - Per work lot
label | 048f315a-f78f-58fa-99d6-e644fe9b251e |  | note | Key - PE (H)
label | bed46666-8067-5d41-8bf2-eed8a78d3007 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | cdf3b8e5-9d6b-5ba1-8c5f-75a17a5c2032 |  | tickbox | Records & Comments - Work Lot Map
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 MATERIAL COMPLIANCE - Prior To Commencement of Work
checkpoint-status |  |  | checkpoint | 2.1 - Calibration Certificates
label | 50ad8373-bf2b-5abd-a3f4-e8e3e3307fe8 |  | note | Specification Reference - Process Control
label | f2372a1a-426a-5542-904c-06780c2a9a82 |  | note | Acceptance Criteria - Confirm that external equipment calibration and testing facilities are registered, External equipment calibration meets contract requirements for each item of test equipment
label | 0fb131be-2154-55dd-8b9c-b156898abacf |  | note | Test / Inspection Method & Frequency - Visual check with certificates, ITP, checklist or inspection report
label | 976fd0ba-3ccf-5940-8f26-cb877472e4e1 |  | note | Key - PE (H)
label | 1eb72beb-5ed5-56a9-80dc-5144f5a8efbb |  | note | Multiplex / Vic Roads Key - PE (H)
label | c5688953-e17b-5afc-80e0-5b1ea1da54a5 |  | note | Records & Comments -
boolean | b8ac7a7e-5da7-5275-9184-19043a5fe777 |  | tickbox | Record of visual inspection
boolean | 28cfeb72-7e41-5120-82e6-106764151156 |  | tickbox | Calibration Certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Concrete Mix Design
label | 457bea29-7b5b-50fd-b678-3633b453a006 |  | note | Specification Reference - VicRoads 610.07 AS 3600 IFC Drawings
label | 7c6232cf-2211-5525-b6ea-344c17659b5c |  | note | Acceptance Criteria - Concrete mix design approved and in accordance with the IFC drawings
label | 5afe713a-af15-5f32-9291-5ba4072e40ea |  | note | Test / Inspection Method & Frequency - Approved mix confirmation prior to commencing works
label | f326f643-1cd5-5b3a-aa55-20693dbbb629 |  | note | Key - PE (H)
label | 3b475f7a-51ac-5260-9610-fd415b0ee707 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | f09711b1-3349-545c-9173-b8563b7bfa0b |  | tickbox | Records & Comments - Approved VicRoads mix design registration
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Steel Reinforcement Certification
label | e00999e5-3acd-55cf-ade4-825993753480 |  | note | Specification Reference - VicRoads 611.05 AS 4671 IFC Drawings
label | 0275dd0f-8a07-5aca-83f1-29249126cec7 |  | note | Acceptance Criteria - ACRS certificate provided for suppliers and manufacturers of steel
label | ff9c8931-81c8-50fe-8f70-e19b98960b17 |  | note | Test / Inspection Method & Frequency - ACRS certificate supplied within 14 days of contract award
label | 71cc4023-211b-55d8-aab1-d6768aa461f2 |  | note | Key - PE (H)
label | b9fdb415-a30c-585f-963a-c55c56417fff |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 6c488f81-522e-5fce-9d2e-547e28ccc393 |  | tickbox | Records & Comments - ACRS Certificate
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Bar chairs and spacer compliance
label | aae12866-fc06-5b18-882c-39bd980189a6 |  | note | Specification Reference - VicRoads 610.26(a) AS/NZS 2425 IFC Drawings
label | 27e3a614-ffb0-5006-ac89-2ce820341356 |  | note | Acceptance Criteria - Reinforcement supports comply with AS/NZS 2425. Concrete bar chairs are tested in accordance with VicRoads 610.26(a)
label | 985befa3-48ac-5126-a159-eda8e955ccfa |  | note | Test / Inspection Method & Frequency - Review of certificates prior to ordering materials
label | 13b02024-ee19-5e79-812b-ebe7f79c5b25 |  | note | Key - PE (H)
label | e891a67c-adcc-53b3-b18e-9db746712d68 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 37cf3284-e150-5d67-952b-b1896c9c6113 |  | tickbox | Records & Comments - Compliance certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Formwork / Falsework Design
label | ec76775d-4e9b-529b-95ef-61ec5f973247 |  | note | Specification Reference - VicRoads 614.04, VicRoads 613.04 JHG Temp Works Design Procedure
label | eaab3d60-b5cf-5748-ab5f-c1dd1aaf2208 |  | note | Acceptance Criteria - Approved Formwork Design, Approved Falsework Design, Design brief approved and verified
label | 0dca90f7-937f-5bd4-b6b8-2884df623f52 |  | note | Test / Inspection Method & Frequency - Proof Eng’g Certificate or Design Verification forwarded to Client
label | b640af3e-364d-5436-8a9a-b98758207d61 |  | note | Key - PE (H)
label | 36834c3b-3e4b-54e9-871b-68b8cb80fa06 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 683e740f-5fae-549e-9a24-9a19d2f31e45 |  | tickbox | Records & Comments - Temporary Works Design
text | f1ed38c7-e999-5879-9a82-28a17d6a181d |  | textbox | Ref No.
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.7 - Confirm approval of curing compound
label | c06a4fbe-2c28-564f-b2a4-18047ba77d3c |  | note | Specification Reference - VicRoads 610.23
label | 79bfed9f-13c3-5706-9866-10e78289179d |  | note | Acceptance Criteria - Curing compound approved and in accordance with VR IFC Design via RFI.
label | 80aaa37f-1b7b-57fb-8b0e-887cc94427e0 |  | note | Test / Inspection Method & Frequency - All batches
label | 78372b7f-0cd0-585b-abb5-083abf961183 |  | note | Key - PE (H)
label | 5a28a5f0-7a5f-590a-891f-ab9389c18855 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 5bd2f8da-c2c9-531b-a1ee-c8616bc669d6 |  | tickbox | Records & Comments - Curing compound Design Approval
text | b21c3f0d-68c9-5df5-9291-5f446a1f2bda |  | textbox | Ref:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 QUALIFICATION REQUIREMENTS - Prior To Commencement of Work
checkpoint-status |  |  | checkpoint | 3.1 - Welding Requirements
label | e177af43-d60b-518f-90cf-919589e84afe |  | note | Specification Reference - Approved Weld Procedures
boolean | 133cf4ea-989f-518f-a697-6e8ccf890d07 |  | tickbox | AS 1554.1 Clause 4.1 to 4.11
boolean | 2d1a8e77-c48d-5933-9828-4847f9fc237a |  | tickbox | AS 1554.3 Clause 4.1 to 4.11
label | b42fb44f-75e1-5e65-8d9f-14ab34aa10c7 |  | note | ○ IFC Drawings Welder Qualifications.
boolean | 62d77b6d-1bd1-5e8a-8f08-333b03d0247e |  | tickbox | AS 1554.1 Clause 4.12
boolean | 855f4f21-6312-5e99-b8e6-c11d684393aa |  | tickbox | AS 1554.3 Clause 4.12
label | 9377d45b-8da3-5105-bdaa-a9262f627070 |  | note | ○ TGN-BC-01: Tack welding of reinforcement bar
label | 931d0fe6-da06-5e81-ac2b-82655bd07c2c |  | note | Acceptance Criteria - Weld Procedures have been reviewed and approved by Construction Team & Quality Team for all welding required- this includes Non Load Bearing tack welds, Evidence that all welders are qualified with regards to the applicable welds, Weld Supervisor has required qualifications
label | b7bf11cc-dbe6-5ae5-929a-7cad360791aa |  | note | Test / Inspection Method & Frequency - Provided by subcontractor
label | 7b38efbf-1369-554d-9329-d9ff71f4b89d |  | note | Key - PE (H)
label | 69831c77-d4e5-57db-b79b-9c57cc17efd3 |  | note | Multiplex / Vic Roads Key - PE (H)
label | d168ee76-2af5-5b31-a950-ff376648c278 |  | note | Records & Comments -
boolean | 3ff92281-1e48-5576-b9b7-017ee42c6aed |  | tickbox | Weld Procedures
boolean | ea625f47-9409-57a2-a9e4-06c2c498db34 |  | tickbox | Weld Procedure Qualification Records
boolean | 80d834cb-2c82-5a1e-aec7-a6869f2c1ce1 |  | tickbox | Welder Qualifications
boolean | 7d7984e1-3244-59e9-a445-40f345e225eb |  | tickbox | Supervisor Qualifications
label | ac7680c2-85b6-50a6-8002-a35741cf17e8 |  | note | Welding Procedures required for the works to be listed here
label | dc593065-08f4-5eb1-8860-2800f5927388 |  | note | Eg. Fillet welds/ splices, tack etc:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Concrete Technical Specialist
label | 046dfe37-6b4b-59f3-8c3c-a207053f247a |  | note | Specification Reference - VicRoads 610.24
label | 977360e4-3aca-50db-9630-c1c01771d2f2 |  | note | Acceptance Criteria - The assessment of the cracked concrete structure shall be undertaken by a technical specialist with a minimum of 5 years’ experience
label | 2bb0c63c-e451-5650-a716-47637d7eef9b |  | note | Test / Inspection Method & Frequency - Prior to repair
label | 1101a487-a3cf-59ed-b847-eed6dcf6360a |  | note | Key - PE (H)
label | 3f7c696a-51b7-50de-bed3-9df4be2e8531 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | c45ebb45-9567-5d8f-8859-531e17dd2414 |  | tickbox | Records & Comments - Evidence of experience
checkpoint-group |  |  | section | 4.0 CONSTRUCTION ACTIVITIES - Prior To Commencement and During Works – Sub-lot Records (if applicable)
checkpoint-status |  |  | checkpoint | 4.1 - Inspection of incoming materials: All embedded Items cast into structural concrete
label | a5ab42c5-8a84-5e4a-a172-ef732ff2a054 |  | note | Specification Reference - Project Requirement Specification
label | ad8b82eb-b6e9-52a1-a5a1-5745a06a7550 |  | note | Acceptance Criteria - Materials conform to IFC drawings and Specifications, Free of defects, transportation damage and/or imperfections
label | c1e1c9de-00dd-5f2f-bd3b-bc781eacace6 |  | note | Test / Inspection Method & Frequency - Visual check with written notes in Delivery docket, ITP, checklist or inspection report. Upon Delivery
label | b19437b6-0294-5552-9fa5-5cd2d48b41dd |  | note | Key - SE (W)
label | aedfeecf-466d-551d-8338-8411a360c550 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 0a372a35-d71d-563c-b547-3814ce27ff97 |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Survey Set-out & Initial pour against ground
label | 50e6dda5-996d-5380-8a60-716447287637 |  | note | Specification Reference - IFC Drawings
label | dd3ced1e-7eef-58ca-9d5a-e45d30f68686 |  | note | Acceptance Criteria - Survey marks (levels and offsets) in place (where applicable)
label | d8c978d9-e41d-5b0f-8c5c-31e7dfd8e052 |  | note | Test / Inspection Method & Frequency - Visual Inspection / Spot Check – Prior to commencing works
label | 9c92c82a-c1f8-5932-b070-101e2071a83f |  | note | Key - SE (W)
label | b13e79cf-39f6-581f-bb6d-556ead08e546 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | c91904a0-adb8-5fc8-81e1-7643918c83cc |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.3 - Pre-pour inspection: Reinforcement
label | 2afa1cf7-1c95-5535-afef-cdf43a629de7 |  | note | Specification Reference - IFC Drawings VicRoads 611 AS 5100 AS 1554
label | deb1eb76-629b-5012-a4d2-f067659510c2 |  | note | Acceptance Criteria - Concrete shall not be placed until: All reinforcement installed as per design
label | b625c8d3-b7e9-5cff-ace5-47ad35d33144 |  | note | Test / Inspection Method & Frequency - Visual Inspection prior to concrete pour
label | 2c71a0e4-3734-5a23-9128-672877328253 |  | note | Key - SE (W)
label | 98aa76f4-611d-5425-833d-6f18c039fae2 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 1bd5ce33-f79e-55b3-9110-7b433614e3fa |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.4 - Pre-pour inspection: Formwork, falsework & scaffold
label | 6908c77a-af53-5844-b48d-abe9960b0513 |  | note | Specification Reference - VicRoads 610.18, VicRoads 614 IFC Drawings Temp Works Design & Procedure AS 3610
label | 21e68fda-4b94-5f96-8458-3e565dad005a |  | note | Acceptance Criteria - On-site inspection and validation of Temporary Works Design, Falsework erected in accordance with certified design, Refer to checklist
label | 22173947-5d45-5d4e-91da-8581f4e3a2cc |  | note | Test / Inspection Method & Frequency - Visual inspection prior to concrete pour, Inspection of falsework construction by Engineer
label | 101c7dfb-a7d0-5cf9-8e4a-4a9fb7c455f0 |  | note | Key - SE (W)
label | df0f129b-bb9b-5125-a680-aa45e7ecba45 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 8519dcc7-9b27-53cf-8a02-31c223a896b9 |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.5 - Construction Joints
label | 95a79fbc-2eb3-5730-a4de-f863a17add24 |  | note | Specification Reference - IFC Drawings VicRoads 610.20
label | c61b6370-adec-5fd4-ad6e-088f56673e20 |  | note | Acceptance Criteria - Concrete cast against concrete to be clean and free of laitance with roughened and coarse aggregate exposed to depth of 3mm
label | f5aa0fe5-6b62-579f-980d-fbdc46d792fa |  | note | Test / Inspection Method & Frequency - As required
label | 240c4ec4-b99f-5221-b327-6883ae17db43 |  | note | Key - SE (W)
label | 82322c2d-76d6-50b9-bae5-03bb3c8ab915 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 8270e08e-e7b8-5a92-bed5-a5ff872269e7 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.6 - Cast in items, voids and block outs
label | 924fc2f6-19ee-5252-928e-70fc3811d823 |  | note | Specification Reference - IFC Drawings Temp Work Drawings
label | b3caceb6-d8d5-5420-bf03-64830fd2af52 |  | note | Acceptance Criteria - All cast in items, voids and block outs installed as per design and given tolerances
label | 966e3bab-5561-59b9-8151-faa5cdc5ea58 |  | note | Test / Inspection Method & Frequency - Visual Inspection prior to concrete pour
label | 2534e19e-8da2-5086-a45e-047e272f1b07 |  | note | Key - SE (W)
label | 229757b7-de74-5aa3-a4bc-5e7428289158 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 955c6421-4e0c-548c-b197-1ac2cc131422 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.7 - Install thermocouples to monitor early age thermal cracking of large members >500mm.
label | a5ae2240-61a5-5d75-ab36-921d2acf06d9 |  | note | Specification Reference - VicRoads 610.22
label | 0da32afa-343c-58f9-be3a-0826a52e6ad1 |  | note | Acceptance Criteria - Required for concrete members where:
label | c7043157-d4ab-566b-a6aa-0b9e55d30357 |  | note | (a) The least dimension of a member exceeds 500mm; or
label | e14f3401-6941-5404-8374-78d0a5cd9096 |  | note | (b) One or more faces of a concrete member is restrained by previously placed hardened concrete or by other external restraints.
label | 6bdb85ea-0f39-5110-adc8-fa1200e20711 |  | note | ○ Thermocouples installed
label | d014acfa-4741-5696-9942-e7bb3e261099 |  | note | ○ Temperature differential across concrete member is less than 20ºC during the period of curing.
label | 8d72af7c-0b80-5915-9dc0-54fc5cf71b03 |  | note | Test / Inspection Method & Frequency - As required
label | 75b4da52-b7c4-57ac-aad3-adecedb7d9f4 |  | note | Key - SE (W)
label | 388fe933-8385-5ffa-ac94-076d38f99960 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | e443801c-fe9b-5cc4-ba99-712fb4d33316 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.8 - Concrete supply & testing
label | 88efcc78-25ca-51d9-ad56-0c5920e8dff6 |  | note | Specification Reference - VicRoads 610.16 Mix Design AS 1379
label | 04606edf-43b2-59ab-9da3-15beb02eae54 |  | note | Acceptance Criteria - Slump tests acceptable within limits of mix design, If mix contains superplasticiser, slump testing shall be in accordance with VicRoads 610.16(c), Concrete samples taken in accordance with VicRoads 610.16
label | c7728a3b-7807-5bc2-b4a9-88891171b47f |  | note | Test / Inspection Method & Frequency - Complete the structural checklist for every pour, Testing frequency as per VicRoads Table 610.161
label | f971c7e9-86c3-5a2c-9197-3df299626ffe |  | note | Key - SE (W)
label | b3d2ac95-a782-5007-874f-f8009dad16e6 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | de1b8d20-5639-5457-842c-b8e899c1aa7a |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.9 - Discharge of Concrete
label | 51e53bc7-da26-52d0-b45d-dee3133231bf |  | note | Specification Reference - VicRoads 610.13, VicRoads 610.17, VicRoads 610.18 AS 1379
label | 22772aac-a118-5aa4-b871-58d23715e4e2 |  | note | Acceptance Criteria - Discharge completed within time limit approved on mix design, No water added once discharge commenced, Concrete temp between 10-32 °C and Air temp between 5-35 °C.
label | fdd88cc2-3694-5fe4-982c-db629b1f028e |  | note | Test / Inspection Method & Frequency - Visual inspection – Each delivery
label | ce6a277f-0392-51fe-9de1-0b7bb8798669 |  | note | Key - SE (W)
label | ea24ccec-beae-5db0-8b14-1233aea10c1f |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | b656126d-c1b2-5b61-ac4b-96b76ac96cb5 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.10 - Placement
label | 1edfbdc7-3e2f-5dd1-b3a5-4dee455ee7fa |  | note | Specification Reference - VicRoads 610.17, VicRoads 610.18
label | 2218b30b-8fef-58f8-bae6-2eaec202dfe3 |  | note | Acceptance Criteria - Placed in near horizontal layers not more than 350mm thick, Concrete shall not be dropped from a height exceeding 2m. Compacted with vibrators and power screeds as appropriate, Needle vibrators to be used vertically to full depth plus 100mm into the lower layer.
label | 73992913-fe4a-554b-b3e8-86fde2b8423c |  | note | Test / Inspection Method & Frequency - Visual inspection – Each pour
label | a98af70e-ea7f-5ebc-8fed-e87b6a6f5e03 |  | note | Key - SE (W)
label | c74a1575-e115-5f91-babe-907dc54fd104 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | ab72be0a-4a7c-5884-ab3a-e022ed731327 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.12 - Concrete Testing - Compressive Testing
label | b7575f8d-ae25-5532-9ec3-dd4198ea088d |  | note | Specification Reference - VicRoads 610.16
label | 44686bdd-65f1-552d-88e3-ac31780d10c0 |  | note | Acceptance Criteria - Concrete shall be tested for compressive strength in accordance with VR 610, 3 cylinders (1 x 7day, 2 x 28 Day) taken for each sample, minimum no. of samples:
label | dba3472e-82ac-5f53-8680-3261555c5488 |  | note | – – – – – – – – – – – – – – – – – – –
label | 4df56eab-1068-535e-af97-b6cccdb402ec |  | note | Quantity, m3 ¦¦ # Samples
label | 81ecdc1b-c519-5f71-b92d-51a34a7a6876 |  | note | – – – – – – – – – – – – – – – – – – –
label | 1d1f46e6-8ffa-5eaf-9c95-4da1a474c5be |  | note | 0-10 ¦¦ 1
label | 1ead7ef8-5528-581a-84d4-5f37b3568c18 |  | note | 10 to 25 ¦¦ 2
label | 6854eb64-65e1-5b15-976e-66084eb90235 |  | note | 25 to 50 ¦¦ 3
label | 42738e99-fb79-534f-a53f-ab1e9e42e146 |  | note | 50 to 100 ¦¦ 4
label | 9ed201c7-be2a-5f9f-bb47-cb842fdac415 |  | note | >100 ¦¦ 1 sample for each 50m3 >100
label | f677c846-c1fb-505b-aaa4-08a15f4480b3 |  | note | – – – – – – – – – – – – – – – – – – –
label | 10544b3e-dcc7-5e43-8314-5f63e2554200 |  | note | Test / Inspection Method & Frequency - Each Pour
label | ae501aa5-d68f-5a20-9f02-df312a20584f |  | note | Key - SE (W)
label | 6eed8006-1b75-5b46-9ecb-34a9b85fb70d |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 05b60b5f-606e-51f5-bc16-5fc000523af2 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.13 - Formwork and Falsework Deformation check
label | 770418a9-2c3a-5da9-8311-8d12a3c8a7c1 |  | note | Specification Reference - Temp Work Drawings
label | 26d17521-c279-5cb9-b69b-a967542ddf3d |  | note | Acceptance Criteria - Ensure that no significant deformations have occurred during the pour
label | 4f097f21-e982-5f49-8d8a-ca635dc3cf06 |  | note | Test / Inspection Method & Frequency - Visual – Each Pour
label | 7f9bed9a-3cbb-5bec-813d-043c50f6698a |  | note | Key - SE (W)
label | c388916a-8ff0-5420-add5-e11879e5a650 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 667b9957-6693-5e8b-86bc-bac195455a5a |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.14 - Surface Finishing
label | bf15cfe3-a8a9-5f3f-a6f5-7d3f69da6e4c |  | note | Specification Reference - VicRoads 610.31, VicRoads 610.18(d)
label | 8940b13d-4a69-5e39-b2eb-bca1edc7f373 |  | note | Acceptance Criteria - Surface finished as specified in drawings, Joint surfaces left rough, set retardant applied where required
label | 5dbde385-bb60-581a-a7a0-c0af2fd1faf5 |  | note | Test / Inspection Method & Frequency - Visual – Each Pour
label | 1986f397-9d69-5435-b328-e3a2d0630a0f |  | note | Key - SE (W)
label | 1c77a576-adf8-5125-ae7d-705c502b2ea6 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | cca50a6d-43c0-5d57-9fda-90b3d8370d1f |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.15 - Curing
label | a12d759f-7283-5123-9160-ed2018a4a7fc |  | note | Specification Reference - VicRoads 610.23 BCRC REPORT
label | 3440cc76-edae-5abf-9b85-d0cac0ffff93 |  | note | Acceptance Criteria - Approved methodology and application rate
label | b8d51f15-d994-53fb-82c0-e71e3f39a7f4 |  | note | Test / Inspection Method & Frequency - Where Required, after discharge
label | cd4c7a75-3ffe-5e15-b09d-56767de21451 |  | note | Key - SE (W)
label | 06be64df-6698-528d-87ee-6edcf915f1d4 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 76032dd2-4d8d-57b1-b92b-681cd8f5dd6d |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.16 - Removal of Form / Falsework & Inspection of Stripped Surfaces
label | b36bca2c-1651-5284-8ed8-b78abb581a59 |  | note | Specification Reference - VicRoads 610.24, VicRoads 610.25, VicRoads 610.31, VicRoads 610.34
label | 34453362-b6b5-5117-9304-114af6c17bd3 |  | note | Acceptance Criteria - Falsework and formwork removed no earlier than specified in Table 610.251, unless otherwise approved, Specified Surface finish class achieved. Specified cover achieved within tolerance
label | 38678cf5-584b-5b4d-913c-792769fe5cc4 |  | note | Test / Inspection Method & Frequency - Visual Inspection – Each Pour, 10 cover checks in 3m2 test areas for every 25m2 surface area
label | 2f970fdd-0fb9-5747-8495-4786d1371009 |  | note | Key - SE (W)
label | 9e7eadc1-0867-566f-ad9f-2cb7f0023bd6 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | ec96e748-bb16-5ce8-80d4-c664c5ad946a |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.17 - Patch repair (Where applicable)
label | 54d290af-cf30-5e7c-ae28-81e4db6cec68 |  | note | Specification Reference - VicRoads 610.32, VicRoads 689
label | 5ed64306-ec3f-50f5-b970-e30e70ea5930 |  | note | Acceptance Criteria - Surfaces repaired using approved cementitious products achieving similar texture and colour to surrounds
label | 5b493662-9e11-57d3-b0b8-be323b65605a |  | note | Test / Inspection Method & Frequency - Review – Each Pour
label | de3171ad-59b3-5b60-a0ca-ee91aaee0c11 |  | note | Key - SE (W)
label | 58b14841-3460-5c79-8d5b-116a555259d9 |  | note | Multiplex / Vic Roads Key - SE (W)
boolean | 3539b354-d3b9-5078-8b55-9d0ae11a2f28 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 4.18 - Crack Inspection and repair (Where applicable)
label | fcf995b7-89be-5c27-8e95-1250918734b2 |  | note | Specification Reference - VicRoads 610.24, VicRoads 687
label | bf4a271f-a128-54c3-b7bc-a4dbd6047b8b |  | note | Acceptance Criteria - Structural cracks assessed by qualified professional, Approved crack repair procedure
label | f2537806-a09e-5491-8ddb-5972e756e02b |  | note | Test / Inspection Method & Frequency - Visual/measure– Each Pour
label | dc93717e-86eb-5095-bcb6-dda2bb0afb23 |  | note | Key - PE (W)
label | 1639ba0b-81d4-58ad-8c33-2a192c2587d2 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 0b43613e-bf40-536e-832e-c6f5d968edcc |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 TESTING AND COMMISSIONING REQUIREMENTS – Post Construction Works – Sub-lot Records (if applicable)
checkpoint-status |  |  | checkpoint | 5.1 - As Built Survey
label | c6a8fb7a-d570-50c8-a954-fba3762d2d69 |  | note | Specification Reference - IFC drawings
label | 7a8263f5-61af-5d65-91cb-2eb11dda1218 |  | note | Acceptance Criteria - As-built survey is within tolerance when compared to Design & Specifications
label | abaf6591-6a79-5e9d-ba92-dcea90d77ef0 |  | note | Test / Inspection Method & Frequency - As-built vs Design Survey is within Tolerance
label | 13898459-d8a6-5311-91dd-67ab8272be01 |  | note | Key - SE (R)
label | 06003bb9-0085-5dd8-84f3-ffd16e00ebc9 |  | note | Multiplex / Vic Roads Key - SE (R)
boolean | 7897cc41-c664-513f-af1a-2c249a2c9b57 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 5.2 - Maturity Testing
label | 14d658fc-d543-5c47-8dc7-430502d7e0be |  | note | Specification Reference - VR610.16
label | f62f2841-154a-5fe5-8835-10088a0c9b55 |  | note | Acceptance Criteria - Confirm concrete has achieved minimum compressive strength required for demoulding/lifting
label | 973a44a6-9448-50b4-8e0f-f59b44fd671e |  | note | Test / Inspection Method & Frequency - As required
label | 563fcb31-0935-50c8-b31f-377215f67625 |  | note | Key - SE (R)
label | 980385c7-5b90-57da-8bff-e59d37ac4645 |  | note | Multiplex / Vic Roads Key - SE (R)
boolean | 5dd46f7e-3716-567a-9e52-a7899d93d37c |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 5.3 - Concrete cover checks
label | 312107bf-8db5-5ee7-b2bc-39397c9f224b |  | note | Specification Reference - VR610.34, VR 610.41 AS5100.5, 4.14.3
label | 72845051-7653-5893-b7ec-a17abd5ff1e9 |  | note | Acceptance Criteria - Minimum Cover measurements demonstrated that minimum concrete cover as per the drawings and the allowable dimensional tolerances as stated in Clause VR 610.41.
label | deae555b-46e4-5a52-9ecd-a02c1f059061 |  | note | Test / Inspection Method & Frequency - Min. 10 concrete cover measurements carried out using a cover meter in a 3m2 test area for every 25 m2 or part thereof on a representative and randomly selected number of exterior surface areas. Record min. measurement.
label | 7070c0b2-e554-5233-90ba-e0ac60ac19ae |  | note | Key - SE (R)
label | 133fece3-74f7-544a-869d-a0639390d57a |  | note | Multiplex / Vic Roads Key - SE (R)
boolean | f309fa95-06c0-57fc-b6f0-f2dcdb85e6f3 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 5.4 - Temperature Monitoring Report
label | 737c494a-8b9a-5b23-9420-857d56b739a8 |  | note | Specification Reference - VR 610.22
label | 9e8ca5b8-4f1b-53b9-b950-9ee5e30623aa |  | note | Acceptance Criteria - Monitor early age thermal cracking of concrete for large and restrained members to ensure temperature differential is not greater than 20°C during the period of Internal concrete temperature does not exceed 75⁰C.
label | eef65086-57b0-5168-8ec9-0a85bf248526 |  | note | Test / Inspection Method & Frequency - As required
label | ace8a79c-e223-50f8-bcaf-19430ff7ef24 |  | note | Key - SE (R)
label | 3d091b31-1307-59d0-8650-dcd876ddf772 |  | note | Multiplex / Vic Roads Key - SE (R)
boolean | 14ee1a7e-80b8-5b39-8609-ec77f14b9122 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 5.5 - Laboratory testing of concrete
label | 0b235333-cded-5a25-ab27-ddab42b6cd8a |  | note | Specification Reference - VicRoads 610.05, VicRoads 610.16
label | 03f1c098-1c9a-500a-b714-e85f90fa5ed6 |  | note | Acceptance Criteria - Compressive strength testing, Slump test results
label | d5fc8e52-004d-509d-b584-25775bc78473 |  | note | Test / Inspection Method & Frequency - As per VicRoads Table 610.161
label | d0d2f38e-bbfc-5e4e-a157-1c1620192f67 |  | note | Key - SE (R)
label | 9130a4a7-0162-5344-af73-add9f06c22d2 |  | note | Multiplex / Vic Roads Key - SE (R)
boolean | b5d8d74d-5326-545c-8445-1259b0064e44 |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-group |  |  | section | 6.0 COMPLETION REQUIREMENTS – Post Construction Works – Sub-lot Records (if applicable)
checkpoint-status |  |  | checkpoint | 6.2 - Close out NCR(s)
label | bbe2d6bd-e75d-5d77-858c-3511195e8dae |  | note | Specification Reference - Project Specification
label | aeb8a365-e947-55c5-aea1-67d873adef76 |  | note | Acceptance Criteria - All out of tolerances notified via Site NCR reporting system
label | 4b623900-ba96-50f7-b57e-80c33d910867 |  | note | Test / Inspection Method & Frequency - Prior to closing and signing ITP
label | 35d8969a-ef7e-5eb8-9661-3b907565aa67 |  | note | Key - PE (H)
label | f119231e-2459-5932-bf5e-8acceb6492a4 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 1a7f50a5-6e5c-5bd0-8199-ffd08bb05c16 |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.3 - Relevant RFI(s):
label | 15e8801e-d730-5787-9ffb-bea8d6d04ba1 |  | note | Specification Reference - Project Specification
label | 9817e656-d238-5861-b852-90685553b536 |  | note | Acceptance Criteria - Design/Construction Queries or clarifications relating to this ITP are addressed and closed. All ‘parts’ of RFI are included. All ‘supporting evidence’ is included
label | eca2f7a3-a5e7-545f-9ba6-37290b60157f |  | note | Test / Inspection Method & Frequency - RFIs closed and linked to NCRs where applicable
label | f0b96621-327d-5273-8f45-97ac22167beb |  | note | Key - PE (H)
label | e0c846ec-8485-5211-bd72-261dcc02e295 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | a16b3e42-e151-53e6-a475-8811d8f89c8a |  | tickbox | Records & Comments - Structural Concrete Checklist
checkpoint-status |  |  | checkpoint | 6.4 - Redline Marked-up Drawings
label | 4c4255a3-9aaf-5b8c-885d-ce31fc4b2d70 |  | note | Specification Reference - Project Specification
label | 4f06278f-d57b-5278-ae4e-090d331c4381 |  | note | Acceptance Criteria - Redline drawing to be produced & maintained by engineers to include all changes made during construction, Redline to use latest IFC version of the design drawings and be marked- up in red pen, to identify any variations, RFI, DCR, ECW and Client Wavers to be referenced in redlines (as required)
label | 11423b42-e48d-53e6-b6ac-fc4220eebde4 |  | note | Test / Inspection Method & Frequency - Completion of Works
label | 5362700f-fdd6-5235-bb8c-536c780075ef |  | note | Key - PE (H)
label | ba9a5726-e2e5-5bfb-ae39-d0d8b730d575 |  | note | Multiplex / Vic Roads Key - PE (H)
boolean | 9b349039-0608-5eee-9445-0aa5440b611c |  | tickbox | Records & Comments - Structural Concrete Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | ITP CLOSE OUT
text | 6751def3-43d9-5959-98c7-6fe0a0be2aaf |  | textbox | Vic Civil Representative:
text | 59490bbf-17ff-5f93-8ee0-ddad03135221 |  | textbox | Multiplex Representative:
date | c01493da-fecd-5fce-a9dd-7806b0aa8d51 |  | date | Date:
holdpoint |  |  | signoff | Vic Civil/Multiplex Signature
checklist-sectioned |  |  | checklist | ITP007 - Concrete - Column Installation | itp |  |  |  | Yes | ITP007 - Concrete - Column Installation | f41499fc-e2b7-4fd9-a8aa-74cd935c27d9
checkpoint-group |  |  | section | SECTION 1 – GENERAL DETAILS
checkpoint-no-status |  |  | checkpoint | GENERAL DETAILS
text | 42a92198-ecb3-5b25-84ce-b0ef0cb4b3a8 |  | textbox | Project Name:
text | 7978ae2b-d9eb-50c3-88d4-e531569b8a53 |  | textbox | Project Number:
label | b3e140f8-187e-5227-b018-c0a59c0410fc |  | note | Client:
label | 83eeeda5-ca10-5258-841b-91386d45da40 |  | note | Contract Number:
label | e041717a-10f7-5af7-ace0-abe1591801ed |  | note | Lot Number / ID
text | 66b71f17-4b8e-5c23-95af-0eb55b7de0fe |  | textbox | ITP Number:
text | 1ce8de30-1c27-572e-8bc0-dd42771511e2 |  | textbox | Version:
label | ce367631-fd9a-5809-8bf4-57f4837ef0b4 |  | note | ITP Description: Install Concrete Column
text | 3f8e69d2-9743-5801-a1de-10fd1a1cc7f6 |  | textbox | Prepared By:
date | ad7907f0-5351-5f83-b53c-a686ab50f74b |  | date | Revision Date
checkpoint-group |  |  | section | SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
checkpoint-no-status |  |  | checkpoint | ITP Close-Out by Vic Civil
text | 8bb66d57-c1cf-509d-a395-f9980e643568 |  | textbox | Name:
date | a20db616-61b9-5c64-bfc1-170acd790905 |  | date | Date:
checkpoint-no-status |  |  | checkpoint | Client Close Out (If Req)
text | ac7d5347-8905-56ba-a08a-51f177a36ef2 |  | textbox | Name:
date | 4896ddc4-201d-53f3-a88a-a3e100422eaa |  | date | Date:
checkpoint-group |  |  | section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint-status |  |  | checkpoint | 3.1 - Survey / Set out
label | c43a51fd-688c-5e36-8ba0-141834a3ee31 |  | note | Inspection Point: Quality Control Activity - Levels confirmed on site
label | 950dbd46-bc0c-5bdb-9911-a46da82757ff |  | note | Acceptance Criteria - Set out in accordance with design drawings or site conditions
label | d380a811-f080-5fa0-afca-827e35c59989 |  | note | Verifying Document - Visual Inspection / On Site Verification
label | 885ee09c-2c49-5e51-95e5-e260738af7f3 |  | note | Key - I
label | b13111e9-0c5c-5ccf-9052-4609e974c5f1 |  | note | By - IP
checkpoint-group |  |  | section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint-status |  |  | checkpoint | 4.1 - Reinforcement Installation
label | 4bc0ece2-0937-5f0e-a426-050d353c2ca1 |  | note | Inspection Point: Quality Control Activity - Structural Reinforcement as per Structural Design documentation / additional SDA
label | 72dee98e-b0a1-59ab-a6ea-ccb70e12b93d |  | note | Acceptance Criteria - Steel bar installed as required, with starter bars if needed
label | d5c533b8-e432-5b52-99e5-6af074ee030c |  | note | Verifying Document - Client Engineering Inspection
label | 3a475025-1e31-5cb5-bcb0-0d0aca433b1f |  | note | Key - HP
label | bce1f12e-bba9-596b-8a08-52eaf99ef148 |  | note | By - IP
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Formworks
label | f9b6620d-4d8a-54c1-a352-12c2d9add61f |  | note | Inspection Point: Quality Control Activity - Formworks to comply with the final shape/size of the column
label | 4477bb4f-4fa5-50a5-92de-7d6ccef14e07 |  | note | Acceptance Criteria - Formworks match designs and will enable concrete finishes as desired
label | 29f035b1-6a8a-5912-bea8-6e1dcc63d856 |  | note | Verifying Document - Visual Inspection
label | 366de69d-fc34-5c95-8d77-a41036802270 |  | note | Key - WP
label | f09f6793-8da9-5235-a637-4020e8d278a8 |  | note | By - IP
checkpoint-status |  |  | checkpoint | 4.3 - Finish
label | 87973ec9-4dc8-5a07-b732-96aa554e1a5b |  | note | Inspection Point: Quality Control Activity - Finish surface of column or off-form finish
label | ed095117-4790-558a-a442-f9f69a771ec2 |  | note | Acceptance Criteria - Finished as required
label | 600dfc30-57cb-5cab-8d60-c1453f2831ad |  | note | Verifying Document - Visual Inspection
label | bb0ec99c-f2b7-5fb5-8535-d8defa04d8f3 |  | note | Key - WP
label | 1067d326-2da2-5901-82b5-3678bde9764e |  | note | By - IP
checkpoint-status |  |  | checkpoint | 4.4 - Pre-Pour Concrete Check
label | 0c31437a-fd50-5fb3-9bc8-ceeba4b7720f |  | note | Inspection Point: Quality Control Activity - Inspection of reo and formworks
label | a488eef5-e651-5de7-8c2c-7a2509b9c6a0 |  | note | Acceptance Criteria - Steel reinforcement in accordance with design documentation
label | d621992a-36b2-5de1-8e90-38a70b351062 |  | note | Verifying Document - Client Inspection
label | 37ab53d0-d680-5faa-9eb4-fc1de3620358 |  | note | Key - HP
label | ded7bc38-6dd9-5e6a-8371-b30861ff4b88 |  | note | By - IP
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.5 - Concrete Pour
label | 71dedf9b-27c3-5811-868d-153deaf8f79b |  | note | Inspection Point: Quality Control Activity - Concrete is poured to required levels and strength
label | a747667d-357b-5281-9a97-ee71261a6504 |  | note | Acceptance Criteria - Strength and finish requirement met, Finished level within tolerances
label | 291f3953-60f6-5fa8-8a36-7ff5261dbdbd |  | note | Verifying Document - Visual inspection Strength Test Supplier:
label | 8c9a4004-0c8e-53b9-b3aa-af6a56a739ee |  | note | Key - HP
label | ef7534b4-3e97-5d7c-8f4c-6ecde626de74 |  | note | By - IP
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint-status |  |  | checkpoint | 5.1 - Completions
label | c7357bfc-f061-5294-8c40-ce25d17fdecb |  | note | Inspection Point: Quality Control Activity - Inspection of works
label | 24c0a87c-edc0-5226-8719-d27908e8cfc8 |  | note | Acceptance Criteria - Works completed to the client requirements
label | af1b92e9-c86a-5dcc-958f-10426772e73c |  | note | Verifying Document - This document
label | 6c2295b0-2f02-55ae-925d-593951621e7d |  | note | Key - H
label | 254d8d68-ba05-57aa-b173-e94f139b23fd |  | note | By - PE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | SECTION 6 – COMMENTS
checkpoint-no-status |  |  | checkpoint | Comments