## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-019-AX-LOT-XXX - Desc | itp |  |  |  |  | ITP 0019 - Bonded Anchors (100 Year Design Life)
section | 1 - Preliminaries - Materials
checkpoint | 1.1 - Bonded Anchor System - Chemical Adhesive
label | Reference: IFC Drawings 680.05 (a), 680.05 (b) (i - vi)
label | - - - - - - - - -
label | Acceptance Criteria: Bonded anchor systems shall be certified in accordance with a third party materials accreditation scheme shown below:
label | i. ATIC SPEC 38
label | ii. EOTA EAD 330499-00 or 01-0601
label | iii. ICC-ES (USA)
textbox | Enter: Teambinder Material Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Once, per product, prior to commencement of Works
label | - - - - - - - - -
label | WP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 1.2 - Bonded Anchor System - Reinforcement
label | Reference: IFC Drawings 680.05 (c), 611.05 (a)
label | - - - - - - - - -
label | Acceptance Criteria: Where applicable, current ACRS certification for materials and for bar processing.
label | Anchor bars need to remain uncoated (black) for durability purposes in fatigue loading.
label | Note: Galvanised steel dowels are only to be used where maximum design life is 25 years and only permanently dry conditions.
label | Note: ACRS certificate may cover both aspects or be for each separate portion (e.g 1 for the material supplier and another for the bar processor (bending, cropping and delivery)
textbox | Enter: Teambinder Material Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Where applicable, once for each supplier, 14 days of award of contract
label | - - - - - - - - -
label | WP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 1.3 - Bonded Anchor System - Stainless Steel Anchors
label | Reference: IFC Drawings 680.05 (c)
label | - - - - - - - - -
label | Acceptance Criteria: Where applicable, stainless steel grades 1.4401, 1.4404, 1.4362 and 1.4571 (marking A4) may not be used in conditions where the component is either permanently inundated in seawater or in the splash zone.
label | Stainless steel grades 1.4529 (marking C) may be used in conditions where the component is either permanently inundated in seawater or in the splash zone.
textbox | Enter: Teambinder Material Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Where applicable, once, prior to commencement of Works
label | - - - - - - - - -
label | WP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 1.4 - Bonded Anchor System - Proprietary Threaded Anchor Rods CHAR(AMP) Metallic Bolts
label | Reference: IFC Drawings 680.05 (c)
label | - - - - - - - - -
label | Acceptance Criteria: Where applicable, bonded anchor systems shall be certified in accordance with a third party materials accreditation scheme shown below:
label | i. ATIC SPEC 38
label | ii. EOTA EAD 330499-00 or 01-0601
label | iii. ICC-ES (USA)
textbox | Enter: Teambinder Material Approval Number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Where applicable, once, prior to commencement of Works
label | - - - - - - - - -
label | WP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 1.5 - Ultimate Load Testing (for Alternate Product or Changes to Existing Product)
label | Reference: 680.05 (a), 680.09 (b)
label | - - - - - - - - -
label | Acceptance Criteria: Where applicable, if an alternative system is proposed, where a bonded anchor system falls outside the scope of certification or where directed by the Superintendent, Ultimate Load Testing shall be performed to validate the bonded anchor system meets or exceeds the intended durability and load capacities.
label | A sample of 5 no. anchors per combination of adhesive type, anchor orientation, type, grade, diameter and concrete grade shall be installed in accordance with the manufacturer's installation instructions, load tested and results reported by a third-party accredited testing authority.
label | Refer to section 5.2 if the Ultimate Load Test fails.
label | Results of the Ultimate Load Testing to be submitted to the Superintendent.
textbox | Enter: Teambinder Approval number
label | - - - - - - - - -
label | Frequency: Where applicable, 2 weeks prior to installation of anchors
label | - - - - - - - - -
label | HP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: ConQA Hold Point Release
holdpoint | AUTHORITY HOLDPOINT
section | 2 - Preliminaries - Documentation & Procedures
checkpoint | 2.1 - Design of Bonded Anchors Subject to Tensile Forces
label | Reference: 680.04 BTN 006, Clause 2.6
label | - - - - - - - - -
label | Acceptance Criteria: If bonded anchors are proposed to be used in full or partial tension, submit full details of the proposal, including a Proof Engineering Certificate of Compliance, for the approval of the Superintendent.
label | The Design Engineer must be a member of Engineers Australia and have a minimum of 5 years experience in the design and construction of bonded anchors.
label | The Proof Engineer must be independent of the Design Engineer and be pre-qualified to DTP's level PE.
textbox | Enter: Teambinder Approval number
label | or
label | Attach: PE Certificate of Compliance
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Where applicable, 2 weeks prior to installation of anchors
label | - - - - - - - - -
label | HP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: ConQA Hold Point Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Bonded Anchor Work Method Statement
label | Reference: 680.11, 680.07
label | - - - - - - - - -
label | Acceptance Criteria: Bonded anchor WMS, detailing the method for locating reinforcement/tendons/services, equipment to be used, load testing regime and repair of concrete (spalled and cracking) to be submitted for review to the Superintendent.
textbox | Enter: Teambinder Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Once, prior to trial installation
label | - - - - - - - - -
label | HP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: ConQA Hold Point Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Load Testing Work Method Statement
label | Reference: 680.09 (a)
label | - - - - - - - - -
label | Acceptance Criteria: Load Testing WMS, detailing the target loads (1.5x or 2x the design loads), load increments, duration for the load to be stained at each increment, testing frequency, measures if fail occurs and equipment to be used.
label | Additional testing equipment requirements:
label | i. capable of measuring the applied force to an accuracy of ±2%
label | ii. capable of measuring the elongation with an accuracy of ±0.02 mm
label | iii. have a valid calibration certificate
label | The above is to be submitted for review to the Superintendent.
textbox | Enter: Teambinder Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Once, 1 week prior to prior testing
label | - - - - - - - - -
label | HP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: ConQA Hold Point Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.4 - Competency & Training of Personnel
label | Reference: 680.06
label | - - - - - - - - -
label | Acceptance Criteria: All bonded anchor installation crews and direct supervisory personnel shall either be:
label | i. listed on the "AEFAC Certified List of Installers"; or
label | ii. trained by the Supplier of the bonded anchor system.
label | Evidence of either is to be submitted to the Superintendent.
label | The bonded anchor tester shall be experienced in testing bonded anchors and test reporting.
textbox | Enter: Teambinder Approval number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Once, prior to commencement of Works
label | - - - - - - - - -
label | WP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: This ITP
section | 3 - Pre-installation Activities
checkpoint | 3.1 - Installation Equipment
label | Reference: 680.07 Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Bonded anchors shall be installed using the equipment specified by the bonded anchor system's installation instructions.
label | This includes drill bits / dustless drill bits, diamond cores, roughening tools, cleaning brushes, mixing nozzles, piston plugs and extensions.
label | - - - - - - - - -
label | Method: Visual
label | - - - - - - - - -
label | Frequency: Each discrete population
label | - - - - - - - - -
label | IP
checkpoint | 3.2 - Setting Out
label | Reference: 680.08 (a) Bonded Anchors Work Procedure
label | - - - - - - - - -
label | Acceptance Criteria: Locations of bonded anchor holes shall be positioned at the design spacings and angles using a calibrated covermeter or ground penetrating radar (GPR) to ensure that no damage occurs to reinforcement, pre-stressing strand, ducting and embedded services.
label | Where clashes are detected, adjust the anchor location if able to maintain the maximum and minimum spacings, edge distance and cover requirements.
label | If unable to maintain these parameters, consult the Designer Engineer via the RFI process to provide updated locations.
label | Note: The marked out locations shall be traceable to determine a discrete population of anchors and installed by the same work crew.
label | - - - - - - - - -
label | Method: Measure, Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: Surveyor, SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
section | 4 - Installation Activities
checkpoint | 4.1 - Hole Drilling/Coring
label | Reference: 680.08 (a) & (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Holes shall be drilled or cored in the orientations, angles (if not perpendicular to the concrete surface) and depths shown on the IFC drawings.
label | Drill or core diameters shall be those shown in the manufacturer's installation instructions.
label | Coring may require the internal surface of the hole to be roughened.
label | If reinforcement is encountered during the drilling or coring process, cease drilling immediately and relocate the hole.
label | Refer to section 5.4 for repair of abandoned holes.
label | If reinforcement is damaged, consult the Designer Engineer via the RFI process to provide a clear direction moving forward prior to continuing installation of that discrete population of anchors.
label | - - - - - - - - -
label | Method: Measure, Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.2 - Hole Cleaning
label | Reference: 680.08 (a) & (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Hole cleaning shall commence as soon as practical following the drilling / coring process to remove debris, dust particles and moisture / free-standing water (where required).
label | The process shall follow the manufacturer's installation instructions which is a repetitive sequence of brush cleaning and air flushing, resulting in no dust detected on a finger-tip when in contact with the internal wall of the hole.
label | The minimum hole depth shall be verified before proceeding to the next step.
label | Note: Where hollow-tipped drill bits are used in conjunction with a vacuum drill, cleaning may not be required - consult the manufacturer's installation instructions.
label | - - - - - - - - -
label | Method: Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.3 - Substrate Temperature
label | Reference: 680.08 (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Bonded anchors shall not be installed where the temperature of the concrete is less than -5°C, or greater than 40°C or outside the limits shown on the manufacturer's installation instructions.
label | Record: The substrate temperatures at the time of commencing the discrete population, the corresponding available working and curing times and the temperature at the completion of installation.
label | - - - - - - - - -
label | Method: Measure, Visual
label | - - - - - - - - -
label | Frequency: Each discrete population
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.4 - Anchor Surface Condition
label | Reference: 680.08 (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Anchors shall be clean, free from debris, oil and other contaminants.
label | Note: Any substrate coatings may need to be factored into determining the embedment depth
label | - - - - - - - - -
label | Method: Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.5 - Adhesive Injection
label | Reference: 680.08 (a) & (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: Connect the specific adhesive, cartridge gun and required injection equipment (nozzle, tubes, piston plug and valves) for the task and discharge the initial adhesive to waste to ensure that only fully mixed product will be used in the Works.
label | Note: Repeat the "initial discharge to waste" for each new mixing nozzle used and do not modify the nozzles.
label | Inject the adhesive into the hole, starting from the base working towards the substrate surface at a rate that prevents the creation of air voids, until approximately 2/3 of the hole depth is reached, checked visually prior to the insertion of the anchor.
label | - - - - - - - - -
label | Method: Measure, Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.6 - Anchor Insertion
label | Reference: 680.08 (a) & (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: While the adhesive is within the temperature dependent working time, the anchor shall be inserted and verified to the minimum embedment depth with a singular twisting motion, to ensure that the adhesive completely surrounds the anchor.
label | Where required, the anchor shall be centralised within the hole using temporarily supports to provide a uniform film of adhesive around the anchor and Excessive adhesive shall be cleaned from the substrate surface.
label | Loss of adhesive during the working time shall be prevented by sealing around the anchor as required.
label | - - - - - - - - -
label | Method: Measure, Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 4.7 - Adhesive Curing
label | Reference: 680.08 (a) & (b) Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: The anchor shall not be disturbed, moved, loaded or torqued during the specified temperature dependent curing period before proceeding to the next step.
label | - - - - - - - - -
label | Method: Visual
label | - - - - - - - - -
label | Frequency: Each anchor
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
section | 5 - Post-installation Activities
checkpoint | 5.1 - Proof Load Testing
label | Reference: 680.09 (c) Load Testing of Bonded Anchors Work Procedure, Manufacturer's Installation Instructions
label | - - - - - - - - -
label | Acceptance Criteria: After completion of the curing period, bonded anchors shall be subject to proof load testing, as outlined in the approved Work Procedure for Load Testing of Bonded Anchors.
label | All (100%) of anchors subject to tensile loads, a combination of shear and tensile loads or fatigue loads, shall be tested.
label | All other anchors not subject to tension shall be tested at the greater number of 2.5% of the lot quantity or 5 no. anchors.
label | Test results shall be equal to or greater than the factored tensile or shear loads and equal to or less than the maximum displacements shown in the Manufacturer's Installation Instructions.
label | If any anchor fails the proof load or is displaced beyond the limits, the entire discrete population shall be tested for compliance.
label | Refer to section 5.2 if the entire discrete population fails.
label | Attach: Proof Load Test Results
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Each discrete population
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 5.2 - Failure of Load Testing
label | Reference: 680.09 (d) Load Testing of Bonded Anchors Work Procedure
label | - - - - - - - - -
label | Acceptance Criteria: Should an anchor fail an Ultimate Load test, or an entire discrete population fail a Proof Load; rectification proposals must be provided to the Superintendent for assessment prior to any further installation.
textbox | Enter: Teambinder Approval Number
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Where applicable
label | - - - - - - - - -
label | HP
label | - - - - - - - - -
label | Responsibility: Superintendent
label | - - - - - - - - -
label | Verifying Documents: ConQA Hold Point Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Surface Inspection - Cracks
label | Reference: Structural Concrete Crack Repair ITP
label | - - - - - - - - -
label | Acceptance Criteria: No cracks greater than the maximum widths shown below.
label | Exposure classification:
label | A = 0.2mm
label | B1 = 0.2mm
label | B2 = 0.15mm
label | C,U = 0.10mm
label | If cracking beyond the limits of the exposure classification is observed, follow Structural Concrete Crack Repair ITP (Specification 687), for investigation and repair.
label | - - - - - - - - -
label | Method: Visual, Measure
label | - - - - - - - - -
label | Frequency: Where applicable, each lot
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 5.4 - Surface Inspection - Abandoned Holes & Post-testing Spalling
label | Reference: IFC Drawings, Structural Concrete Patch Repair ITP 610.31 (a) - (n), 610.32
label | - - - - - - - - -
label | Acceptance Criteria: Where holes have been abandoned, follow Structural Concrete Patch Repair ITP (Specification 689) for repair.
label | Where spalling around a tested anchor has occurred, preparation of the repair shall follow the Structural Concrete Patch Repair but the repair may allow for the newly cast concrete to create the cover.
label | - - - - - - - - -
label | Method: Visual
label | - - - - - - - - -
label | Frequency: Where applicable, each lot
label | - - - - - - - - -
label | IP
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | 5.5 - Non-conformance Report (NCR) Closure
label | Reference: Project Quality Management Plan
label | - - - - - - - - -
label | Acceptance Criteria: Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | - - - - - - - - -
label | Method: Document Review
label | - - - - - - - - -
label | Frequency: Once, prior to closure of this lot / element / Work area
label | - - - - - - - - -
label | HP*
label | - - - - - - - - -
label | Responsibility: SE/PE/SPE
label | - - - - - - - - -
label | Verifying Documents: This ITP
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications
textbox | Print Name:
textbox | Position:
date | Date:
date | Work Completed On