## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITP017 Temp DBs |  |  |  |  | Yes | ITP017 Temp DBs | 5d39e870-b714-434b-b59d-ec8a361c768e
checkpoint-status |  |  | checkpoint | 1 - RCD
checkpoint-status |  |  | checkpoint | 2 - Date of testing
checkpoint-status |  |  | checkpoint | 3 - Next test due
checkpoint-status |  |  | checkpoint | 4 - Results and/or trip current (less 30ma) for earth leakage device
checkpoint-status |  |  | checkpoint | 5 - Has a new tag been installed on the db - please take a photo
checkpoint-status |  |  | checkpoint | 6 - Has the front cover been updated
checkpoint-status |  |  | checkpoint | 7 - Please take a photo of DB - pass once attached
checkpoint-status |  |  | checkpoint | 8 - Compliance certificate completed and attached
checkpoint-status |  |  | checkpoint | 9 - License no.
checklist-flat |  |  | checklist | ITP002 In-Deck/Slab Conduits |  |  |  |  | Yes | ITP002 In-Deck/Slab Conduits | 454702d3-cbbd-4f6e-9bd9-1a2e9ddb20fc
checkpoint-status |  |  | checkpoint | 1 - Confirm that the selected conduit is of adequate size for purpose
checkpoint-status |  |  | checkpoint | 2 - It has been confirmed that all outlets/fittings in slab have been captured
checkpoint-status |  |  | checkpoint | 3 - Conduit has been securely fixed
checkpoint-status |  |  | checkpoint | 4 - Conduit has been securely fixed to the box or volcano
checkpoint-status |  |  | checkpoint | 5 - Conduit box has temporarily been secured and tied down in place for pour
checkpoint-status |  |  | checkpoint | 6 - Alternative route has been supplied in case main route is damaged
checkpoint-status |  |  | checkpoint | 7 - Conduit runs have all been marked on as builts
checklist-flat |  |  | checklist | Emergency Lighting Testing Evidence |  |  |  |  | Yes | Emergency Lighting Testing Evidence | 3ad0c446-d3cb-4c9b-95fd-35f916e0038e
checkpoint-status |  |  | checkpoint | Emergency Lighting Testing Evidence uploaded
checklist-flat |  |  | checklist | ITP005 Mains, Submains Cable in Conduits or on Trays |  |  |  |  | Yes | ITP005 Mains, Submains Cable in Conduits or on Trays | d7ee0921-61da-4fa6-9a30-4b72e3e1a1f5
checkpoint-status |  |  | checkpoint | 1 - Measure cable runs with appropriate accurate measuring instrument eg tape measure, wheel
checkpoint-status |  |  | checkpoint | 2 - Check cable sizes. Resistance of protective earth conductor shall be low enough to permit passage of current necessary to operate protective device.
checkpoint-status |  |  | checkpoint | 3 - Confirm length of cable
checkpoint-status |  |  | checkpoint | 4 - Install cable in applicable method eg. Cable stands, electric winch, pulleys etc. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint-status |  |  | checkpoint | 5 - Tri-foil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status |  |  | checkpoint | 6 - Check requirements for cable identification and install
checklist-flat |  |  | checklist | ITP018 Temp Lighting |  |  |  |  | Yes | ITP018 Temp Lighting | 5e4936f5-f086-4a91-8502-9a6951e5c761
checkpoint-status |  |  | checkpoint | 1 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint-status |  |  | checkpoint | 2 - Install cable support system
checkpoint-status |  |  | checkpoint | 3 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint-status |  |  | checkpoint | 4 - Fix cables to support system
checkpoint-status |  |  | checkpoint | 5 - Temporary construction tape has been installed along cabling
checkpoint-status |  |  | checkpoint | 6 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint-status |  |  | checkpoint | 7 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint-status |  |  | checkpoint | 8 - Location/compliance
checkpoint-status |  |  | checkpoint | 9 - Fit off light fittings
checkpoint-status |  |  | checkpoint | 10 - Functional test carried out on each fitting
checklist-flat |  |  | checklist | ITP008 Data Wiring Rough In |  |  |  |  | Yes | ITP008 Data Wiring Rough In | a90e2c5b-c3fc-4457-ac4e-19dd5837f84c
checkpoint-status |  |  | checkpoint | 1 - Refer to drawing to determine cable support route and check separation from power services
checkpoint-status |  |  | checkpoint | 2 - Determine cable type
checkpoint-status |  |  | checkpoint | 3 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint-status |  |  | checkpoint | 4 - Install cable support system
checkpoint-status |  |  | checkpoint | 5 - Install and identify cables.
checkpoint-status |  |  | checkpoint | 6 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint-status |  |  | checkpoint | 7 - Fix cables to support system
checkpoint-status |  |  | checkpoint | 8 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint-status |  |  | checkpoint | 9 - All outlets have been wired as per drawings
checkpoint-status |  |  | checkpoint | 10 - All outlets have been marked on the site as built drawing
checkpoint-status |  |  | checkpoint | 11 - Height and location have been confirmed for each outlet
checklist-flat |  |  | checklist | ITP009 Power Installation and Fit Off |  |  |  |  | Yes | ITP009 Power Installation and Fit Off | 45264a0e-05b7-42c3-b65b-7397bf852744
checkpoint-status |  |  | checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint-status |  |  | checkpoint | 2 - Each circuit is terminated at the db and protected by the correct protective device
checkpoint-status |  |  | checkpoint | 3 - Location/compliance wet areas, hazards etc. Mounting heights,
checkpoint-status |  |  | checkpoint | 4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
checkpoint-status |  |  | checkpoint | 5 - Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use shroud. Each circuit must be fitted off completely.
checkpoint-status |  |  | checkpoint | 6 - Fit off final appliances
checkpoint-status |  |  | checkpoint | 7 - Functional test carried out on each outlet
checkpoint-status |  |  | checkpoint | 8 - Cover plates (if required)
checkpoint-status |  |  | checkpoint | 9 - Install label (if a specified requirement)
checkpoint-status |  |  | checkpoint | 10 - All outlets & appliances marked on the site as build’s
checklist-flat |  |  | checklist | ITP0012 Exit & Emergency Light Installation |  |  |  |  | Yes | ITP0012 Exit & Emergency Light Installation | de44cee0-0d93-4ae5-8c52-a7ab3968a6a3
checkpoint-status |  |  | checkpoint | 1 - Delivery check for damage and correct quantities
checkpoint-status |  |  | checkpoint | 2 - Locations coordinate with other services
checkpoint-status |  |  | checkpoint | 3 - Marking out (if required) - refer to reflected ceiling plan for locations
checkpoint-status |  |  | checkpoint | 4 - Plug in or fit off light fit-off data cable if applicable
checkpoint-status |  |  | checkpoint | 5 - Number and install light fitting and as built drawing
checkpoint-status |  |  | checkpoint | 6 - Install lamp & diffuser and clean fitting
checkpoint-status |  |  | checkpoint | 7 - Mark up lighting drawing, data loop included, numbering all exit and emergency lights (if applicable)
checkpoint-status |  |  | checkpoint | 8 - Complete log book and record results if applicable
checklist-flat |  |  | checklist | ITP015 Submains Test Results |  |  |  |  | Yes | ITP015 Submains Test Results | 152f9a66-a984-4a32-9594-71bfca8d8a1b
checkpoint-status |  |  | checkpoint | Submains Test Results - Complete and Test Sheet attached
checklist-flat |  |  | checklist | ITP006 Power Wiring Rough In |  |  |  |  | Yes | ITP006 Power Wiring Rough In | c06f951b-79d4-4ed6-a655-6f22c7be0987
checkpoint-status |  |  | checkpoint | 1 - Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint-status |  |  | checkpoint | 2 - Determine cable size
checkpoint-status |  |  | checkpoint | 3 - Cable sizes max length
checkpoint-status |  |  | checkpoint | 4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint-status |  |  | checkpoint | 5 - Install cable support system
checkpoint-status |  |  | checkpoint | 6 - Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint-status |  |  | checkpoint | 7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint-status |  |  | checkpoint | 8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint-status |  |  | checkpoint | 9 - Fix cables to support system
checkpoint-status |  |  | checkpoint | 10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint-status |  |  | checkpoint | 11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint-status |  |  | checkpoint | 12 - All outlets have been wired as per drawings
checkpoint-status |  |  | checkpoint | 13 - All outlets have been marked on the site as built drawing
checkpoint-status |  |  | checkpoint | 14 - Height and location have been confirmed for each outlet
checklist-flat |  |  | checklist | Toolbox Safety Talks Meeting Minutes |  |  |  |  | Yes | Toolbox Safety Talks Meeting Minutes | 0db990c1-00cf-4ec1-829b-2c298b42992d
checkpoint-status |  |  | checkpoint | Toolbox Safety meeting completed
text | 2a89c104-f7e9-5149-b1b3-f0b716afab44 |  | textbox | Location:
text | 418dc8ac-d145-5638-871a-fc7587bb5e0e |  | textbox | Date:
text | 358f1937-df0b-587e-8f48-8070e79972a9 |  | textbox | Client:
text | 8b0f244c-659e-5be6-8e40-18518758e711 |  | textbox | Supervisor:
text | 9c7f2b34-9642-5c10-86f0-fc6cc8aa28cc |  | textbox | Subject:
text | 9fae3c6d-f41a-57a3-bc49-cd8c33425315 |  | textbox | Duration:
text | d87e0f1f-3abf-5db1-ab36-aaab268d4663 |  | textbox | Persons present
text | 22d0c969-9512-5e57-8214-1e6d63a88dd7 |  | textbox | Comments & points raised
checkpoint-status |  |  | checkpoint | Signed off by Ergo Group Supervisor
checklist-sectioned |  |  | checklist | ITP001 Underground Conduits |  |  |  |  | Yes | ITP001 Underground Conduits | 4255957c-1940-4618-8151-69b764ad192d
checkpoint-group |  |  | section | Preparation
checkpoint-status |  |  | checkpoint | 1 - Determine origin & destination
checkpoint-status |  |  | checkpoint | 2 - Confirm area of work is accessible & acceptable to commence
text | 0cc52e13-dd65-5ac1-b55d-2f90e45fb25c |  | textbox | 3 - Drawing & revision number
checkpoint-status |  |  | checkpoint | 4 - Check clear of other services N.B. the clearance for gas pipes is 300mm & other services 100mm
checkpoint-status |  |  | checkpoint | 5 - Check cable size to verify conduit size & determining size of trench
checkpoint-status |  |  | checkpoint | 6 - Organise barricades, webbing, plates, warning lights if applicable prior to excavation
checkpoint-status |  |  | checkpoint | 7 - Determine spoil removal, back fill material, compaction, cable marking & protection & re-instatement requirements
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | 8 - Mark out trench route arrange saw cutting if required
checkpoint-status |  |  | checkpoint | 9 - Excavate trench & install barricades as required check depth, taking into account final ground levels
checkpoint-status |  |  | checkpoint | 10 - Determine which way cable will be installed and lay couplings in no friction direction, install conduit, glue
checkpoint-status |  |  | checkpoint | 11 - Install draw wire if required
checkpoint-status |  |  | checkpoint | 12 - Inspect trench by supply authority if applicable
checkpoint-status |  |  | checkpoint | 13 - Inspect & back fill trench
checkpoint-status |  |  | checkpoint | 14 - Re-instate & clean area
checkpoint-status |  |  | checkpoint | 15 - Install direction marker if applicable
checkpoint-status |  |  | checkpoint | 16 - Do sketch or mark up drg for future as builts
checklist-sectioned |  |  | checklist | ITP004 Conduit & Cable Tray |  |  |  |  | Yes | ITP004 Conduit & Cable Tray | 050464b1-c5a0-42ff-80d0-7f78f8c5ee9b
checkpoint-group |  |  | section | Conduit Installation
checkpoint-status |  |  | checkpoint | 1 - Coordinate with other services ensure segregation from comms / data services
checkpoint-status |  |  | checkpoint | 2 - Size and type of conduit
checkpoint-status |  |  | checkpoint | 3 - Install conduit
checkpoint-status |  |  | checkpoint | 4 - Fixings
checkpoint-group |  |  | section | Cable Tray Installation
checkpoint-status |  |  | checkpoint | 5 - Coordinate with other services
checkpoint-status |  |  | checkpoint | 6 - Size of cable tray each cable support has sufficient room for future expansion
checkpoint-status |  |  | checkpoint | 7 - Cable support system has been selected to correctly hold the required weight
checkpoint-status |  |  | checkpoint | 8 - Install fixings
checkpoint-status |  |  | checkpoint | 9 - Install cable tray cable support system has been correctly installed and is secure in place
checkpoint-status |  |  | checkpoint | 10 - Height of cable support system has been confirmed and installed to that height in all areas
checkpoint-status |  |  | checkpoint | 11 - Cable support system is as per shop drawings and not impacting any other services
checkpoint-status |  |  | checkpoint | 12 - All threaded rods have been cut off to correct size
checkpoint-status |  |  | checkpoint | 13 - All nuts/bolts/channel nuts have been tightened
checkpoint-status |  |  | checkpoint | 14 - Do sketch or mark up drawing for future as builts
checklist-flat |  |  | checklist | ITP010 Lighting Installation and Fit Off |  |  |  |  | Yes | ITP010 Lighting Installation and Fit Off | 1273c234-fc32-4d7b-a312-fa64e00da85d
checkpoint-status |  |  | checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint-status |  |  | checkpoint | 2 - Each circuit is terminated at the db and protected by the correct protective device
checkpoint-status |  |  | checkpoint | 3 - Location/compliance wet areas, hazards etc. Mounting heights,
checkpoint-status |  |  | checkpoint | 4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
checkpoint-status |  |  | checkpoint | 5 - Fit off final light fittings
checkpoint-status |  |  | checkpoint | 6 - Functional test carried out on each outlet
checkpoint-status |  |  | checkpoint | 7 - Cover plates (if required)
checkpoint-status |  |  | checkpoint | 8 - Install label (if a specified requirement)
checkpoint-status |  |  | checkpoint | 9 - All lights and switches marked on the site as build’s
checklist-flat |  |  | checklist | ITP016 Earth Grids / Lighting Protection |  |  |  |  | Yes | ITP016 Earth Grids / Lighting Protection | ceb8a2ce-8d73-424b-8610-c3a02de12374
checkpoint-status |  |  | checkpoint | 1 - Refer to drawings to determine size of grid.
checkpoint-status |  |  | checkpoint | 2 - Check size of cable and earth electrode.
checkpoint-status |  |  | checkpoint | 3 - Check specification for resistance level.
checkpoint-status |  |  | checkpoint | 4 - Drive earth electrode into ground.
checkpoint-status |  |  | checkpoint | 5 - Earth test electrode or grid.
text | 0b09b009-da4d-5705-87b0-1ced2b5c0a81 |  | textbox | Earth tester number
checkpoint-status |  |  | checkpoint | 6 - If insufficient reading, add other electrodes 2 metres apart and link up with initial electrode with earth cable.
checkpoint-status |  |  | checkpoint | 7 - Terminate cable from first electrode to frame or earth bar and label.
checkpoint-status |  |  | checkpoint | 8 - Test sheet completed and attached
checklist-flat |  |  | checklist | ITP003 Main Switchboard & Termination of Cables |  |  |  |  | Yes | ITP003 Main Switchboard & Termination of Cables | c01038d3-8e7f-40be-b735-686d2d301671
checkpoint-status |  |  | checkpoint | 1 - Locate and fix switchboard into position
checkpoint-status |  |  | checkpoint | 2 - Determine cable sizes for cable glands, mark out gland plate (if not previously determined at planning meeting)
checkpoint-status |  |  | checkpoint | 3 - Install cable glands and cables
checkpoint-status |  |  | checkpoint | 4 - Install lugs & terminate
checkpoint-status |  |  | checkpoint | 5 - Clean and vacuum out board
checkpoint-status |  |  | checkpoint | 6 - Check all circuits are terminated & safe at the other end or disconnect.
checkpoint-status |  |  | checkpoint | 7 - Visual inspection
text | 5762c427-dcec-58bc-b8b4-d6ea346510a7 |  | textbox | 8 - Test earth continuity and resistance
text | 91f17188-87f5-5432-8423-eea162ff6183 |  | textbox | 9 - Test insulation resistance
text | dcf8ff91-8c39-5fec-a6e4-7972edd2b88c |  | textbox | 10 - Test polarity
text | a0ee9a15-f721-59a7-b718-66e3acd77c02 |  | textbox | 11 - Test phase rotation
checkpoint-status |  |  | checkpoint | 12 - Lodge prescribed certificate of electrical safety. Organise inspection by inspector.
checkpoint-status |  |  | checkpoint | 13 - Isolate / lock off / danger tag all outgoing circuits.
checkpoint-status |  |  | checkpoint | 14 - Ensure all labelling is complete and accurate.
checkpoint-status |  |  | checkpoint | 15 - Energize
checkpoint-status |  |  | checkpoint | 16 - Check phase rotation
checkpoint-status |  |  | checkpoint | 17 - Check switchboard as installed matches shop drawing
checkpoint-status |  |  | checkpoint | 18 - Modify shop drawing to match existing & return to office
checkpoint-status |  |  | checkpoint | 19 - Clean switchroom
checkpoint-status |  |  | checkpoint | 20 - Check if requirement for spare fuse
checkpoint-status |  |  | checkpoint | 21 - Check requirements for laminated drawing to be installed
checklist-flat |  |  | checklist | ITP013 Install Distribution Boards -Terminate Cables |  |  |  |  | Yes | ITP013 Install Distribution Boards -Terminate Cables | 40800703-87cf-43dd-b5cd-0be89715be12
checkpoint-status |  |  | checkpoint | 1 - Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-status |  |  | checkpoint | 2 - Locate & fix into position
checkpoint-status |  |  | checkpoint | 3 - Install submains cabling as appropriate eg. Glands, tray, duct
checkpoint-status |  |  | checkpoint | 4 - Install lugs and terminate
checkpoint-status |  |  | checkpoint | 5 - Install sub circuit cabling and terminate. If circuit not complete at the other end, it must not be terminated.
checkpoint-status |  |  | checkpoint | 6 - Clean & vacuum
checkpoint-status |  |  | checkpoint | 7 - Record results
checkpoint-status |  |  | checkpoint | 8 - Organise inspection by inspector. Lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status |  |  | checkpoint | 9 - Clearly identify services
checkpoint-status |  |  | checkpoint | 10 - Energize
checkpoint-status |  |  | checkpoint | 11 - Check phase rotation
checkpoint-status |  |  | checkpoint | 12 - Check switchboard as installed matches shop drawing. If necessary modify shop drawing to match installed & return to office
checkpoint-status |  |  | checkpoint | 13 - Check typed schedule for accuracy and install in schedule holder
checkpoint-status |  |  | checkpoint | 14 - Clean switchboard cupboard
checklist-flat |  |  | checklist | ITP011 Data Installation and Fit Off |  |  |  |  | Yes | ITP011 Data Installation and Fit Off | 642b1e0d-134d-4ab9-9f19-29b8d9e079b0
checkpoint-status |  |  | checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint-status |  |  | checkpoint | 2 - Fit off and fix outlets, terminations have been checked and all terminations are correct and secure in all outlets
checkpoint-status |  |  | checkpoint | 3 - Outlets have all been secured in place and levelled
checkpoint-status |  |  | checkpoint | 4 - All cabling has been tested using the fluke data tester
checkpoint-status |  |  | checkpoint | 5 - Each cable has been correctly installed and terminated in the patch panel
checkpoint-status |  |  | checkpoint | 6 - Cover plates (if required)
checkpoint-status |  |  | checkpoint | 7 - Install label (if a specified requirement)
checkpoint-status |  |  | checkpoint | 8 - All outlets & appliances marked on the site as build’s
checklist-flat |  |  | checklist | Temp Board Install Checklist |  |  |  |  | Yes | Temp Board Install Checklist | 9d91da92-7526-4dc4-a4b4-7f9dbf1a1701
checkpoint-status |  |  | checkpoint | Are all final circuits protected by an RCD
checkpoint-status |  |  | checkpoint | Are all DB doors lockable
checkpoint-status |  |  | checkpoint | Are all DB’s securely fixed in position
checkpoint-status |  |  | checkpoint | Are all switchboards labelled correctly
checkpoint-status |  |  | checkpoint | Are all final circuits labelled at board
checkpoint-status |  |  | checkpoint | Are all live parts at DB inaccessible
checkpoint-status |  |  | checkpoint | Are socket outlets in DB in good working order
checkpoint-status |  |  | checkpoint | Are empty glands and holes covered over
checkpoint-status |  |  | checkpoint | Is switchboard door lockable, fitted with a retaining bar, and unable to be removed without the use of a tool
checkpoint-status |  |  | checkpoint | Is emergency lighting provided adjacent to switchboard
checkpoint-status |  |  | checkpoint | CCEW form been completed? (Take photo of each page)
checklist-flat |  |  | checklist | Test and Tag Register |  |  |  |  | Yes | Test and Tag Register | e46e2dad-2069-4ab8-b383-6b4b4711fad9
checkpoint-status |  |  | checkpoint | Test and Tag register completed (upload picture of each page)
checklist-flat |  |  | checklist | Temporary DB Monthly Testing |  |  |  |  | Yes | Temporary DB Monthly Testing | 91a17dcb-ec34-4d77-8c07-8c9ccb021759
checkpoint-status |  |  | checkpoint | Operating time of RCD’s (note trip times in comments)
checkpoint-status |  |  | checkpoint | RCD Push button Operation
checkpoint-status |  |  | checkpoint | General condition of DB (must include a photo)
checkpoint-status |  |  | checkpoint | Photo of completed tag on DB
checklist-flat |  |  | checklist | ITP019 Switchboard and Sub Main Terminations |  |  |  |  | Yes | ITP019 Switchboard and Sub Main Terminations | ecadcd74-5492-4622-8c3f-759e530157ac
checkpoint-status |  |  | checkpoint | What size lug is being used?
checkpoint-status |  |  | checkpoint | What size cable is being used?
checkpoint-status |  |  | checkpoint | What brand lug is being used?
checkpoint-status |  |  | checkpoint | Take picture of lug terminated on to cable
checkpoint-status |  |  | checkpoint | Is there a double nut or bevelled washer installed on all connections? Take picture
checkpoint-status |  |  | checkpoint | Cable has been tightened with a torque wrench set at the manufacturers advice – Take picture of wrench in confirmed settings
checkpoint-status |  |  | checkpoint | Has a termination mark/line been marked on each termination (used to make sure that connections have not moved on future visits) – Take picture
checklist-flat |  |  | checklist | ITP007 Lighting Wiring Rough In |  |  |  |  | Yes | ITP007 Lighting Wiring Rough In | d13b3368-1ff6-4521-bead-5420fbf1650b
checkpoint-status |  |  | checkpoint | 1 - Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint-status |  |  | checkpoint | 2 - Determine cable size
checkpoint-status |  |  | checkpoint | 3 - Cable sizes max length
checkpoint-status |  |  | checkpoint | 4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint-status |  |  | checkpoint | 5 - Install cable support system
checkpoint-status |  |  | checkpoint | 6 - Check cable size/type/colour
checkpoint-status |  |  | checkpoint | 7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint-status |  |  | checkpoint | 8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint-status |  |  | checkpoint | 9 - Fix cables to support system
checkpoint-status |  |  | checkpoint | 10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint-status |  |  | checkpoint | 11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint-status |  |  | checkpoint | 12 - All lighting points and switches have been wired as per drawings
checkpoint-status |  |  | checkpoint | 13 - All lighting points and switches have been marked on the site as built drawing
checkpoint-status |  |  | checkpoint | 14 - Height and location have been confirmed for each lighting points and switches
checklist-flat |  |  | checklist | ITP014 Distribution Board Test Results |  |  |  |  | Yes | ITP014 Distribution Board Test Results | 105bee61-93ed-4135-bdbb-65ddc403a5d6
checkpoint-status |  |  | checkpoint | Distribution Board Test Results - Complete and Test Sheet attached