## Table 1
ITP Inspection and Test Plan
Project Title: WDC Fluoridation | [5 empty] | Project No: CON23011 (internal #J2028) | [6 empty] | Procedure No:
Description of Activity: Ruddell’s Mechanical Installation | [12 empty] | ITP No.: 002
Location of Inspection / Testing: Ruddells WTP | [8 empty] | ITP Approved by (BCL) Name: | [6 empty] | Date:
ITP Prepared by Name: Moira Brady |  |  | Date: 25/01/2024 | [5 empty] | ITP Approved by (Client) Name: | [6 empty] | Date:
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  |  | Inspection Responsibility | [5 empty] | Verification Records of Inspection(s) / Test(s)
[14 empty] | BCL |  |  | Client | Date
2 | Documentation
2.1 | Construction Drawings |  |  | All drawings are for construction and latest revision. | [5 empty] | IFC drawings |  |  |  | I |  |  | S |  |  | Drawing Register
2.2 | Methodology |  |  | Approved construction plan & sequence drafted and briefed to all involved with activity prior to construction. Includes any isolation permits for tie ins. | [5 empty] | Workpack Approved |  |  |  | S |  |  | A |  |  | Approved Workpack Isolation Permit
3 | Manufacturing
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  |  | Inspection Responsibility | [5 empty] | Verification Records of Inspection(s) / Test(s)
[14 empty] | BCL |  |  | Client | Date
3.1 | Pipe & Pipe Fitting (Flanges, Elbows, Tees etc.) |  |  | Confirm pipe and pipe fitting materials are correct; material grade, size, rating etc. on delivery | [5 empty] | Pipe Data Sheet, Supplier Packing Slips |  |  |  | S |  |  | I |  |  | Supplier Packing Slips
3.2 | Nuts & Bolts |  |  | Confirm nuts and bolt materials are stainless steel grade 316 | [5 empty] | Supplier Packing Slips |  |  |  | S |  |  | I |  |  | Supplier Packing Slips
3.3 | Consumables |  |  | Confirm consumable materials are correct on delivery | [5 empty] | Supplier Packing Slips |  |  |  | S |  |  | A |  |  | Supplier Packing Slips
4 | Delivery, Storage & Handling
4.1 | Delivery |  |  | Check pipe materials, tanks, structural steel and dosing cabinets are undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery | [5 empty] | N/A |  |  |  | I |  |  | I |  |  | ITC-002
4.2 | Storage |  |  | For project entirety store materials in clean environment, protected from external damage; cover flange faces, store off ground using pallets. Ensure materials are free from contaminants and foreign debris. | [5 empty] | N/A |  |  |  | W |  |  | I |  |  | N/A
4.3 | Handling |  |  | Handle materials with care and with the correct equipment (gloves, slings etc.) | [5 empty] | N/A |  |  |  | I |  |  | I |  |  | N/A
5 | Site Installation
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  |  | Inspection Responsibility | [5 empty] | Verification Records of Inspection(s) / Test(s)
[14 empty] | BCL |  |  | Client | Date
5.1 | Install Pipe Supports |  |  | Install pipe supports in the correct locations before pipe installation | [5 empty] | As per pipe manufacturer specifications |  |  |  | I |  |  | I |  |  | Redline Drawings, ITC-02
5.2 | Equipment Set-Out |  |  | Survey and mark the correct locations of all pipes, tanks, structures and equipment before installation | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | Survey Record, Redline Drawings, ITC-02
5.3 | Install Pipework |  |  | Install piping on the pipe supports during construction | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | ITC-02
5.4 | Install Dose Tank |  |  | Install tank in correct location and orientation as specified in IFC mechanical layout drawings and tank manufacturers drawings | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | ITC-02
5.5 | Install Access Platform |  |  | Install access platforms in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | ITC-02
5.6 | Install Dosing Cabinet |  |  | Install cabinet in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | ITC-02
5.7 | Install Safety Shower |  |  | Install safety shower in correct location as specified in IFC mechanical layout drawings | [5 empty] | IFC Drawings |  |  |  | I |  |  | I |  |  | ITC-02
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  |  | Inspection Responsibility | [5 empty] | Verification Records of Inspection(s) / Test(s)
[14 empty] | BCL |  |  | Client | Date
5.8 | Install new nozzles into Existing Raw Water Pipework |  |  | Hot tap into Raw water pipework for new Flow Switch and Fluoride Dose point at correct locations | [5 empty] | IFC Drawings, Flow Switch O&M manual | [9 empty] | ITC-02
5.9 | Pressure Testing |  |  | All Fluoride dosing pipelines to be hydrotested 1.5 times the maximum working pressure for 15 minutes and inspected for leaks | [5 empty] | NZS 7643 |  |  |  | W |  |  | A |  |  | Pressure Test Records
6 | As-builts
6.1 | Redline Drawings |  |  | Redline P&ID Drawings and Mechanical Drawings Sets post construction | [5 empty] | N/A |  |  |  | S |  |  | A |  |  | Redline Drawings Issued
Revision Status of ITP | [6 empty] | Inspection Responsibility Legend | [10 empty] | Records Legend
Rev. No: |  | Revision 1: | Revision 2: |  |  | Revision 3: | A: |  | Approve |  | H: | Hold Point |  |  | T: | Test |  | ITR: Inspection and Test
Rev. Date: |  | 01 25/01/24 |  |  |  |  | D: I: |  | Document Inspection |  | R: S: | Random Submit |  |  | V: W: | Visual Witness |  | Report HPR: Hold Point Release form
Approved by: | [6 empty] | S.Con: |  | Subcontractor | [5 empty] | Cons: | Consultant
Signature Verification Record
Sign |  |  |  |  | Name |  |  | Position / Title | [10 empty] | Company