## Table 1
ITP Inspection and Test Plan Template
Project Title: WDC Fluoridation – Ruddells WTP | [5 empty] | Project No: J2028 (CON23011) | [7 empty] | Procedure No:
Description of Activity: Structural Steel | [13 empty] | ITP No.: 003
Location of Inspection / Testing: Millbridge Engineering/Site | [8 empty] | ITP Approved by (Bellcon) Name: Stephen A Date: 08/02/2024
ITP Prepared by Name: William Carlson Date: 30/01/2024 | [8 empty] | ITP Approved by (Client) Name: Whangarei District Council Date:
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [6 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL |  |  |  | Client | Date
1 | Documentation
1a | Construction Drawings |  |  | All drawings are for construction and latest revision. | [5 empty] | IFC Drawings |  |  | I |  |  |  | S |  |  | Drawing Register
1b | Shop Drawings |  |  | All drawings are for construction and latest revision. (hold Point) | [5 empty] | AISC Detailing for Steel Construction |  |  | H |  |  |  | A |  |  | Drawing Register
2 | Manufacturing
2a | Structural Steel |  |  | Confirm structural steel grade is correct | [5 empty] | Sec. 19 4.15.1.1 Table 1. Materials |  |  | D |  |  |  | R |  |  | Manufacturers Mill Certificates
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [6 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL |  |  |  | Client | Date
2b | Nuts, Bolts, & Washers |  |  | Confirm nuts, bolt and washer materials are hot dip galvanised Approved stainless steel components must be Grade A4 (Austenitic 316) strength 70 | [5 empty] | AS 1214 IFC Shop Drawings Bill of Materials |  |  | D |  |  |  | R |  |  | Manufacturers Mill Certificates
3 | Delivery, Storage & Handling
3a | Delivery |  |  | Check structural steel is undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery | [5 empty] | NZS 3404 |  |  | D |  |  |  | R |  |  | Delivery Dockets Photos
4 | Welding
4a | Nominate Inspector |  |  | Employ approved independent Welding Inspector. Submit two weeks before fabrication | [5 empty] | CBIP |  |  | S |  |  |  | A |  |  | N/A
4b | Welder Qualifications |  |  | Ensure welders are competent and accredited to carry out welding activity prior to construction. | [5 empty] | ASME IX |  |  | I |  |  |  | I |  |  | Welder Qualification Records
4c | Weld Procedure |  |  | Ensure procedure is Code compliant to weld specification of applicable work being done All welds to be category GP unless category SP nominated | [5 empty] | ASME IX |  |  | A |  |  |  | I |  |  | Welding Procedure
4d | Weld Inspection (Visual) |  |  | The extent of Non-Destructive examination listed in Sec. 19 4.15.2.4 | [5 empty] | ASME IX |  |  | I |  |  |  | I |  |  | Inspector report
5 | Corrosion Protection
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [6 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL |  |  |  | Client | Date
5a | Nominate Inspector |  |  | Employ approved independent Painting Inspector | [5 empty] | CBIP |  |  | D |  |  |  | R |  |  | N/A
5b | Preparation |  |  | Thoroughly clean all surfaces of oil and grease with turpentine, not kerosene. Visual Inspection | [5 empty] | Sa 21/2 in S1S 055900 |  |  | D |  |  |  | R |  |  | Galvanising QA Package
5c | Galvanising |  |  | Apply Zinc coating by hot dip process to give coating weight of not less than 600g/m2 | [5 empty] | AS/NZS 4680 |  |  | D |  |  |  | R |  |  | Galvanising QA Package
5d | Galvanising Inspection |  |  | Inspect for defects, misses, etc. Dry film thickness measurements and demonstration that film build up has been achieved | [5 empty] | AS3894 |  |  | D |  |  |  | R |  |  | Galvanising QA Package Painting Inspector Report
6 | Grouting
6a | Grouting Mix |  |  | 50MPa grout to be used, mixing as per the manufacturer spec | [5 empty] | NZS 3404 |  |  | D |  |  |  | R |  |  | Delivery docket
7 | As-builts
7a | Redline Drawings |  |  | Redline Structural Drawings Sets post construction | [5 empty] | N/A |  |  | D |  |  |  | R |  |  | As-Builts
Revision Status of ITP | [6 empty] | Inspection Responsibility Legend | [10 empty] | Records Legend
Rev. No: |  | Revision 1: | Revision 2: |  |  | Revision 3: | A: |  | Approve |  | H: | Hold Point |  |  | T: | Test |  | ITR: Inspection and Test
Rev. (ID No’s) | [6 empty] | D: |  | Document |  | R: | Random |  |  | V: | Visual |  | Report
Date: | [6 empty] | I: |  | Inspection |  | S: | Submit |  |  | W: | Witness |  | HPR: Hold Point Release form
Approved by: | [6 empty] | S.Con: |  | Subcontractor | [5 empty] | Cons: | Consultant
Signature Verification Record
Name |  |  |  |  | Signature |  |  | Position / Title | [10 empty] | Company