## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP 002 - Ruddells Mechanical Installation | itp |  |  |  |  | ITP 002 - Ruddells Mechanical Installation
section | 2.0 Documentation
checkpoint | 2.1 Construction Drawings
label | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
label | Acceptance Criteria - IFC drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - S
label | Verification Records of Inspection(s) / Test(s) - Drawing Register
checkpoint | 2.2 Methodology
label | Type of inspect / Test and Frequency - Approved construction plan & sequence drafted and briefed to all involved with activity prior to construction. Includes any isolation permits for tie ins.
label | Acceptance Criteria - Workpack Approved
label | Inspection Responsibility: BCL - S
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Approved Workpack Isolation Permit
section | 3.0 Manufacturing
checkpoint | 3.1 Pipe & Pipe Fitting (Flanges, Elbows, Tees etc.)
label | Type of inspect / Test and Frequency - Confirm pipe and pipe fitting materials are correct; material grade, size, rating etc. on delivery
label | Acceptance Criteria - Pipe Data Sheet, Supplier Packing Slips
label | Inspection Responsibility: BCL - S
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
checkpoint | 3.2 Nuts & Bolts
label | Type of inspect / Test and Frequency - Confirm nuts and bolt materials are stainless steel grade 316
label | Acceptance Criteria - Supplier Packing Slips
label | Inspection Responsibility: BCL - S
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
checkpoint | 3.3 Consumables
label | Type of inspect / Test and Frequency - Confirm consumable materials are correct on delivery
label | Acceptance Criteria - Supplier Packing Slips
label | Inspection Responsibility: BCL - S
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
section | 4.0 Delivery, Storage & Handling
checkpoint | 4.1 Delivery
label | Type of inspect / Test and Frequency - Check pipe materials, tanks, structural steel and dosing cabinets are undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery
label | Acceptance Criteria - N/A
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-002
checkpoint | 4.2 Storage
label | Type of inspect / Test and Frequency - For project entirety store materials in clean environment, protected from external damage; cover flange faces, store off ground using pallets. Ensure materials are free from contaminants and foreign debris.
label | Acceptance Criteria - N/A
label | Inspection Responsibility: BCL - W
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - N/A
checkpoint | 4.3 Handling
label | Type of inspect / Test and Frequency - Handle materials with care and with the correct equipment (gloves, slings etc.)
label | Acceptance Criteria - N/A
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - N/A
section | 5.0 Site Installation
checkpoint | 5.1 Install Pipe Supports
label | Type of inspect / Test and Frequency - Install pipe supports in the correct locations before pipe installation
label | Acceptance Criteria - As per pipe manufacturer specifications
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - Redline Drawings, ITC-02
checkpoint | 5.2 Equipment Set-Out
label | Type of inspect / Test and Frequency - Survey and mark the correct locations of all pipes, tanks, structures and equipment before installation
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings, ITC-02
checkpoint | 5.3 Install Pipework
label | Type of inspect / Test and Frequency - Install piping on the pipe supports during construction
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.4 Install Dose Tank
label | Type of inspect / Test and Frequency - Install tank in correct location and orientation as specified in IFC mechanical layout drawings and tank manufacturers drawings
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.5 Install Access Platform
label | Type of inspect / Test and Frequency - Install access platforms in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.6 Install Dosing Cabinet
label | Type of inspect / Test and Frequency - Install cabinet in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.7 Install Safety Shower
label | Type of inspect / Test and Frequency - Install safety shower in correct location as specified in IFC mechanical layout drawings
label | Acceptance Criteria - IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.8 Install new nozzles into Existing Raw Water Pipework
label | Type of inspect / Test and Frequency - Hot tap into Raw water pipework for new Flow Switch and Fluoride Dose point at correct locations
label | Acceptance Criteria - IFC Drawings, Flow Switch O&M manual
label | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint | 5.9 Pressure Testing
label | Type of inspect / Test and Frequency - All Fluoride dosing pipelines to be hydrotested 1.5 times the maximum working pressure for 15 minutes and inspected for leaks
label | Acceptance Criteria - NZS 7643
label | Inspection Responsibility: BCL - W
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Pressure Test Records
section | 6.0 As-builts
checkpoint | 6.1 Redline Drawings
label | Type of inspect / Test and Frequency - Redline P&ID Drawings and Mechanical Drawings Sets post construction
label | Acceptance Criteria - N/A
label | Inspection Responsibility: BCL - S
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Redline Drawings Issued