## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | 10985 KV Hills Kenmure Area 1-A |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561450 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9459 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 561450-DOW-ITP-X001 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Installation of Gravity Sewwer PVC pipes |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | Utilities |  |  |  |  | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | DCC code of subdivision and Project Specification |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | [5 empty] | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary |  | Date: | 2025-03-25 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Material Delivery | Inspect for damage and wear, Confirm items are correct size as per drawings and Specifications | -Pipes shall be DN150 SN16 PVC-U rubber ring jointed - Items are approved as per contract specification - DCC approved | Photos, delivery docket, | On Delivery | Visual | C | SP/QE
3.2 | Set out | Set out completed by an approved surveyor marked allignment | Allignment set out matches drawings or aggreed by the Engineer | Survey marks, photos | Prior to commencement of works | Survey | H | SV/QE/PE/CR
3.3
3.4
3.5
3.6

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Trench Excavation | - excavate to achieve required depth to invert as per drawings - Floor of trench to be even across width and length | - Allow 100mm for bedding | Photos, measurement checks | During Installation | Visual | C | SP/QE/CM
4.2 | Foundation | - Trench Floor Foundation to be checked it is suitable to support loads | - Foundation should avoid very soft clay, saturated soil, or fragmented rock | Photos | During Installation | Visual | H | SP/QE
4.3 | Install Pipe | - Pipe installed to grade as per design drawings | - Pipe not damaged during installation - pipe installed to grade within tolerances | Photos, Grade check sheet, Survey of position for as-built | During installation | Visual, Survey | C | SP/QE
4.4 | Laterals connections and installation | - Lateral connection as per drawing | - Lateral connection as per drawing and DCC standard details | Photos | Every Lateral | Visual, Survey | C | SP/QE
4.5 | Embedment zone | -Embedment material AP20 or approved by the Engineer in writing -where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate) | - min 100mm bedding - 100mm overlay | Photos | During Installation | Visual | C | SP/QE
4.6 | Backfill and Compact | - Backfill in 200mm layers of compacted material - Compaction testing one test every two layers as required - conductive signal strip to be laid at 300mm above pipe | 95% MDD in roads, paths, and pavements | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline or per straight section of pipeline | Visual, On Site test | H | SP/QE/CM
4.7 | Basecourse | - 200mm compacted layer of M440 | 98% MDD in roads | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline or per straight section of pipeline | Visual, On Site test | H | SP/QE/CM
Note on D8: Calisa McLeary: potential to add NDM testing requirements - 95% MDD in road

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Leak Testing | Completed pipelines including laterals to be tested in the presence of the Engineer or their Representative in accordance with AS/NZS 2566.2 Section 6.4 | Engineer Approval | Test Records | Every section of pipe completed | On-Site Test | H | SP/QE/CM/CR
5.2 | CCTV | CCTV inspection to confirm pipeline conforms with specification | Pipeline will fail is any of the following is visible: - pipe misalignment or deformation more than 5% of the pipe diameter - dips or ponding of water inside the pipe - defects such as open joints, potruding laterals, cracked barrels, or similar | Test Records, CCTV footage | Every section of pipe completed | On-Site Test | H | SP/QE/CM/CR
5.3
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: