## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | 10985 KV Hills Kenmure Area 1-A |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561450 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | DR | DCC Operations Rep
Contract Number: | 9459 |  |  |  |  | C | Check | CR | Contractors Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 561450-DOW-ITP-X004 |  | Version: | 01 |  | H | Hold Point | OP | Operations Manager
ITP Description: | [5 empty] | I | Inspection | PM | Project Manager
Discipline: | Utilities |  |  |  |  | M | Monitor on Random Basis | PE | Project Engineer
Specification: | DCC code of subdivision and Project Specification |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | [5 empty] | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary |  | Date: | 2025-03-25 |  | W | Witness Point | SV | Surveyor
Quality Specified: | ISO 9001, AS/NZS2566.2, (Schedule 18 Attachment C clause 3.1.4) | [6 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Material Delivery | Inspect for damage and wear, Confirm items are correct as per drawings and specifications | - Pipes shall be DN180 PE100 PN16 - material and fittings are approved as per contract specification | Photos,delivery docket, | On delivery | Visual | C | CR/IP
3.2 | Set out | Allignment set out as per design or as agreed with Engineer | Set out matches drawings or as agreed with the Engineer | Photos | Prior to commencement of works | Visual | C | CR/IP
3.3 | Service Locate | Mark out known existing services from service plans along alignment Pothole sevices and confirm design alignment | positive locate of services close to planned alignment Review and acceptance of any required changes due to services by Engineer | Photos | Prior to commencement of works | Hold Point | H | CR/IP
3.4
3.5
3.6
3.7
3.8
3.9
3.10

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Excavate Launch Pits | - Excavate to acheive required depth - Floor of trench to be even across width and length. | - Cover of 750mm for directional drilled watermains in all areas | Photos | During Installation | Visual | V | SP/CR
4.2 | Trench Excavation | - Excavate to acheive required depth to invert as per drawings. - Floor of trench to be even across width and length. | - Allow 100mm for bedding - Allow for minimum cover of 750mm for watermain - As shown on Drawings | Photos | During Installation | Visual | V | SP/CR
4.3 | Foundation | Material trench floor is inspected to ensure suitable | - Able to support loads - Free of very soft material or irregular or fragmented rock | Photos | During installation | Visual | V | SP/CR
4.4 | Pipe Installation | Pipes installed and positioned as per design | - Pipe not damaged during installation - Pipe is centrally located within trench - Pipe levels are within tolerance and according to the drawings | Photos, weld records (if required), Survey of position for asbuilt | During installation | Visual | V | SP/CR
4.5 | Embedment zone | Embedment material shall be AP20 or approved by the Engineer in writing | - min 100mm bedding - 150mm overlay | Photos | During Installation | Visual | V | SP/CR
4.6 | Backfill and Compact | - Backfill in 200mm layers of compacted material - Compaction testing one test every two layers as required - Conductive signal strip to be laid at 300mm above pipe | Passing compaction results - 95% MDD backfill - basecourse | Photos, compaction test results | During Installation, compaction testing per 50m of pipeline | Visual, On site test | H | SP/CR/IR
4.6 | Basecourse | - 200mm compacted layer of M440 | 98% MDD in roads | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline or per straight section of pipeline | Visual, On Site test | H | SP/QE/CM
4.7
4.8
4.9
4.10

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Pressure Testing (PE pipeline) | PE pipelines to be tested in accordance with specifications | Specification Attachment C, clause 4.7.5 No Thrust block failures, No visible leaks, Do not exceed make-up water limit | Test Records | Before commissioning | On-Site Test | H | CR/IP/DR
5.2 | Disinfection | Disinfection to be completed in accordance with specifications | Specification Attachment C, clause 4.12 | Test Records | Before commissioning | On-Site Test | H | CR/IP/DR
5.3
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: