## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | 10985 KV Hills Kenmure Area 1-A |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561450 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | DR | DCC Operations Rep
Contract Number: | 9459 |  |  |  |  | C | Check | CR | Contractors Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 561450-DOW-ITP-X006 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | [5 empty] | I | Inspection | PM | Project Manager
Discipline: | Utilities |  |  |  |  | M | Monitor on Random Basis | PE | Project Engineer
Specification: | [5 empty] | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | [5 empty] | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary |  | Date: | 2025-03-17 |  | W | Witness Point | SV | Surveyor
Quality Specified: | ISO 9001; AS/NZS4130; ISO 13954; PIPA POP 01 | [6 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Material delivery | - each pipe welding location check pipes to be welded - each EF fitting - check bags undamaged and sealed | - Pipes shall be DN180 PE100 PN16 - EF fittings correct size, SDR, PE100 and pressure rating. | - Photo of markings and labels on pipe. - Delivery docket/ packing slip - Scan bar code on fitting | On delivery | Visual | V | CR, IP
3.2 | Certification of welding equipment | Confirming just one EF welding machine in use during life of project. | Accepted by Client as suitable for use | Current calibration certificate/service record | Prior to commencement of works | Hold point | H | IP
3.3
3.4
3.5
3.6
3.7
3.8
3.9
3.10

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | PE Welding – Operator and Equipment | - Competency certificate of welder and certificate of fitness for welding equipment - Generator capacity adequate for the EF fittings. | Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory. | - Current welding certificates of operatives - Current calibration record of welding Equipment - Peel decohesion test results | During Installation | Inspection, Examine | I, E | CR, IP
4.2 | Test Sampling | - one pre-qualification per operator, one pilot weld per machine/per DN. | - Pass/Fail - ISO 13953 (Testing) | Peel decohesion test results from Kiwi Mechanical Ltd | - Every 20 welds per operator (or as requested by Client). - Test frequency to be reduced in response to consistent pass results, with Engineers approval. | Operation, Review | O, R | WS/CR, IP
4.3 | Weld Completion | - Weld completed to required standard and specification. - Only move strings after EF’s have cooled! | - Pass/Fail - PIPA POP001 version 8.1 2021 and POP014 - EF controller printout for all EF joints | - Power App or manual records - Data log from welding equipment - Photo Log | Each weld | Check, Dimension Inspection | C, D, R | WS/CR, IP
4.4
4.5
4.6
4.7
4.8
4.9
4.10

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Completion of QA | - Ensure QA package complete. | - all necessary documents including HDPE welding compiled and handed over to ER in completeness. | - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment. | Before practical completion | Inspection, Monitor on Random Basis | I, M | CR, IP
5.2
5.3
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: