## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561450-DOW-ITP-X001 Gravity Sewer | itp |  |  |  |  | 561450-DOW-ITP-X001 Gravity Sewer
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct size as per drawings and Specifications
label | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
label | ○ Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Photos, delivery docket,
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Survey
label | Inspection: Key - H
label | Inspection: By - SV/QE/PE/CR
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - excavate to achieve required depth to invert as per drawings
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Allow 100mm for bedding
label | Verifying Document - Photos, measurement checks
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP/QE/CM
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
label | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By - SP/QE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Install Pipe
label | Inspection Point: Quality Control Activity - Pipe installed to grade as per design drawings
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe installed to grade within tolerances
label | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual, Survey
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 4.4 - Laterals connections and installation
label | Inspection Point: Quality Control Activity - Lateral connection as per drawing
label | Acceptance Criteria - Lateral connection as per drawing and DCC standard details
label | Verifying Document - Photos
label | Frequency - Every Lateral
label | Inspection Type (Visual, other) - Visual, Survey
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 4.5 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
label | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
label | Acceptance Criteria - min 100mm bedding
label | ○ 100mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 4.6 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above pipe
label | Acceptance Criteria - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.7 - Basecourse
label | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
label | Acceptance Criteria - 98% MDD in roads
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
label | Inspection Point: Quality Control Activity - Completed pipelines including laterals to be tested in the presence of the Engineer or their Representative in accordance with AS/NZS 2566.2 Section 6.4
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - Test Records
label | Frequency - Every section of pipe completed
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - CCTV
label | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
label | Acceptance Criteria - Pipeline will fail is any of the following is visible:
label | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
label | ○ Dips or ponding of water inside the pipe
label | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
label | Verifying Document - Test Records, CCTV footage
label | Frequency - Every section of pipe completed
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM/CR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561450-DOW-ITP-X002 Installation of Manhole | itp |  |  |  |  | 561450-DOW-ITP-X002 Installation of Manhole
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification
label | ○ DCC approved
label | Verifying Document - Photos, delivery docket
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - - Allignment set out matches drawings or aggreed with the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Survey
label | Inspection: Key - H
label | Inspection: By - SV/SP/QE
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per drawings
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - - Allow 100mm for bedding
label | Verifying Document - Photos, measurement checks
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - SP/QE
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Trench Floor Foundation to be checked it is suitable to support loads
label | Acceptance Criteria - Foundation should avoid very soft clay, saturated soil, or fragmented rock
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By - SP/QE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - MH Installation
label | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
label | Acceptance Criteria - -Final levels are in accordance with the drawings or within tolerance and agreed with the Engineer
label | Verifying Document - Photos, As-built
label | Frequency - During installation
label | Inspection Type (Visual, other) - Survey
label | Inspection: Key - H
label | Inspection: By - SP/QE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Benching
label | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
label | ○ Benching shape to have smooth transitions at bends and junctions
label | Acceptance Criteria - - Benching built up to the specifications
label | Verifying Document - Photos
label | Frequency - During benching contruction
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By - SP/QE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.5 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | Acceptance Criteria - - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Basecourse
label | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
label | Acceptance Criteria - 98% MDD in roads
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
label | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
label | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
label | Verifying Document - Photos, test records
label | Frequency - For every manhole
label | Inspection Type (Visual, other) - Test, visual
label | Inspection: Key - H
label | Inspection: By - SP/QE/PE/CR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561450-DOW-ITP-X003 Watermain (Trenched) | itp |  |  |  |  | 561450-DOW-ITP-X003 Watermain (Trenched)
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
label | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
label | ○ Material and fittings are approved as per contract specification
label | Verifying Document - Photos,delivery docket
label | Frequency - On delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - CR/IP
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
label | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
label | Verifying Document - Photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - CR/IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings
label | ○ Floor of trench to be even across width and length.
label | Acceptance Criteria - Allow 100mm for bedding
label | ○ Allow for minimum cover of 750mm.
label | ○ As shown on Drawings
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
label | Acceptance Criteria - Able to support loads
label | ○ Free of very soft material or irregular or fragmented rock
label | Verifying Document - Photos
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.3 - Pipe Installation
label | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe is centrally located within trench
label | ○ Pipe levels are within tolerance and according to the drawings
label | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.4 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
label | Acceptance Criteria - min 100mm bedding
label | ○ 150mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.5 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above pipe
label | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
label | Verifying Document - Photos, compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
label | Inspection: By - SP/CR/IR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Basecourse
label | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
label | Acceptance Criteria - 98% MDD in roads
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pressure Testing (PE pipeline)
label | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
label | Acceptance Criteria - Specification Attachment C, clause 4.7.5
label | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - CR/IP/DR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Disinfection
label | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
label | Acceptance Criteria - Specification Attachment C, clause 4.12
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - CR/IP/DR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561450-DOW-ITP-X004 Watermain (Directional Drill) | itp |  |  |  |  | 561450-DOW-ITP-X004 Watermain (Directional Drill)
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
label | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
label | ○ Material and fittings are approved as per contract specification
label | Verifying Document - Photos,delivery docket,
label | Frequency - On delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - CR/IP
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
label | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
label | Verifying Document - Photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - CR/IP
checkpoint | 3.3 - Service Locate
label | Inspection Point: Quality Control Activity - Mark out known existing services from service plans along alignment
label | ○ Pothole sevices and confirm design alignment
label | Acceptance Criteria - Positive locate of services close to planned alignment
label | ○ Review and acceptance of any required changes due to services by Engineer
label | Verifying Document - Photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Hold Point
label | Inspection: Key - H
label | Inspection: By - CR/IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Excavate Launch Pits
label | Inspection Point: Quality Control Activity - Excavate to acheive required depth
label | ○ Floor of trench to be even across width and length.
label | Acceptance Criteria - Cover of 750mm for directional drilled watermains in all areas
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.2 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings.
label | ○ Floor of trench to be even across width and length.
label | Acceptance Criteria - Allow 100mm for bedding
label | ○ Allow for minimum cover of 750mm for watermain
label | ○ As shown on Drawings
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.3 - Foundation
label | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
label | Acceptance Criteria - Able to support loads
label | ○ Free of very soft material or irregular or fragmented rock
label | Verifying Document - Photos
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.4 - Pipe Installation
label | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe is centrally located within trench
label | ○ Pipe levels are within tolerance and according to the drawings
label | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.5 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
label | Acceptance Criteria - min 100mm bedding
label | ○ 150mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - SP/CR
checkpoint | 4.6 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above pipe
label | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
label | Verifying Document - Photos, compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
label | Inspection: By - SP/CR/IR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.6 - Basecourse
label | Inspection Point: Quality Control Activity - 200mm compacted layer of M440
label | Acceptance Criteria - 98% MDD in roads
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
label | Inspection: By - SP/QE/CM
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pressure Testing (PE pipeline)
label | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
label | Acceptance Criteria - Specification Attachment C, clause 4.7.5
label | ○ No Thrust block failures, No visible leaks, Do not exceed make-up water limit
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - CR/IP/DR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Disinfection
label | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
label | Acceptance Criteria - Specification Attachment C, clause 4.12
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
label | Inspection: By - CR/IP/DR
holdpoint | AUTHORITY HOLDPOINT
checklist | 561450-DOW-ITP-X005 Butt Welding | itp |  |  |  |  | 561450-DOW-ITP-X005 Butt Welding
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
label | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
label | ○ Material and fittings are approved as per contract specification
label | Verifying Document - Photo of pipe bundle(s) showing pipe classification.
label | ○ Delivery docket/packing slip
label | Frequency - On delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - CR, IP
checkpoint | 3.2 - Certification of welding equipment
label | Inspection Point: Quality Control Activity - Confirming just one butt welding machine in use during life of project.
label | Acceptance Criteria - Accepted by Client as suitable for use
label | Verifying Document - Current calibration certificate/service record
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Hold point
label | Inspection: Key - H
label | Inspection: By - IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - PE Welding – Operator and Equipment
label | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
label | Acceptance Criteria - Testing of weld samples carried out by an IANZ accredited laboratory.
label | Verifying Document - Current welding certificates of operatives
label | ○ Current calibration record of welding Equipment
label | ○ Tensile test results
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Inspection, Examine
label | Inspection: Key - I, E
label | Inspection: By - CR, IR
checkpoint | 4.2 - Test Sampling
label | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
label | ○ Test failures will require the previous weld and the following weld to be tested and passed.
label | Acceptance Criteria - Pass/Fail
label | ○ ISO 21307
label | ○ ISO 13953 (Testing)
label | Verifying Document - Tensile test results from Kiwi Mechanical Ltd
label | Frequency - Every 50 welds per operator (or as requested by Client).
label | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
label | Inspection Type (Visual, other) - Operation
label | Inspection: Key - O, R
label | Inspection: By - WS/CR, IR
checkpoint | 4.3 - Weld Completion
label | Inspection Point: Quality Control Activity - Weld completed to required standard and specification
label | Acceptance Criteria - Pass/Fail
label | ○ ISO 21307
label | Verifying Document - Power App or manual records
label | ○ Data log from welding equipment
label | ○ Photo Log
label | Frequency - Each weld
label | Inspection Type (Visual, other) - Check, Dimension Inspection
label | Inspection: Key - C, D, R
label | Inspection: By - WS, CR, IR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Completion of QA
label | Inspection Point: Quality Control Activity - Ensure QA package complete.
label | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
label | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
label | ○ EF controller printout for all EF joints
label | Frequency - Before practical completion
label | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
label | Inspection: Key - I, M
label | Inspection: By - CR, IP
checklist | 561450-DOW-ITP-X006 EF Welding | itp |  |  |  |  | 561450-DOW-ITP-X006 EF Welding
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Material delivery
label | Inspection Point: Quality Control Activity - Each pipe welding location check pipes to be welded
label | ○ Each EF fitting
label | ○ Check bags undamaged and sealed
label | Acceptance Criteria - Pipes shall be DN180 PE100 PN16
label | ○ EF fittings correct size, SDR, PE100 and pressure rating.
label | Verifying Document - Photo of markings and labels on pipe.
label | ○ Delivery docket/ packing slip
label | ○ Scan bar code on fitting
label | Frequency - On delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
label | Inspection: By - CR, IP
checkpoint | 3.2 - Certification of welding equipment
label | Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project.
label | Acceptance Criteria - Accepted by Client as suitable for use
label | Verifying Document - Current calibration certificate/service record
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Hold point
label | Inspection: Key - H
label | Inspection: By - IP
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - PE Welding – Operator and Equipment
label | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
label | ○ Generator capacity adequate for the EF fittings.
label | Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory.
label | Verifying Document - Current welding certificates of operatives
label | ○ Current calibration record of welding Equipment
label | ○ Peel decohesion test results
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Inspection, Examine
label | Inspection: Key - I, E
label | Inspection: By - CR, IP
checkpoint | 4.2 - Test Sampling
label | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
label | Acceptance Criteria - Pass/Fail
label | ○ ISO 13953 (Testing)
label | Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd
label | Frequency - Every 20 welds per operator (or as requested by Client).
label | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
label | Inspection Type (Visual, other) - Operation, Review
label | Inspection: Key - O, R
label | Inspection: By - WS/CR, IP
checkpoint | 4.3 - Weld Completion
label | Inspection Point: Quality Control Activity - Weld completed to required standard and specification.
label | ○ Only move strings after EF’s have cooled!
label | Acceptance Criteria - Pass/Fail
label | ○ PIPA POP001 version 8.1 2021 and POP014
label | ○ EF controller printout for all EF joints
label | Verifying Document - Power App or manual records
label | ○ Data log from welding equipment
label | ○ Photo Log
label | Frequency - Each weld
label | Inspection Type (Visual, other) - Check, Dimension Inspection
label | Inspection: Key - C, D, R
label | Inspection: By - WS/CR, IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Completion of QA
label | Inspection Point: Quality Control Activity - Ensure QA package complete.
label | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
label | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
label | Frequency - Before practical completion
label | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
label | Inspection: Key - I, M
label | Inspection: By - CR, IP