## Sheet1
3.1 | Material delivery | - each pipe welding location check pipes to be welded - each EF fitting - check bags undamaged and sealed | - Pipes shall be DN180 PE100 PN16 - EF fittings correct size, SDR, PE100 and pressure rating. | - Photo of markings and labels on pipe. - Delivery docket/ packing slip - Scan bar code on fitting | On delivery | Visual | V | CR, IP | 3.1 - Material delivery | Inspection Point: Quality Control Activity - - each pipe welding location check pipes to be welded - each EF fitting - check bags undamaged and sealed | Acceptance Criteria - - Pipes shall be DN180 PE100 PN16 - EF fittings correct size, SDR, PE100 and pressure rating. | Verifying Document - - Photo of markings and labels on pipe. - Delivery docket/ packing slip - Scan bar code on fitting | Frequency - On delivery | Inspection Type (Visual, other) - Visual | Inspection: Key - V | Inspection: By - CR, IP | 3.1 - Material delivery
3.2 | Certification of welding equipment | Confirming just one EF welding machine in use during life of project. | Accepted by Client as suitable for use | Current calibration certificate/service record | Prior to commencement of works | Hold point | H | IP | 3.2 - Certification of welding equipment | Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project. | Acceptance Criteria - Accepted by Client as suitable for use | Verifying Document - Current calibration certificate/service record | Frequency - Prior to commencement of works | Inspection Type (Visual, other) - Hold point | Inspection: Key - H | Inspection: By - IP | Inspection Point: Quality Control Activity - - each pipe welding location check pipes to be welded - each EF fitting - check bags undamaged and sealed
4.1 | PE Welding – Operator and Equipment | - Competency certificate of welder and certificate of fitness for welding equipment - Generator capacity adequate for the EF fittings. | Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory. | - Current welding certificates of operatives - Current calibration record of welding Equipment - Peel decohesion test results | During Installation | Inspection, Examine | I, E | CR, IP | 4.1 - PE Welding – Operator and Equipment | Inspection Point: Quality Control Activity - - Competency certificate of welder and certificate of fitness for welding equipment - Generator capacity adequate for the EF fittings. | Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory. | Verifying Document - - Current welding certificates of operatives - Current calibration record of welding Equipment - Peel decohesion test results | Frequency - During Installation | Inspection Type (Visual, other) - Inspection, Examine | Inspection: Key - I, E | Inspection: By - CR, IP | Acceptance Criteria - - Pipes shall be DN180 PE100 PN16 - EF fittings correct size, SDR, PE100 and pressure rating.
4.2 | Test Sampling | one pre-qualification per operator, one pilot weld per machine/per DN. | - Pass/Fail - ISO 13953 (Testing) | Peel decohesion test results from Kiwi Mechanical Ltd | - Every 20 welds per operator (or as requested by Client). - Test frequency to be reduced in response to consistent pass results, with Engineers approval. | Operation, Review | O, R | WS/CR, IP | 4.2 - Test Sampling | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN. | Acceptance Criteria - - Pass/Fail - ISO 13953 (Testing) | Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd | Frequency - - Every 20 welds per operator (or as requested by Client). - Test frequency to be reduced in response to consistent pass results, with Engineers approval. | Inspection Type (Visual, other) - Operation, Review | Inspection: Key - O, R | Inspection: By - WS/CR, IP | Verifying Document - - Photo of markings and labels on pipe. - Delivery docket/ packing slip - Scan bar code on fitting
4.3 | Weld Completion | - Weld completed to required standard and specification. - Only move strings after EF’s have cooled! | - Pass/Fail - PIPA POP001 version 8.1 2021 and POP014 - EF controller printout for all EF joints | - Power App or manual records - Data log from welding equipment - Photo Log | Each weld | Check, Dimension Inspection | C, D, R | WS/CR, IP | 4.3 - Weld Completion | Inspection Point: Quality Control Activity - - Weld completed to required standard and specification. - Only move strings after EF’s have cooled! | Acceptance Criteria - - Pass/Fail - PIPA POP001 version 8.1 2021 and POP014 - EF controller printout for all EF joints | Verifying Document - - Power App or manual records - Data log from welding equipment - Photo Log | Frequency - Each weld | Inspection Type (Visual, other) - Check, Dimension Inspection | Inspection: Key - C, D, R | Inspection: By - WS/CR, IP | Frequency - On delivery
5.1 | Completion of QA | Ensure QA package complete. | - all necessary documents including HDPE welding compiled and handed over to ER in completeness. | - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment. | Before practical completion | Inspection, Monitor on Random Basis | I, M | CR, IP | 5.1 - Completion of QA | Inspection Point: Quality Control Activity - Ensure QA package complete. | Acceptance Criteria - - all necessary documents including HDPE welding compiled and handed over to ER in completeness. | Verifying Document - - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment. | Frequency - Before practical completion | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis | Inspection: Key - I, M | Inspection: By - CR, IP | Inspection Type (Visual, other) - Visual
Inspection: Key - V
Inspection: By - CR, IP
3.2 - Certification of welding equipment
Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project.
Acceptance Criteria - Accepted by Client as suitable for use
Verifying Document - Current calibration certificate/service record
Frequency - Prior to commencement of works
Inspection Type (Visual, other) - Hold point
Inspection: Key - H
Inspection: By - IP
4.1 - PE Welding – Operator and Equipment
Inspection Point: Quality Control Activity - - Competency certificate of welder and certificate of fitness for welding equipment - Generator capacity adequate for the EF fittings.
Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory.
Verifying Document - - Current welding certificates of operatives - Current calibration record of welding Equipment - Peel decohesion test results
Frequency - During Installation
Inspection Type (Visual, other) - Inspection, Examine
Inspection: Key - I, E
Inspection: By - CR, IP
4.2 - Test Sampling
Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
Acceptance Criteria - - Pass/Fail - ISO 13953 (Testing)
Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd
Frequency - - Every 20 welds per operator (or as requested by Client). - Test frequency to be reduced in response to consistent pass results, with Engineers approval.
Inspection Type (Visual, other) - Operation, Review
Inspection: Key - O, R
Inspection: By - WS/CR, IP
4.3 - Weld Completion
Inspection Point: Quality Control Activity - - Weld completed to required standard and specification. - Only move strings after EF’s have cooled!
Acceptance Criteria - - Pass/Fail - PIPA POP001 version 8.1 2021 and POP014 - EF controller printout for all EF joints
Verifying Document - - Power App or manual records - Data log from welding equipment - Photo Log
Frequency - Each weld
Inspection Type (Visual, other) - Check, Dimension Inspection
Inspection: Key - C, D, R
Inspection: By - WS/CR, IP
5.1 - Completion of QA
Inspection Point: Quality Control Activity - Ensure QA package complete.
Acceptance Criteria - - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
Verifying Document - - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
Frequency - Before practical completion
Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
Inspection: Key - I, M
Inspection: By - CR, IP