## Master List Templates
Id | Type | Name | Values | Prompting Name
60f5486b-f744-5d27-b8fb-e1e5f7108955 | checklist | Add Site Diary Checklist |  | Site Diary
bf78f897-fea7-5cd1-8800-293868168998 | checkpoint | Areas of work accessible for the day
e048d81c-b120-5201-90b9-737dc818e2c4 | dropdown | Day | Friday, Saturday, Sunday, Thursday, Tuesday, Wednesday,Monday
8b06ec40-8a3c-5890-8eef-2138d0007662 | textbox | Date
220bbcf8-26f5-50d0-8333-a92a92c45817 | textbox | Year
2ee2d4ff-2e7a-5a32-abbd-16864834758c | textbox | Number of workers on site
f718a78d-8c75-581f-8ecc-f206357c4ca1 | textbox | HSR on site today enter name
67e1eae6-6cc5-54f1-9e71-af2e0d4466a4 | textbox | First Aider on site today enter name
300a822f-3c8d-5eb4-ace2-997e233cf07a | textbox | Injury on site today enter name
01f1b588-929d-53f2-aad3-d4b5cd7ea92b | checkpoint | Work area 1 details entered
47c51389-20da-5ede-8014-b3d862ef3eaa | textbox | Area
be2d3209-4753-5610-ab16-ae8739025b3a | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
8e3893b8-ed2f-5026-a09c-93c5cb077f2f | textbox | Comments
08b81b9f-23d8-52c9-a8ca-eac43bb9ea69 | checkpoint-no-value | Work area 2 details entered
c3bf60c1-b562-5b80-a516-8f9ebd4704ed | textbox | Area
4be3a27e-4b3d-586a-b513-ceb15fc40bfe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
c2b720eb-8138-59ab-8725-672f980b9236 | textbox | Comments
d36229fe-bf34-5147-bb14-ad0c6625023d | checkpoint-no-value | Work area 3 details entered
67ba33fd-a2e8-519a-9718-9602c1c22c34 | textbox | Area
d67e8a5c-0701-5122-8469-a3f875979c90 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
e0c6f448-ea66-5571-ab37-d4e5b00d7eba | textbox | Comments
80a68090-6901-508a-bb51-839019e42ad5 | checkpoint-no-value | Work area 4 details entered
a65ca3a0-57ef-5fca-9a21-6c58979e77b1 | textbox | Area
228c593c-8c7b-556a-a358-a302692731ee | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
be73872c-40d0-5fe1-95e7-28fc71abd66b | textbox | Comments
104410fe-70a4-5c51-80ba-e83f3c874291 | checkpoint-no-value | Work area 5 details entered
5c62749c-d156-5f1a-a0db-c1bfbf345bbe | textbox | Area
fb2b9525-bedc-5e79-8595-7d9e44168dbe | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0f36562c-85d2-5c15-b10e-0e0351ca42a0 | textbox | Comments
6f677beb-e344-5d16-baa9-7fe0f3ae1253 | checkpoint-no-value | Work area 6 details entered
df45fc36-050d-52a7-b4de-4c3dfd8b7dc1 | textbox | Area
ce639f3d-bbb2-5e33-bfa7-831d0f7f3ce4 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
7a39984c-f43a-5db8-bbb8-67cb3b46d3ad | textbox | Comments
4284857c-6f64-58f3-8927-ba5ab4118ca5 | checkpoint-no-value | Work area 7 details entered
f56b01be-ce67-517e-9201-21fbb9da80c2 | textbox | Area
cd1edc93-5190-52b7-8b91-cd4940a807f6 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
0ce609f8-0e23-570c-84bf-8d4ab1c5a902 | textbox | Other
b9a615da-cbe6-5d4c-be7c-01ad213f34d8 | checkpoint-no-value | Work area 8 details entered
87fec433-1b39-5b0c-85ab-47b3724894e7 | textbox | Area
497f30d6-7d3e-567a-9fde-26ab4d0ca912 | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
64afa6dd-5e29-541b-8f7a-b3eefebb69ef | textbox | Comments
7d6b1c3f-bf2b-5380-b63b-7ed9566a0d11 | checkpoint-no-value | Weather conditions entered
e4a9dd83-8a46-5d40-9016-ecdf1143b19f | dropdown | Conditions: | Hot, Overcast, Rain, Showers, Windy,Fine
c4eca12e-6581-575e-a282-008a28f85230 | textbox | Min temp predicted
9f6d3c08-4655-5cb2-a2ec-d500dc6aaf2c | textbox | Max temp predicted
5b3f52a8-b761-5f61-933f-a47148ab9fb7 | checkpoint-no-value | Delays from inclemency
f4baf749-c7b9-5264-82f9-225bad01bac5 | textbox | Total Hours of delay
c7cb66ed-53d5-5a5a-8876-a70cef304006 | dropdown | Conditions: | , Heat, Other trades, Windy,Rain
5b80d7d4-4a1c-5832-8683-847c7af64ab9 | checkpoint-no-value | Delays from Builders or Others
afcd53cc-c4ba-599f-8ce0-c3160cb74e57 | textbox | Total Hours of delay
c19fccf4-46f7-5cda-af3d-ffd8ba800343 | dropdown | Conditions: | Concreter, Crane, Earthworks, Other, PT, Safety, Scaffold, Steel fixer, Union,Builder
df62053a-68f1-5a9a-9162-77035b5d14a0 | checkpoint | Attach Specific site photos for respective day
6127f1dc-4f1e-4792-a980-9c46997559ef | checklist | Additional Tasks - add as required |  | Additional Tasks - add as required
99437fe9-c39f-53b1-9358-61d182ae2111 | checkpoint | Details of additional tasks - comment below
572b08b0-6ae6-5f16-81e4-2c167c64c8af | checklist | Additional Tasks Checklist |  | Additional Tasks Checklist
99437fe9-c39f-53b1-9358-61d182ae2111 | checkpoint | Details of additional tasks - comment below
6cac0869-3cda-508d-b9cb-4651e4731164 | checklist | Daysheets (Labour & Materials) (V.180521) |  | Daysheets (Labour & Materials)
4bce506c-bcdf-576c-b16b-6de3c5e3143d | checkpoint | Daysheet Completed & Ready for Invoicing
931dd1e9-e6f7-5970-96bc-c5fb9280165b | textbox | Date
3bff79c6-0816-52cd-9e1f-63cee682347c | textbox | Project
fadd42ae-e4b2-55ca-840e-a83ee3ddce8b | textbox | Location
a3f6da3f-5df2-56d2-b92e-0f3d0d2589e6 | textbox | Workers Name (Add hours in brackets)
6d361e0f-2263-54e3-b3ca-3bda46ad2f47 | textbox | Material 1 (Quantity & Description)
e983444b-af8c-5726-bee7-c484318a6209 | textbox | Material 2 (Quantity & Description)
d7bdc89c-6dca-5cc2-8bf8-22fc1c0e86b9 | textbox | Material 3 (Quantity & Description)
509caee7-e268-5f5d-ad4b-0812134a7dcd | textbox | Material 4 (Quantity & Description)
6e9d09c8-8a97-5a17-9cdf-0c0915621169 | textbox | Material 5 (Quantity & Description)
c20aadcd-5e8c-5e28-a24b-24f5efd5259f | button | Reviewed by Leemark Supervisor | No,Yes
44ff8f03-db9b-5a6b-ace2-12ab20bcdcb2 | tickbox | Signature of Builder's Supervisor Added
6435f32c-7cd0-5652-bb67-410fc08c8aae | signoff | Signature Added - Click Here
8f1df2a9-920c-50cd-bd21-5f261f2893fd | checklist | Defect / Issue to be rectified |  | ADD new defect / issue to be rectified [RENAME CHECKLIST TO LOCATION & DETAILS OF DEFECT]
1ce33f58-bceb-5bb5-b5a7-61ac5e21fa4d | checkpoint | Upload photo of defect / issue to be rectified. Add comments if necessary.
97acd7e5-f320-523a-9616-f769c9258094 | checkpoint | Has issue been rectified / defect been closed out? Upload photo
bab1d5a9-a3d7-58ff-a01f-4224a18aac6b | note | Only PASS once issue is rectified / defect is closed out
64c98d5d-ff41-4d76-b1f0-386f45007bc5 | checklist | LM-FOR-50-ITR-402 Fire Detection Commissioning |  | LM-FOR-50-ITR-402 Fire Detection Commissioning
2be0308f-a17d-456f-b74c-5608b18f68b8 | section | Preliminary
7005b448-5149-49fe-b4e3-df8f98ddce68 | checkpoint | Confirm the corresponding ITR - Fire Detection and Alarm System Installation is complete
0c0960d1-1dda-478d-a8c7-650e18d7f196 | checkpoint | Confirm that the test equipment’s are calibrated.
cfd90734-c1a3-41e1-8f74-d8f2b8e01a4e | section | Commissioning
98d695b0-564a-4c4b-8893-290171415c81 | checkpoint | Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation and power supply requirement in accordance with AS 1670.1:2018 section 3.16 power supply equipment (PSE).
58ec0c41-5144-4cd7-84fe-2a59483eab90 | checkpoint | Spray the aerosol directly at the smoke detector until the detector activates. Observe the FIP for the activation of an alarm signal and verify the device ID displayed on the panel.
186374a5-67fd-438a-988f-244e9152cc5f | checkpoint | Position the testing kit over the heat detector and apply heat until the detector activates. Observe the FIP for the activation of an alarm signal and verify the device ID displayed on the panel.
60741f53-e59e-4473-97d9-a34594ebff93 | checkpoint | Activate the manual call point by pressing or breaking the glass. Observe the FIP for the activation of an alarm signal and verify the device ID displayed on the panel.
360c7376-3417-4faf-bccd-45e9f977a15b | checkpoint | Activate the input device to activate the I/O module. Observe the FIP for the activation of the I/O signal and verify the device ID displayed on the panel. Confirm that the I/O output devices activate as programmed during alarm event.
865e62c6-8e6f-4c44-bbee-d109cdaef046 | checkpoint | Introduce smoke from a smoke pen near the sampling point of the aspirating smoke detector and verify activation of the alarm at the FIP. Observe the FIP for the activation of an alarm signals and verify the device ID displayed on the panel.
f42376e7-0dd7-4691-b4d2-60466ed4ff93 | checkpoint | Verify activation of all water flow switches. Close the outlet isolation valve associated with the water flow switch. Open the drain valve slowly to simulate a drop in pressure. Observe the water flow switch for activation. Ensure that the flow switch sends a signal to the FIP. Duration: Until the alarm is triggered.
d4bc32c1-569f-429b-a1d1-d12c4f475776 | checkpoint | Verify the EWIS system is activated upon alarm activation.
6d383632-753b-4751-9b89-75ac2e602aa6 | checkpoint | Open and short signalling line circuits and verify that the fault signal actuates. Observe the FIP for the activation of a fault signal and verify the device ID displayed on the panel.
db1a7b45-88a5-4326-907e-b52fe1bda474 | checkpoint | Ground all circuits and verify response of trouble signals at the FIP.
1ae0c8ef-1374-46f4-b2a1-b26a0ce3465e | checkpoint | Confirm all addressable devices are associated with the fire indicator panel are commissioned and functioning correctly in accordance with the cause-and-effect matrix
8ed3ef31-3d6d-4cb1-8a10-a08cd80b53c3 | checkpoint | Confirm that all ancillary equipment connected to the input / output module blocks have been commissioned and functioning correctly in accordance with the cause-and-effect matrix.
793482c6-0d57-4c3c-b896-004c77e56660 | section | Completion
9fc3cfcd-f7e6-4308-8101-50c0dfc7ca7c | checkpoint | Visually inspect equipment for damage and cleanliness.
68705264-22e1-4059-8d94-5068fd3509be | checkpoint | Confirm all labelling is correct as per IFC design.
010e2b62-6761-4de9-94d7-eff4a4730a90 | checkpoint | AS-installed drawings covering the whole system complete as per AS1670.1: 2018.
0e7a762d-c7e3-4b43-ae2f-167bdc6a6dd5 | checkpoint | Provide Installer’s Statement in accordance with AS1670.1: 2018 Appendix F.
cde13296-b42d-43f7-9505-af9db3e48218 | checkpoint | Provide Commissioning Statement in accordance with AS1670.1: 2018 Appendix G.
37f52d3b-1e22-44c3-9175-20bfda7df54b | checkpoint | All baseline Data has been recorded as per AS1670.1: 2018.
188a7306-5904-4674-ad02-b96649a75d85 | checkpoint | Confirm all covers and settings are returned to service state on completion of checks.
4cce9465-82b4-4a56-81ed-7638d750b806 | section | Verification & Sign off Acceptance
ea84da2d-a605-475d-9a86-1780d4fe8bab | checkpoint | Completed By (Contractor)
9fa434d6-3aed-44f5-9461-9b02cc5d8eaa | signoff | Signature
82b4be12-b39c-4b3d-bc57-83763a81b27d | checkpoint | Reviewed By (Contractor Supervisor)
6bcc14eb-a2d8-4484-9ee1-6f7523dea1f1 | signoff | Signature
2f8bccc0-3d22-44aa-aece-ad5442236984 | checkpoint | Reviewed By (client/Consultant)
185e9f7a-2afe-4527-a815-c47a6a1b2c5b | signoff | Signature
ef2e7854-a324-4773-aaad-bbadf2ba8eba | checklist | LM-FOR-50-ITR-403 EWIS Commissioning |  | LM-FOR-50-ITR-403 EWIS Commissioning
d0591313-e557-4698-a7df-95b33278ed34 | section | Preliminary
727c1f7f-292d-4dc7-a650-eaa58ab6d5bc | checkpoint | Confirm the corresponding ITR - Emergency warning and intercom Installation is complete
5639f4e8-1075-4d04-b857-fe36a83b8a9e | checkpoint | Confirm that the test equipment’s are calibrated.
25eb88b1-470c-4b6b-bb72-8f039cff7b4a | section | Commissioning
24f5e7ad-0519-4d1a-93ab-d76ab92d3c30 | checkpoint | Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation and power supply requirement in accordance with AS 1670.4:2018 section 3.5 power supply equipment (PSE).
bfb0a585-f414-401e-a299-5fee07f4ef89 | checkpoint | Verify all the ceiling/surface mounted speakers and horn speakers been tapped to the correct setting in line with amplifier rating.
3b36b444-b0a3-41b1-b8c1-4f2cc60c8795 | checkpoint | Verify the SPL within the zone by triggering the alarm signal (either manually or automatically) and measuring the sound levels using a calibrated sound level meter at various points in the zone. The minimum SPL shall exceed by a least 10 dB the ambient sound pressure level but shall not be less than 75 dB(A). The maximum SPL shall not exceed 105 dB(A) throughout the emergency zone.
d05d9f0b-b1ca-4c56-ae3c-38d40a78411f | checkpoint | Ensure all visual warnings are installed and operational.
abcfc7e2-a4cb-4aaf-b4c6-442128b24b79 | checkpoint | Verify interface/integration between the EWIS system and FIP is complete and operational.
1a3e375c-971b-4af8-a5c3-b0f5c954f81e | checkpoint | Verify the functionality and audio quality check for each intercom handset.
2a2ee188-47bd-4fce-8612-a91190e27e66 | checkpoint | Simulate an EOLR fault by temporarily removing or disconnecting the resistor to check if the control panel detects and signals the fault condition.
72677cf3-801b-449b-b2c7-8003383e8f9e | checkpoint | Create a short circuit for each speaker line at the last speaker and confirm fault at the control panel.
a87bbccf-1c0e-4e91-9017-b366b3c36443 | checkpoint | Ground the circuits and verify response of trouble signals at the control panel.
581b43b6-557e-44e8-8658-90f4377842bc | checkpoint | Confirm all speaker circuits and zones are associated with the EWIS panel are commissioned and functioning correctly in accordance with the cause-and-effect matrix.
b2ee3d48-b38a-46a2-8a97-84b508e27853 | section | Completion
6f4b3f45-dfab-42c6-93f5-e274ec39aebd | checkpoint | Visually inspect equipment for damage and cleanliness.
9e3d6a76-b36d-4641-b045-eb5072948a99 | checkpoint | Confirm all labelling is correct as per IFC design.
1346d763-d84a-4f37-b838-90cb6981d2fd | checkpoint | AS-installed drawings covering the whole system complete as per AS1670.4: 2018.
fa407a4b-6dfd-4408-ac0c-153dd5e95522 | checkpoint | Provide Installer’s Statement in accordance with AS1670.4: 2018 Appendix F.
f5a22650-7b24-4c46-81a1-1b4b7f579e35 | checkpoint | Provide Commissioning Statement in accordance with AS1670.4: 2018 Appendix G.
a3afd4fa-4a14-4c4a-8f3d-57c19bbce880 | checkpoint | All baseline Data has been recorded as per AS1670.4: 2018.
7874373c-fe5a-4d16-9071-9a0c2807717f | checkpoint | Confirm all covers and settings are returned to service state on completion of checks.
736c49c3-a60f-4f52-be2b-b404fa26292d | section | Verification & Sign off Acceptance
42a77089-63b4-4173-9375-ed43865b5d9a | checkpoint | Completed By (Contractor)
53143d54-0766-4d79-b97c-73406a74e68f | signoff | Signature
f7540009-4631-49c3-8860-e1155846f7f7 | checkpoint | Reviewed By (Contractor Supervisor)
1a2f3a6c-5021-455e-950c-bd066cf759f1 | signoff | Signature
ace7c1ad-8c2c-4f27-87ec-5905836d92a0 | checkpoint | Reviewed By (client/Consultant)
d6ae5ef5-958c-450d-93c6-f1f9881648d3 | signoff | Signature
69bbc06c-12d5-503a-863c-8120d1a3a422 | checklist | Variation |  | Variation
a5b62ac3-139a-5ede-85cf-87eaad4252d7 | checkpoint | Variation Details Complete (Pass once inputted)
0cf51977-6d75-5af4-a97d-fbb55832298b | textbox | Variation Name
456c7393-3d47-5f94-96fe-dde149bcdf48 | textbox | Variation Description
83b89ec8-1776-5044-a934-f4d09f4b1d81 | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
ec2054e7-1c8c-5337-b42c-32593298a0a6 | textbox | Acknowledgement
f1d0cdfe-486c-57f8-ab76-60e4a40d8048 | textbox | Signature/Reference Mail
1a6ee5f8-7f76-5a22-a642-f356d017f01f | checkpoint | Photo(s)
06ed2071-cdf9-569b-9d7f-2eac913ce247 | checkpoint | Supporting Documentation (Attached or Referenced)
1a6b4db9-1d2a-5aef-9414-698aed9fc72c | checkpoint | Variation Sign-Off - Click to Add signatures below
64723357-e840-5990-b650-f9868a197067 | button | Leemark Representative Signature Added below | Yes, No
678e2a6c-2c78-56d9-a89f-7bfd9a7761c0 | button | Builder Representative Signature Added below | Yes, No
00a2bba7-2b35-50f7-a8c5-d9b232d00959 | signoff | Click to Add Signatures

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
7a7163e2-186f-4566-89cc-f40cb3311972 | checklist | Document Attachment ITP (V.220421) |  | Document Attachment ITP (V.220421)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ceb21b98-23cd-4811-acfb-42c42d1cb8bb | checkpoint | Documents/Drawings attached for reference - Pass once attached
289eab76-526d-4c8e-ba92-c5e3be7a64fe | checklist | Handover ITP (V.200521) |  | Handover ITP (V.200521)
40103c7e-7c27-46d9-b35d-2a8a8de4c5e0 | section | Design
80997732-1549-4a59-be04-f6d9764da491 | checkpoint | Shop Drawings - Pass once completed
54cc4cf5-1e43-5971-8796-67f2175f33a5 | note | By: Drawing Office
998e491d-28b8-51b0-923a-4c44b2f3916d | note | Verification Criteria
2bd6c66b-bcea-5407-8d09-8507bb1dc109 | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
eed868d7-9449-5002-9e62-e79a6df44195 | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
1303486e-530b-5fc7-a36a-6f1d1f343ca1 | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
cdee54ba-a4fa-5115-bf26-c3f6178c16b3 | note | AS2441-2005 Installation of Hosereels
a809c7f3-3499-5a0a-953b-e608f5e48bf0 | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
e15087d2-b3e7-5fe2-994f-84c26963a8a2 | note | AS 1670.1-2004 Fire detection, warning, control and intercom systems - System design, installation and commissioning
e6f9a49e-da76-5aad-bc5e-63a902cea9e5 | note | AS 1670.4-2015 Fire detection warning control and intercom systems - System design installation and commissioning
74304b6f-c2d7-5bc6-92a4-233339d21012 | note | Project specification (TBC - Once known comment below)
bf8ecbc9-ba47-5293-9fc5-2e1a2a73cf94 | note | .. ..
fa731313-f8c2-5693-9b74-062673e58dfa | note | Quality Control Method
97149614-9a61-53f8-9814-8395a19c5bc8 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
42c8ce40-de7c-56b5-950e-4508dee4ac34 | button | Approved by Project Manager | Yes, No, N/A
6e348f76-0286-5905-9cfc-481cb122f4a9 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
31eacea8-df27-5820-89c6-cccfdb707ac8 | note | Records: Aconex
ae5c0927-8234-4755-a5a0-61684009b080 | checkpoint | Hydraulic Calculations - Pass once completed
36cf3c6f-0bad-5a49-934f-3a4950ca5cde | note | By: Drawing Office
14e7a470-c567-5534-b92d-d57a853c3fce | note | Verification Criteria
82aa09e5-d77c-5bdb-aeed-073799a08afb | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
fe0a630b-e040-5bd9-b2c0-5c4772e6fd00 | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
97c22bc1-7f7d-505b-a166-1f1d098fb36e | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
2b3748ed-4cb3-5fe4-865a-4d98555d95f8 | note | AS2441-2005 Installation of Hosereels
e7750ddc-3650-5695-a770-b4fb3a7d519d | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
27f63974-b06c-5c14-bae4-ccbd573d0262 | note | Latest revision FER. (TBC - Once known comment below)
6da00f99-e433-5030-b4ed-873fef5acd06 | note | Project specification. (TBC - Once known comment below)
9ed28448-c377-5837-a797-9b81155b6e31 | note | Quality Control Method
f7ec08e9-7023-5ff5-a358-1cfd597c5cb2 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
5386ec06-b17d-5769-8471-2a3f2855d73e | button | Approved by Project Manager | Yes, No, N/A
3d5e1ea7-53fb-5ace-bd15-3fa6084e6be2 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
6f1bdc13-cc6a-5045-a07f-2faf3bd46ecf | note | Records: Aconex
b086ffcb-bab3-48f5-b108-0a5279ebbd24 | checkpoint | Samples - Pass once completed
03e63d02-fc2f-59ab-81fe-b14773f64dbb | note | By: Drawing Office
a2ddea5f-df1f-5d27-90b9-824ab7d4ba95 | note | Verification Criteria: Part C.1 Samples & Details Part C.8 Fire Sprinkler System Part C.9 Fire Hydrant Pipe
790a0896-727b-5800-bc10-0f4e3f823454 | note | Quality Control Method
a4eed07a-adb7-57e8-98c4-867459a897d3 | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
92e34e18-1c8e-53d9-ba87-14a626a21470 | button | Approved by Project Manager | Yes, No, N/A
c66b6a83-e7e4-5fc8-91af-f824789d166d | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
240f1c5c-3752-5499-8e47-c4c7e8b3b37d | note | Records: Aconex
d3e87024-5523-4616-9a69-931e3b3028a5 | section | Offsite Manufacture
0086d639-aaf7-4124-8d4a-502f32571bbe | checkpoint | Pipework Fabrication - Pass once completed
eb4acae0-1a8e-5828-88ea-779da3e47734 | note | By: CWS
77affe76-08ff-5ca7-bf03-c596b25ace29 | note | Verification Criteria: C.12 Pipework & Fittings
d9c65a86-633d-536c-8b50-e0221b8f6b06 | note | Quality Control Method
f6899149-01e8-5213-9446-b1f930f9d821 | button | Leemark Inspection Completed | Yes, No, N/A
0559e73e-9841-5c65-b715-22c7e290f6b0 | note | Records: CWS/ITR
dd08831a-78ad-4728-a96b-aa167b4e6425 | section | Installation
05abc52e-be60-4ce6-9bae-e0b261f2ba25 | checkpoint | Sprinkler - Pass once completed
73d04cb5-e27a-5ef8-bd31-a41670bc597d | note | By: Sprinkler Fitters
cb948edd-35e5-5200-953b-3eac5729f0e4 | note | Verification Criteria: Part C.8 Fire Sprinkler System AS2118, 4118
88fdfa22-da1c-5e86-a6b6-81e534a62e6f | note | Quality Control Method
0b848368-b6cb-51bf-bf91-ff722502039a | button | Leemark Inspection Completed | Yes, No, N/A
8691992e-e6ea-579b-8734-c0e2b0bb0f65 | button | Witnessed by Project Manager | Yes, No, N/A
a184d5c3-7d81-5c5f-9edb-4187bc3481a1 | note | Records: Inspection & Test Record, 301/301.1 & 301.2
2eb0e636-3668-4914-a290-468dfe4bd422 | checkpoint | Hydrant & hose Reels - Pass once completed
e79927b1-000f-5461-a074-91bbd2235e1d | note | By: Sprinkler Fitters
f65d7b6c-98da-5454-8f05-20313ecbd553 | note | Verification Criteria: Part C.9 Fire Hydrant Pipe & Hose Reel Installations AS2419.1/.2/.3 & 2441
3156589e-bae5-5a38-9791-a0dffc480d19 | note | Quality Control Method
67a8069c-d811-5919-9c8c-c79703934138 | button | Leemark Inspection Completed | Yes, No, N/A
7acdf074-fdbf-5ac3-863a-357f90fa58f0 | button | Witnessed by Project Manager | Yes, No, N/A
61ac546e-ffea-53f2-90c3-ff3e05783147 | note | Records: Inspection & Test Record, 302.2/302.3 & 302.4
f44de234-b375-4683-9225-06391304ae3c | checkpoint | Alarms / EWIS - Pass once completed
c065e4ee-373c-56e4-8fff-1f284987af53 | note | By: Fire Alarm Technicians
b0f0ebe8-d2c3-5fa4-b5a7-0dfed04d332f | note | Verification Criteria: Part B.12 Fire Detection & Alarm Installation, Part B.13 Emergency Warning & Intercommunication System AS1670
0b8c79cd-774d-5594-b33b-7329a18beebd | note | Quality Control Method
e704b738-34d7-5bac-bcb2-b7ae5b5b0afc | button | Leemark Inspection Completed | Yes, No, N/A
cc8650c5-5192-528e-b069-9d2dd50b7794 | button | Witnessed by Project Manager | Yes, No, N/A
9983dd79-c3a3-5324-93bd-7a02789e5f91 | note | Records: Inspection & Test Record, 303.1 / 303.2 / 303.3 / 303.4 / 303.5
321ec174-633b-432e-addf-b365722629a6 | section | Commissioning
c611a7f9-482d-4309-b4b7-af26306170ec | checkpoint | Hydrostatic Tests - Pass once completed
094940ff-33ec-50e1-9670-9feaadc13727 | note | By: Sprinkler Fitters
08bfa7e2-a489-5d16-a5c2-da8a3521633c | note | Verification Criteria: AS2118, 4118, 2419, 2441, 2941
9ce2dbae-c94d-58b7-a8db-ad3fd71a1d85 | note | Quality Control Method
3e5f1aa9-f1de-5778-9886-02e5f9f6ba44 | button | Leemark Inspection Completed | Yes, No, N/A
b59b09ee-2139-5627-8590-f13314d3f2b8 | button | Witnessed by Project Manager | Yes, No, N/A
86f2672a-fa76-54af-9a79-95468cdce468 | note | Records: Inspection & Test Record, 401
260dadac-ef46-4653-8eb0-3d0c1560f8ba | checkpoint | Sprinkler Inspection - Pass once completed
996e8f9d-2416-5446-8974-d9ef9dd2c9b0 | note | By: Fire Safety Victoria
3c521170-aeb3-53ec-bead-2e9bbb6cccdd | note | Verification Criteria: AS2118.1, AS2118.6
8be7c6ec-660f-53f6-8b44-832db545c1ca | note | Quality Control Method
39774cfe-ea1c-5930-858f-29005a9e6eb2 | button | Witnessed by Project Manager | Yes, No, N/A
d3560a7c-3d2e-51ab-a01b-66ffaf55b7fd | note | Records: Certificate issued - Attached below as applicable
54d1cca0-27d3-4e41-a413-44f5f521b3e6 | checkpoint | Hydrant Inspection - Pass once completed
9eb40f79-d4da-575b-a72a-c06402f233fb | note | By: Victorian Hydrant Test & Plumbing
1c528f76-594b-5c2d-aa74-44ca1483a225 | note | Verification Criteria: AS2419, AS2118.6
d7324380-8ec0-59ea-ba4b-a81d1d295b1f | note | Quality Control Method
62171b23-8466-579f-aaed-ce83f2b5b4e6 | button | Witnessed by Project Manager | Yes, No, N/A
1e27ab2b-ede9-5f2e-82d7-3fed7acc3f17 | note | Records: Certificate issued - Attached below as applicable
001b4362-f889-4903-9e91-5c25f94eb55c | checkpoint | Alarms / EWIS Inspection - Pass once completed
864eb6f6-5963-5173-8e77-b2970b358f03 | note | By: Fire Safety Victoria
7957d0a3-8897-54ee-b028-f73819e369e5 | note | Verification Criteria: AS1670
a788c6d7-278d-5fe9-8412-658fb7689559 | note | Quality Control Method
05c8d74b-d3c2-5e6c-9819-764dfeadcabe | button | Witnessed by Project Manager | Yes, No, N/A
5342cba9-0a41-576a-8a2c-fc9f630a4397 | note | Records: Certificate issued - Attached below as applicable
7196f56c-dbe6-4c27-87d2-701f1287f3c5 | section | Completion
b2016135-d1eb-4d15-8142-1eca4571d992 | checkpoint | As Installed drawings - Pass once completed
270a7789-0811-5b48-8a09-d0c8978d2916 | note | By: Drawing Office
6e75709e-994c-5e41-8435-0c18f55d4a4a | note | Verification Criteria: AS2118.1, AS2118.6, AS1670
074fa7d8-289c-5304-a0bc-b14cf6f47e82 | note | Quality Control Method
f79ab3e5-92dc-5810-b36a-d9de6dada2fe | button | Document Submitted by Leemark | Yes, No, N/A
d76ddbb6-e89b-596e-a0be-8819424f49cd | button | Approved by Project Manager | Yes, No, N/A
232a30ff-dd2c-522e-aec5-f0f09d9a56fb | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
6047239a-7546-534e-bc7a-da686c63ee23 | note | Records: Operation & Maintenance Manual - Attached below as applicable
a8ce506f-3271-4e6c-8882-4e22c0bd6ef3 | checkpoint | Manuals - Pass once completed
562ab92f-c397-513f-9134-91f7c22acb8c | note | By: Drawing Office
8b7e9992-a049-59fe-b352-7eedbf63950d | note | Verification Criteria: As per SOW
a641ae2c-c5b9-52dc-bcbd-42d1c6086022 | note | Quality Control Method
5871ab76-79c9-5c35-b9c9-37372271d0d8 | button | Document Submitted by Leemark | Yes, No, N/A
75e9f222-5351-5cc6-9b44-f98817c8b4f4 | button | Approved by Project Manager | Yes, No, N/A
a40aa75e-5958-5b13-bbf1-3a202cb13b86 | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
b2e58dcf-79c5-560a-9fbb-c9ec23c94330 | note | Records: Operation & Maintenance Manual - Attached below as applicable
04d7be12-a5f9-4324-9ffd-502bae2449c0 | checkpoint | Test Data - Pass once completed
753c9536-3ab8-5a4d-857d-3b4aad3a7a04 | note | By: Site Foreman
2eb46fca-2afd-5986-8b94-190f1b342256 | note | Verification Criteria: Refer Commissioning part of this plan
f3477c3b-008c-57c9-aecf-e06780fccfe0 | note | Records: Operation & Maintenance Manual - Attached below as applicable
7e265d82-5caa-4a37-9f99-5613f571a1c3 | checklist | ITP/R Test Report Gaseous Suppression System (V.240521) |  | ITP/R Test Report Gaseous Suppression System (V.240521)
e6df0780-bb4a-4c8e-b560-9fb7032d2c8f | section | Installation Testing
5202a0fe-346d-42c1-83b1-87021038e042 | checkpoint | Latest consented drawings checked & referenced
62a0fa2a-5977-5c2a-afb9-49c02ed22653 | textbox | Drawing & Revision #
1ec31013-4d4f-5238-87f5-af12f35bc531 | tickbox | Area clear, tidy and accessible
da3eabf4-fcab-5fc0-a7db-5bcc26673a69 | note | Attach Photos/Comments below if any issues & send report to Builder
a2f2d193-9669-433a-86ad-3bbfb716e8b1 | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
31a8aa00-056f-58c6-bf1f-64af9eab2209 | note | Acceptance Criteria: Installed to Approved Drawings
eee0155b-0159-4daa-94c2-f4e427130f32 | checkpoint | Installation inspection of pipes and nozzle droppers/risers
d2025e93-e524-50c8-9068-0883a5a9c25f | note | Acceptance Criteria: Installed to Approved Drawings
9bc8bda9-b66d-4043-9544-9fc66f2ac8c0 | checkpoint | All dirt traps must be capped and all pops temporarily plugged
421aed46-fff9-5c30-b36e-50529f6a8fd0 | note | Acceptance Criteria: Installed to Approved Drawings
1935834e-7fcb-42af-986d-4f904bb28084 | checkpoint | Perform Pneumatic leak test of pipework in accordance with approved Test procedure and SWMS. Gradually apply pressure increments of 100 kPa for 15 minute holds
3836e2b8-145f-519a-9afc-f60aa7a87dd0 | note | Acceptance Criteria: Pressure drop should not exceed 20% of 300 kPa for 10-mins
dd5b4916-e111-4124-8a3d-ed1110cbc042 | section | Installation of Cylinders, Manifolds, Valves, Actuation, Discharge Hoses & Nozzles
31f7eae3-dc5a-4c20-b953-e109b48b6188 | checkpoint | Cycinders shall be adequately mounted and suitably supported according to approved installation plan
47968f42-6357-55cb-bfc8-3ec601e36c06 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 8.2.3.12a
ce660afc-7130-43f2-8a6b-da467ac5d521 | checkpoint | Discharge manifolds and valves shall be mounted and adequately supported
68e734aa-caf2-53dc-9855-9383f96b6563 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.4
fa2032ad-1e27-419c-8aa3-3602387d3bd6 | checkpoint | Adequate quantity, correct code and location of discharge nozzles shall be installed according to approved plan
303b6c5c-53fb-548c-b630-4c6cf02a09c1 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.6.1
c372a293-a80d-40ea-bb01-f97e13d6e738 | checkpoint | Detection, actuation, alarm and control systems shall be installed and tested by “DRY FIRE” contractor in accordance to relevant code/standards
e2ba9b84-2f91-5d38-b511-aa171c595c34 | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.4.1
e42fe181-b24e-45cc-be2f-d043f8b83eec | section | Enclosure Integrity Pre-Test Inspection
18602f5e-1341-4f87-acaa-06409ce01b07 | checkpoint | Client to confirm that all services penetrations and/or openings are sealed prior to the test
f0edb965-99a3-5727-b8ee-ad2ecc4f70a0 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
60bd0a34-510c-4031-9a00-ddda18d07e01 | checkpoint | Client to confirm that all HVAC fire rated dampers including OPR Damper can be closed prior to the test
3fa4cae2-0efb-50f5-9538-31a97d27edaa | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
20ad42eb-48fb-41a8-bd77-5fa7d44e9b7e | section | Enclosure Integrity Test
0c4da889-529a-4fa6-8579-4a2b2c369b58 | checkpoint | Perform both pressurization and depressurization fan test of the room and using the software program, confirm that holding time is equal or more than the required 10 minutes
bbb8d79c-c6f1-5551-9026-4545f97eab60 | note | Acceptance Criteria: Relief Damper Installed is sufficient
28b2edf1-49b7-4b13-a649-346e250561d7 | checkpoint | Prepare full test report of each enclosure demonstrating the level of compliance achieved
f993cc11-2fb6-5e22-80d7-6a4ac901bcb3 | note | Enclosure PASSED the hold time & venting requirements
ad000a8f-93d7-407a-8aef-cd960d40556c | section | System Commissioning and Acceptance
3f558f93-58f4-4c4b-85c8-f7a84eed0133 | checkpoint | Prior to start of any test, ensure all extinguishant storage container release mechanism are disabled or removed
733e612d-dc2a-5f20-bc5a-c04242ebf90f | note | Acceptance Criteria: Release Mechanism Isolated
8d27529c-ccad-4f29-bab1-c6c7f7f8ab77 | checkpoint | Verify and confirm compliance to the approved design of distribution piping system, discharge nozzle sizes & orientations, storage containers quantity & locations and warning signs & notices locations
01ec1181-cdc0-5c6a-a447-f7210452e4b3 | note | Acceptance Criteria: Installed to Approved Drawings
820f4d95-dfb7-4685-b2f9-f4a018ea4a2e | checkpoint | With the operation of fire alarm system, verify and confirm operation of audible & visual alarms, plant shutdown interface, time delay & release mechanism activation/30s time delay / solenoid operated/ audible visual Alarm
41870656-d871-5785-a267-de57067d58f9 | note | Acceptance Criteria: 30s time delay, solenoid operated , Audible/visual alarm operated
7352f725-b2f0-4167-9a84-aca9d25d2e37 | checkpoint | Simulate discharge pressure switch operation and confirm gas released alarm indication at Fire Suppression Panel
91999b87-0227-5345-bb3a-caba2192d222 | note | Acceptance Criteria: Indication at FIP
162684b4-1bb4-425b-8ada-801b2fc51ed2 | checkpoint | After completion of system functional test, reset and reconnect all release mechanism onto storage container and return the system to full service condition
d9783e45-466a-581f-95d9-889e8ec62519 | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
d90526ba-9dc7-47ec-bdde-05c2435bb90e | section | Completion
294eab0b-9c0d-487d-86ef-4467f16755c0 | checkpoint | Works completed to specification/drawings - Attach photos of work below
c04138c6-c5d8-5f70-928c-d87f30e6625f | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
b7baab7c-a5ef-58eb-ba39-87e3f4e13a6e | button | Area left clean & tidy | Yes, No
9b99afbe-74d9-5330-b268-2bbba0a5c42e | tickbox | Leemark Sign-Off
c3941c3a-d96d-565b-8040-4079e7f99ac9 | tickbox | Builder Sign-Off
6b33b20d-5e9b-480b-b805-1fc3130ff8c3 | signoff | Sign-Off - click to Add signature(s)
c095af84-01e8-493f-b393-fc0f782d3459 | checklist | ITP/R Test Report Pre-Action System (V.260521) |  | ITP/R Test Report Pre-Action System (V.260521)
685d98ff-e556-4c2d-aff9-7e2143247a6f | section | Installation Testing
7765d59f-897c-4e6c-b543-b1a3d6a2b417 | checkpoint | Latest consented drawings checked & referenced
2717efb5-ebdb-5698-97fd-4e22e3ac0a9c | textbox | Drawing & Revision #
18657d80-d4bd-5fd4-a387-e93520074dba | tickbox | Area clear, tidy and accessible
3c342476-ac95-504d-aa7b-161b1cee6f22 | note | Attach Photos/Comments below if any issues & send report to Builder
ed8f961e-a4b6-4a4e-916b-b4c0bde2d471 | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
623b5841-e60b-57b6-be82-574878bac6a0 | note | Acceptance Criteria: Installed to Approved Drawings
dce7ec04-b7ed-42d1-95e7-3d770b764126 | checkpoint | Installation inspection of trunk mains and range pipes
fbed70d6-865f-526c-b31f-d036517012ef | note | Acceptance Criteria: Installed to Approved Drawings
f3806b73-6928-41c8-9d00-92875009f8ec | checkpoint | All dirt traps must be capped and all pops temporarily plugged
8c6818e7-3b11-5712-9ee8-6913af6376da | note | Acceptance Criteria: Installed to Approved Drawings
098d79c2-d799-4259-82b8-33205f97c8fa | checkpoint | Inspection of installed sprinkler heads & baffle plates and flexible droppers
f0fabf98-eca0-55b5-a7ff-d60f16a8f56e | note | Acceptance Criteria: Installed to A.S 2118.1
98baa5d2-aed4-4c8c-a624-6173f4680e68 | checkpoint | Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
a5a3bb76-134e-5f6e-b87d-c5667bc1e6a1 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
00b6dfca-ae0b-4bfa-92a6-e584f1652f89 | checkpoint | Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15 minute holds until test pressure of 1400 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours
690b184e-eb84-54a2-9fca-c4732b29d274 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
673cfbc2-a4f4-414b-ab6a-b91d82607a8a | section | Installation of Pre-Action Valve Sets & Ancillary Equipment
57e7d877-e8f2-4412-b35d-80cac1042f81 | checkpoint | Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
bdfba4fc-65b5-501d-a650-bce8725f361f | note | Acceptance Criteria: AS 2118.1-1999 Clause 8.1
b03f32f1-b8e6-44f7-9b26-a14a83f18e23 | checkpoint | Verify installation of alarm devices (e.g. DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP)
20e528f2-5aac-53e0-bbcb-717bac417d5c | note | Acceptance Criteria: Refer AS 2118.1-1999 Clause 8.10.1
e68013a2-a24b-4425-a495-47da72a84dab | section | System Commissioning
88ff7299-cdf8-4399-82e8-bff507daf7cf | checkpoint | Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel
2d0846ed-589e-514e-8128-f08922ef6253 | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, DBA -3 mins
8e2c3b61-95d3-46fb-a9c1-e49c9dca8709 | checkpoint | Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel
bc556e91-befc-5b66-b1b6-2e361229c0ef | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, operational confrimation
d2a8d32b-b328-419d-ab40-258019fdad23 | checkpoint | Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
1f99a2fa-10c3-5196-9008-4175a83de86d | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, Time to recharge 30 mins
793da296-a1ee-4d58-aba8-c6385c9afceb | checkpoint | Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
0b4d3992-2155-52b3-aafa-5c99b28129e2 | note | Acceptance Criteria: AS 2118.1-2006Clause 15.6
12220300-bbe8-487b-a99e-c2d8927bed5a | section | Completion
0b123cf9-f61f-43c1-917d-0e54b5660ba0 | checkpoint | Works completed to specification/drawings - Attach photos of work below
b0287808-882f-581c-8be3-e55eb35158d3 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
75c81048-4d0f-5290-a74d-2c28fd20424d | button | Area left clean & tidy | Yes, No
ef78ec90-1364-5d4f-a6d1-d7c96b03dbc7 | tickbox | Leemark Sign-Off
8baa4335-150b-56fd-9c20-e6d5f364a2c4 | tickbox | Builder Sign-Off
a210d9fa-16f6-4d62-8d0e-c75bcab8d204 | signoff | Sign-Off - click to Add signature(s)
388051ba-c47d-4ed8-a685-a28eaa07b25e | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff (V.171121) |  | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff (V.171121)
850061f1-8a7c-4b26-8d9c-918526c8cce9 | section | Sprinkler Rough-In
06d2a1ab-d01f-40b5-abbf-a2ccda036843 | checkpoint | Latest consented drawings checked & referenced
729fe984-18c8-5ae1-aaaf-dc7f65eefa27 | textbox | Drawing & Revision #
1740f094-105f-5366-be0f-a9dfc3179c93 | tickbox | Area clear, tidy and accessible
cb25e86e-3620-55ff-bfd5-154b180cade2 | note | Attach Photos/Comments below if any issues & send report to Builder
3c48735b-dc7c-4ff0-819d-e7ed9b26c374 | checkpoint | Supports spacing & fixing as per AS2118
a2af940f-5b1d-4079-ab23-3bfcefd72476 | checkpoint | Pipework installed as per drawings
7548be30-23ff-4c8d-9532-37b4db6392f8 | checkpoint | Concealed space sprinklers installed
f131441e-d178-4f82-bbef-769095576f0a | checkpoint | All ends blanked off/plugged for testing
d8dd9cb6-d5a1-42d4-be80-7f558cfe9bc0 | checkpoint | Pipes left out
46adf40c-d712-537d-87be-0a36c7d71ea1 | note | Fail=Missing, Pass=Complete
b71d9fdf-1ef1-510c-afdf-20915454db63 | button | Pipes left out - installed | Yes, No
0a6fcf79-b056-480f-a36f-2fe5eb3fa30a | section | Sprinkler Fit-Off
2d1def4f-bcf2-4e34-ab22-cc60019186f0 | checkpoint | Latest consented drawings checked & referenced
a2447c46-069d-52ab-aff3-5c5a4554a8da | textbox | Drawing & Revision #
fbb38057-1528-534f-a0c4-04150817a7dc | tickbox | Area clear, tidy and accessible
d77a52e6-1471-58ec-8dc0-9207b78232cd | note | Attach Photos/Comments below if any issues & send report to Builder
17cef2ea-a9f5-4d93-aebb-be97a789cd7c | checkpoint | Ceiling grid levelled
ed9ccac6-8592-471b-8f79-c7738936139f | checkpoint | Sprinklers installed as per drawings
8ad1e13a-63eb-409e-bdb1-c57120d5d415 | checkpoint | Sprinkler Type & temperature as per drawings
5c0a5ea3-0848-466c-b2a7-696a29f4fbc9 | checkpoint | All escutcheon plates installed
faca081e-d235-4f56-8433-5f8ce2a60f66 | checkpoint | Areas not fitted-off
dee6254d-04ec-5110-8f51-da41b8f2fd33 | note | Fail=Missing, Pass=Complete
61c37e05-9252-5675-bda3-7107a1693dcb | button | Areas not fitted-off - completed | Yes, No
3af7dc9b-1ece-4f84-a51f-f4126eb2fe17 | checkpoint | Client Sign Off Sheets Complete
af40afe0-d52e-4f66-8f7e-39fed8755d34 | checkpoint | Painting carried out
7c1a2f92-3ca1-4561-8827-43e91560a2fc | checkpoint | Pressure Tested (refer ITR 401) - Completed
ec33152d-3420-4ec6-ac3b-1c6915aa812f | section | Completion
60c223f0-f622-4ae4-801c-7c7f1ef86c8d | checkpoint | Works completed to specification/drawings - Attach photos of work below
ce182bf7-330e-52f8-84b5-fdbf0de09a88 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
cb7e8029-b34a-55e7-857e-976a0ef57110 | button | Area left clean & tidy | Yes, No
2e280c68-389f-5302-bfd3-570d423c4e2f | tickbox | Leemark Sign-Off
a273c4b0-a067-5cbf-af00-192315849bba | tickbox | Builder Sign-Off
56b2bb6e-c65a-4bf3-b3b1-5087f792ac82 | signoff | Sign-Off - click to Add signature(s)
403a95b5-8079-4e20-bf1e-2ad2577ea7b2 | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121) |  | LM-FOR-30-ITR-301.1 Sprinkler Control Valve (V.171121)
586d68e5-56af-4ee8-9c3c-4eb2854ddcdf | section | Installation
0f2eb136-ca1c-400f-82e7-6e61effdfefb | checkpoint | Latest consented drawings checked & referenced
744ffa30-d43c-5a54-8fa2-d705e31b32ca | textbox | Drawing & Revision #
be41f775-3179-5c4c-bba8-a43c5c7d6ef7 | tickbox | Area clear, tidy and accessible
b1a9e4c2-ce24-54bd-bce8-517f90ce2f33 | note | Attach Photos/Comments below if any issues & send report to Builder
5360f36b-0efb-475f-b456-0439df7c8ae4 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
20242b29-98e6-453e-ba61-1da6054ff73f | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
4bca0ea8-9a80-4f0c-8915-e2db9da21d97 | checkpoint | All roll grooved couplings / flanges are properly tightened
e6bd2183-4b66-46a3-aac0-2419b8ed60b2 | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
99bbf574-64e2-4c26-8c37-e034edee5f03 | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
d4360766-c281-49c4-b936-e0af85afada5 | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
267f6cd9-5447-4a3a-907e-98fdfef84e72 | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
3936f0f4-fc65-49e0-920f-549ed98f5eb6 | checkpoint | Correct type solenoid, flow switch, couplings etc installed
e5351134-b91c-4d8f-96b5-1ed8c2cbf72b | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
2653b395-df5b-4f3c-9bdd-8e37f20872a6 | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
9f6ce24c-977d-49d9-b40e-0103a1092c8a | checkpoint | Control Valve is positioned between 1150mm to 1800mm
feda4b01-df1f-4552-85ec-e48d3be8dfbd | section | Completion
a709a9a6-e11d-4f92-a7a2-ff1675603396 | checkpoint | Works completed to specification/drawings - Attach photos of work below
d61e02b1-51a1-5e2d-86aa-c47e99c5a3c7 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
e5ea09a9-9d94-5963-882e-75cb54e16ce4 | button | Area left clean & tidy | Yes, No
4701a567-7a6d-53ce-a1ba-67000ad27c4e | tickbox | Leemark Sign-Off
1a90e724-ccf3-50f3-8336-38fbf91bd63e | tickbox | Builder Sign-Off
e925c883-2f4c-4113-8c01-645f1ddc8c7d | signoff | Sign-Off - click to Add signature(s)
8630b8fe-59d2-44fe-af47-2903875b7cf3 | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121) |  | LM-FOR-30-ITR-301.2 Alarm Control Valve (V.171121)
039e5f44-6f5e-4150-91fb-8561c27340aa | section | Installation
0c8dde60-1352-4aa3-962f-fcdada8e4461 | checkpoint | Latest consented drawings checked & referenced
f13cd7eb-9a16-54e1-859e-b6f37ea5d8c8 | textbox | Drawing & Revision #
4ce3ace6-be3f-53e3-ad9f-62a890d6dbad | tickbox | Area clear, tidy and accessible
b4bc0c5e-a24a-596d-b5db-0fbe73fc0311 | note | Attach Photos/Comments below if any issues & send report to Builder
3b0e7268-0c9a-427f-9bea-a4801023f8e8 | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
d7343718-89e5-4e98-95e5-23ded92e5aed | checkpoint | All supports are completely installed, spaced and bolted down
830e71e5-a1e6-4162-881b-38dba82b3681 | checkpoint | All roll grooved couplings / flanges are properly tightened
7066d8be-ba02-4877-89ec-cb34242b1fcd | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
eb7f48f8-a260-4223-b4b0-184e47876293 | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
99a8d788-8c10-41ba-8ddf-26646dc454a6 | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
ece1775c-8796-473b-9ed5-9832855bab42 | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
a86485ba-992d-4760-bc09-62fd29925ced | checkpoint | Main waste & test valve is fitted and piped to drain
4fb553de-4b2c-427a-ac52-183dcf7b49d8 | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
78990910-bd17-4de2-8403-83429a98b177 | checkpoint | Correct model and range of Pressure Switch is fitted
9f18911f-9c88-4f40-808a-52978aaf97bb | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
3e7c1dbb-d600-48ff-8e64-296cbd8477b8 | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
40aec424-7c72-4969-9804-b0cf0cde9002 | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
149d2280-0624-4cc8-876c-c71f6c49e219 | section | Completion
c260800f-16ad-40b1-aafd-961bd0b7cbc6 | checkpoint | Works completed to specification/drawings - Attach photos of work below
d98a7546-f1c0-54ae-9d09-46c544fd5396 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
e352e9d9-90f7-5782-9cf2-beaf5abe4ff6 | button | Area left clean & tidy | Yes, No
1d660763-7d9e-57e4-a513-82deb83267de | tickbox | Leemark Sign-Off
b7a68b11-ce9c-5004-b7c1-3d15233c9776 | tickbox | Builder Sign-Off
d012422b-b6ea-4832-87b5-207a64291102 | signoff | Sign-Off - click to Add signature(s)
9d18f838-3842-46eb-944b-f8dcc96667ec | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121) |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test (V.171121)
ff789bbc-ea49-46c3-bd09-bfff97bb2a7f | section | Guidelines
003ef4f5-2790-425b-b573-1c29d9889d98 | checkpoint | Guidelines understood - Pass once read
0b64ab13-e812-56ff-a9e8-18f298fdb387 | note | Guidelines: Fire Sprinkler Systems – –AS:2118.1 2017- 1600kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
d9dde3ef-ad8f-5a72-a919-7315df290bca | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
c63f1a54-81db-5cb3-9204-3d09132386c6 | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
18900736-259a-44b4-99b8-51e5b78e2016 | section | Rough In Only OR Rough In & Fit Off Together
d4e29aea-e8d4-437f-acca-95113f76e692 | checkpoint | First Sighting - Pass once entered
e9e63f10-cc53-5fc7-9126-ac010a281e5b | textbox | Date
87b17df7-32f8-5654-a0d4-dd9f00f1ca4c | textbox | Time
a7a176a1-383d-5949-921d-c0a05e0a40f2 | textbox | Pressure
62702824-ce8f-5a87-a111-fec048ceb689 | button | Photo(s) taken | Yes, No
e55fa8db-9bf0-59ce-b365-315b06b264b1 | button | Leemark Sign-Off - Attach below | Pass, Fail
dae0fefe-92d8-5755-a6d1-ec1da8e43ec0 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
94bbaad3-395a-49f8-8786-6c9a5d419e6c | checkpoint | Second Sighting - Pass once entered
7aececd7-0fd6-5ccc-a085-60b24b439dac | textbox | Date
06fc693e-4a07-5359-bada-171d378e15d8 | textbox | Time
a76ec9bf-5d34-5d0b-80fe-9e407c297489 | textbox | Pressure
228c2339-f794-5308-a6f7-779f8af78633 | button | Photo(s) taken | Yes, No
b92caa5c-9f7e-5ad3-9c4c-4ce354a7dc0a | button | Leemark Sign-Off - Attach below | Pass, Fail
fd61f5c9-3d75-59fb-bb71-fdcfc8b7e076 | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
d90e5fa3-a4e9-408e-8969-e34cded6dbce | section | Fit Off (if required ie if not covered by the above section)
2580d96c-1ec4-41a7-a4f1-99f8c4bde8ad | checkpoint | Subsequent Sighting - Pass once entered
e30fe7ab-c6a0-596e-9748-8d8fdc970dec | textbox | Date
f17691a6-54f3-5d37-9691-4492ed6b4c14 | textbox | Time
c2f887a3-443d-5225-acd3-7847a15b3870 | textbox | Pressure
e9d4606a-0774-5b51-bcf1-81ca181c587c | button | Photo(s) taken | Yes, No
91f1679d-6e8e-55d6-88e5-3b3142e71294 | button | Leemark Sign-Off - Attach below | Pass, Fail
9c07e472-9287-56de-89b1-6945159b58fa | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
d26e4d60-de1d-433c-af72-7de7c57d0f25 | section | Completion
80f785a0-a9fb-4779-b355-2e9c951ea254 | checkpoint | Works completed to specification/drawings - Attach photos of work below
a80927bc-0073-5224-8ca2-dd7535c1285b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
a0a51b11-722e-5125-82ee-1b6a2706812f | button | Area left clean & tidy | Yes, No
d9f2c759-4998-53a8-9e20-e9576258129c | tickbox | Leemark Sign-Off
29878c8f-7b72-5e61-8104-99fcec382036 | tickbox | Builder Sign-Off
353e9ccf-98f9-4705-9081-a258684d71f5 | signoff | Sign-Off - click to Add signature(s)
78ebc40e-fd90-4c03-9219-99671e3c4f30 | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121) |  | LM-FOR-40-ITR-302.1 Fire Pump Installation (V.171121)
77ae259f-ccf2-470f-8a93-5c7aaa2b4125 | section | Installation
92323a4b-6bc0-4676-a9a9-9cea35f065f9 | checkpoint | Latest consented drawings checked & referenced
aeddaca1-abde-5aa3-b0d6-449549dd3e1f | textbox | Drawing & Revision #
ab999950-13b2-58ca-bebc-82bc741581fb | tickbox | Area clear, tidy and accessible
e864ffc8-49cc-5ae9-9903-b94b8adf3fc2 | note | Attach Photos/Comments below if any issues & send report to Builder
c926c903-55e2-4a55-9b6c-beb9bdb3ab99 | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
88dee815-da6a-4385-80d1-e61281b8b073 | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
0b749933-3664-49de-82ef-6e7ac55263b2 | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
b77404ee-2c30-4534-bef8-5eee038ad12a | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
f88b16dd-e882-4235-879a-cefe0ccf3d7d | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
d8cc6c37-bce7-4dcd-9be0-fd5113f20815 | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
06216a43-29f0-4baa-a247-e37d3cb83a75 | checkpoint | Suction isolation valve installed is OS & Y type
6876940e-4db1-4d8a-906b-775a98542c20 | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
21f3838f-71e2-48cf-b4e1-497aef263638 | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
27267e1f-0e4a-44cc-b439-a296b76ad962 | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
9b7b1478-2a80-49b9-b63d-35f8a37fc698 | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
08fee66a-767d-423f-9d93-6fe9ba4b408f | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
11bba6ce-ed9c-49ad-a275-7aa19313b9a1 | checkpoint | Exhaust connected to pump and installed to approved discharge location
51000f15-d2ec-4632-b4d9-0e2ccfbf344e | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
d4dd3184-7700-4022-aef3-bc1750f1c1bd | section | Completion
4dd3d6ab-9107-47dd-a4c3-b5bd3019f437 | checkpoint | Works completed to specification/drawings - Attach photos of work below
3ce15177-95b1-5781-949b-545b1c3b33da | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
6c602a8f-ad94-595f-be8c-4843269d8ec0 | button | Area left clean & tidy | Yes, No
8c7a39a0-0aec-58b0-9ba5-a7877fbdb39f | tickbox | Leemark Sign-Off
c11821f2-1aaa-5d49-b45e-2dca2f79ea1b | tickbox | Builder Sign-Off
04c21d64-bf5a-4b27-a185-dbda48aa1e73 | signoff | Sign-Off - click to Add signature(s)
055abede-b709-40a8-a134-aa6f65fbfda9 | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121) |  | LM-FOR-40-ITR-302.2 Hydrant Installation (V.171121)
8bcc7c73-5c7c-47f1-ab7f-57982db2d187 | section | Installation
05166e5e-d04c-46a0-a097-445d072f267f | checkpoint | Latest consented drawings checked & referenced
73f8469e-1576-5f56-8809-e404636cef8e | textbox | Drawing & Revision #
e7b3871d-ceb5-5674-ade0-01d7a85d5c51 | tickbox | Area clear, tidy and accessible
9853057e-56c8-5e7f-aade-9d0a0bca705b | note | Attach Photos/Comments below if any issues & send report to Builder
b8ad2cec-2a32-5b16-9c6a-e8b32bf354e3 | textbox | Hydrant No.
267ee8a1-4c4a-43b6-b14b-807fa17f1b86 | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
cd1e422e-cbc5-420d-beef-c8c3524499f7 | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
be2bd747-ed23-469d-91cb-9c92a25bbf6b | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
5c598f14-6b98-4544-b37b-fdc3a5d2cd2e | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
aeee33d6-d839-40ab-8504-bad204635410 | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
d5324d52-7f9f-4906-a701-c1d74d3db8f6 | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
50c55764-de9b-4473-85d8-f1c58ef78a2b | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
7991e2ce-68ea-421f-929a-6816ca619358 | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
a06d1198-dbcd-4e85-8319-2dd1303af9fd | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
6c378e4a-5518-4f83-be2d-a83b74dbc06d | section | Completion
2769fe2b-9b78-4923-a9b2-292cd19f3bde | checkpoint | Works completed to specification/drawings - Attach photos of work below
f2ab01e0-1666-5ce1-bae1-62a4478c7c6b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
d5cf1117-21bc-5e14-a29e-4ac66e43b9b3 | button | Area left clean & tidy | Yes, No
c2de0326-73f0-571f-960b-6365b8acb514 | tickbox | Leemark Sign-Off
a7005aff-d9db-59ea-951a-f40445155838 | tickbox | Builder Sign-Off
ad44912c-2fd5-456b-85dd-3fea1b3dffb5 | signoff | Sign-Off - click to Add signature(s)
6e7788c7-ca5d-43e7-ad11-f2fcdaaa704a | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121) |  | LM-FOR-40-ITR-302.3 Hose Reel Installation (V.171121)
ac3fbbcf-9dc3-403f-bd85-89953be33696 | section | Installation
8e8dff6b-88bf-4841-8209-15e922d9fcd6 | checkpoint | Latest consented drawings checked & referenced
9d407ec6-79d4-5cee-8199-f3f69b7e3003 | textbox | Drawing & Revision #
9ac18e16-ac28-5040-befa-b7e77a4efae0 | tickbox | Area clear, tidy and accessible
09a5763f-977e-58bd-b3f4-024d47e9a586 | note | Attach Photos/Comments below if any issues & send report to Builder
10718bcc-bb5a-51ef-a003-9d7ce64a86ca | textbox | Hose Reel No.
4a6e2e40-54bd-430b-b24a-f2c120a741bc | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
8a0314c6-b794-43b1-b426-9ce566d3484a | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
0bf29b1e-a2b8-4dbc-94c7-dbbff68d62bc | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
e931115e-ae96-42b2-9397-37e8700fed91 | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
34247448-1f65-43b4-aa27-3464620134e0 | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
1ed2b50c-5646-4729-a5f8-9b235178c4cc | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
6133dd15-b679-463a-8523-e8edd2015c81 | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
edd6d320-1d32-4de4-9498-d585e69a0f0e | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
75ebada4-37b9-4a0f-9b23-7fe6b56767b4 | checkpoint | Any defects found on the hose reel assembly have been corrected
2003ab0a-9d0d-450d-95dd-7145dd47bd4d | section | Completion
38431196-b19d-40f9-b3d8-2274fb8f1e22 | checkpoint | Works completed to specification/drawings - Attach photos of work below
94523590-7594-5ddc-9074-543cfed2cc20 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
cc365632-8ca6-547e-b25b-c24eeccbe055 | button | Area left clean & tidy | Yes, No
5bdd7707-0228-55fe-9aa5-41d211a0b3da | tickbox | Leemark Sign-Off
bae5aadd-eaf3-5aa9-99af-5f06f0de97d5 | tickbox | Builder Sign-Off
ae771029-7e8f-4782-8420-1d5ccf82b5ad | signoff | Sign-Off - click to Add signature(s)
d4e1d234-eeba-4652-8c78-af80f12db9c7 | checklist | LM-FOR-40-ITR-302.4 Tank Installation (V.171121) |  | LM-FOR-40-ITR-302.4 Tank Installation (V.171121)
8b6eb205-38c7-46ac-9a47-f09be3c25fef | section | Installation
24055db7-991e-4ed1-a2f8-350a4701529f | checkpoint | Latest consented drawings checked & referenced
0625be13-62a4-59dd-ba05-3b4f56026a96 | textbox | Drawing & Revision #
76c11138-000c-52e4-8f27-684bf3c95be2 | tickbox | Area clear, tidy and accessible
75892506-b5bc-5b2a-bea3-8735934b9e2e | note | Attach Photos/Comments below if any issues & send report to Builder
6668b773-6283-45a7-bebe-f7d792d7e393 | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
19606019-9f86-4d7e-b709-2cb1f1bfbf98 | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
18226b7d-3bae-46ee-81c6-4f54f45636e6 | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
7a40409f-f809-4004-b77b-ae3096d225dc | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
8376fb3a-0aa3-408a-aaaa-5fea71e58d17 | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
46b4c029-0fb8-4ca3-80fd-c1782f6711e1 | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
e35e0a46-882d-4d97-9e5f-eae4b372363e | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
7ebea5e2-f1ac-4357-9bff-9011169ea91b | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
0631d8a6-9d8e-4ddc-8d46-d58713197745 | checkpoint | Tank external water level indicator is fitted and operational
ebb974e6-aef1-471e-b8c0-69768e44b1f4 | checkpoint | Tank internal and external access ladders are fitted & secured
bbb3f661-b824-40ab-927b-d60108220c56 | checkpoint | Tank access hatch is fitted and provided with lockable cover
8898fc52-281f-4e84-acb3-01923c73d86f | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
0a7b7b1f-3569-4c02-9f7f-d925b1249d53 | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
ffe99a06-0cd7-498c-9fe1-973ace713b2b | section | Completion
3fb3b317-14a7-4d38-90d8-0d650fe68196 | checkpoint | Works completed to specification/drawings - Attach photos of work below
d8a2bf5f-21c6-5bab-8521-0c81c5b82e87 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
db77c929-77bb-5caf-86ed-d6e6ae714c94 | button | Area left clean & tidy | Yes, No
fa4aeff5-e4df-5165-a917-dbac1fc4859b | tickbox | Leemark Sign-Off
93642111-a755-501f-aa5f-9bb00204e296 | tickbox | Builder Sign-Off
ea5f0bfe-e4a5-4785-a107-519c1df05626 | signoff | Sign-Off - click to Add signature(s)
2ae2f77e-e96a-401b-9cbc-d7d685f04bda | checklist | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121) |  | LM-FOR-40-ITR-302.5 Booster Assembly (V.171121)
4a40655d-9273-447f-8f9e-6b5bed3dbab3 | section | Installation
eae1b246-ff80-42c9-bb6b-470c77b5d9dd | checkpoint | Latest consented drawings checked & referenced
56bbc797-cdcd-5500-bc5e-f201f7135f6f | textbox | Drawing & Revision #
97b0563a-1145-5712-8117-d2c3f81f3d3e | tickbox | Area clear, tidy and accessible
35c9c454-0e34-52ff-bb4b-15389255d8d3 | note | Attach Photos/Comments below if any issues & send report to Builder
adb78d3b-e000-4526-b5ac-4639e13de0d6 | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
61f06423-7854-448a-a964-6e136b57dd03 | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
55fda8f6-935b-4426-af1b-82bf42cd09e6 | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
af476014-9702-43ac-b1d7-c0bcc908d4f6 | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
eaf2f471-1d1a-446f-af95-3f8928a03ca9 | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
f2ca59a4-9b53-401d-82cf-8171eb85a747 | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
888e7bda-e635-42f5-9a6e-f78686a40071 | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
7ef3f12d-d5a5-46ab-8e51-de88e86eccba | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
17e6fdac-bfac-419a-a354-ffaf6c5aaee5 | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
dad4ed50-881e-4b1b-9642-cfcbfacd9428 | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
e2e48e4d-2ca9-437b-a374-19841caa52ad | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
7d0b3ace-4748-42eb-8352-2a7a43917f50 | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
8e316779-73e9-4fdf-81a4-415a03c8af59 | checkpoint | Full flow non-return valve of correct size is installed in the proper location
af167c8c-e807-4544-a777-abec442673c4 | checkpoint | Approved type of cabinet enclosure is installed as required
a688cf2f-c504-46c7-a925-2cefb12ee045 | section | Completion
e2203c7a-8d75-4867-838d-12903df16bcd | checkpoint | Works completed to specification/drawings - Attach photos of work below
c3b0c150-2143-5a32-86b4-b55d1b842de3 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
0579ee63-48b6-5733-85d5-f3cf8f3c145a | button | Area left clean & tidy | Yes, No
f4583a50-c433-52d0-8506-92032328c592 | tickbox | Leemark Sign-Off
8619d35f-7cbb-5713-be21-5bf04e07475f | tickbox | Builder Sign-Off
f1567efe-956e-4f36-a24e-d59937d873d4 | signoff | Sign-Off - click to Add signature(s)
4e616913-2027-4c5a-bca6-8460ce491039 | checklist | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121) |  | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121)
b2e9c17e-1996-44b3-a41a-28194ba52086 | section | Pre-commissioning Procedures
000fc381-3b27-45a7-a10b-815d730609f5 | checkpoint | Check the location of installation is as per approved shop drawings and manufactures recommendations
c5f39467-c07f-462e-8ede-2c6cc4fa7ab8 | checkpoint | Check the Height of Panel is as per manufacturer's recommendations and in accordance with the relevant Australian Standards
306730ca-1e01-46c2-bbc7-5d57aad9b4e6 | checkpoint | Confirm operation of auto-reset from FIP is wired through GP relay
5a42ae5f-84dd-4d74-8f5e-7a4aad78aede | checkpoint | Check all wiring connections are tight and secure
459ae02b-70ba-4888-95e4-ae1e1e3c0a9f | checkpoint | Check routing of the conduits are as per approved shop Dwg’s
0b4e691d-8878-4de3-93ee-71a338827842 | checkpoint | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks
6d83e6b2-dc53-4de8-a51a-75f979caee64 | checkpoint | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket
ba01aceb-74fe-4fe4-8574-24a6eeba80eb | checkpoint | Check the sensing holes are drilled as per design
91eb25ae-c1fa-46b3-be55-b795811f5446 | checkpoint | Confirm the exhaust has been routed back into the sampling space
e3876482-1754-4a52-b9b4-03361bb93074 | checkpoint | Confirm end caps have been installed un-glued to all pipes at a serviceable height
7654cc32-b014-434f-912b-e3f7746b3830 | checkpoint | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP.
c8e4fa53-099f-4c51-80df-bbfe85ed38d5 | section | Commissioning
69ad6722-0de4-45ed-9c96-0f76841f8de1 | checkpoint | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational.
595d398e-5908-4066-bcb9-60c7be029f11 | checkpoint | Induce smoke into the furthest sampling point from the head end unit
4864c75d-fd83-4975-936e-c2e799abc6d3 | checkpoint | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe
06f5c510-8646-4c05-b97d-02385ada829d | checkpoint | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly.
83e48283-c069-48c8-9f96-70725ddbbfd7 | checkpoint | Remove the power from the VESDA and confirm Fault is received at the FIP
89fb81f0-f1d2-4df2-8248-82df2b9ea19a | checkpoint | Check the fire signal is conveyed to the fire Alarm system and BMS, if required
9cf303e9-784e-414d-b37d-77ba068ef560 | checkpoint | Check the transmission of signals to operate ancillary devices, if required.
298603bc-874e-49ff-9efd-6ed849d534a8 | checkpoint | Record all baseline data as required
fa2063ce-0cf9-4fd4-a60e-0db87dc7907d | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V.160421) |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V.160421)
ce3a9ee2-9d0a-483a-82fa-54df9e673272 | section | Fit-Off
8a0f9043-d07d-41e5-a042-3c6f47aa0da5 | checkpoint | Latest consented drawings checked & referenced
cd2a6eb7-34c4-5abf-be46-861989e96f51 | textbox | Drawing & Revision #
51b69dae-69fc-5851-be9d-80e5eaaeff27 | tickbox | Area clear, tidy and accessible
2c97c8f1-140b-5ec0-92db-10f57823a5f1 | note | Attach Photos/Comments below if any issues & send report to Builder
2053b334-d4fa-475a-9db0-a65f930f7258 | checkpoint | Have all devices been installed in the correct position with no obstructions
144b51fd-0a51-4325-bb5a-5abf1dd69dc2 | checkpoint | Have all detectors been installed in the correct position and addressed
c824d353-c964-4a4c-af7b-5a7a8c88e7ad | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
169a4098-702d-4aa3-a07c-a446c43399d2 | checkpoint | Have all magnetic door holders been installed correctly
fa938e62-edbf-4d42-8928-5f4fd3123ca8 | checkpoint | Have all input/output devices been installed and addressed for security fire trips
dd98819d-b010-4270-956e-c6f25796bc3f | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
fb6d84d9-58c0-4ed7-a54f-6be57a80d03f | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
f3162272-1373-4f67-af17-49aa9c5daae4 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
3429e41d-a166-46e8-a601-12bf6a533741 | checkpoint | Have all cables and conduits been installed in the correct position for devices
462a6095-8325-4439-9d64-b32eb168c473 | checkpoint | Have all devices been terminated for testing purposes
effe3195-05b9-4427-b7e5-6dd446c6805d | section | Cable Feeds
0a2c1823-3a7f-4811-ab4f-2c87c8e86882 | checkpoint | Have all cable feeds been connected to the first device
93890a50-9a53-4989-9e69-45efee4ddb1b | checkpoint | Have all cable feeds been connected to the last device
6a7c4a0c-a7b2-482d-b435-d67698269371 | checkpoint | Have cable feeds been connected at the panel
df3d9a31-ded6-4dad-b56b-60a5d9c09338 | section | Visual Check
6f900232-3091-45a1-8758-50586856b237 | checkpoint | Check that no other services are run with or attached to fire detection cables
093d98ad-0de2-4000-9ec1-c7bab3c2dac6 | checkpoint | Check that no cables have been damaged
20828e3f-4f97-4617-89ca-0831c84b49fd | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
6aeb4e55-d4a3-4638-843b-86af369037b2 | checkpoint | Check that all address tags and labels are clear and readable
98e6cefa-bb97-4f31-9d3a-f4e702fae6a2 | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
1fd05b45-eaaf-46d2-ab76-48c90ac43c65 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
dac10669-b1ba-462b-b151-7f4ebb46c3af | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
dd20d096-0905-4404-996d-50466012adaf | section | Completion
cc0ab093-4d87-43eb-bfdb-088f0c0b97d7 | checkpoint | Works completed to specification/drawings - Attach photos of work below
3bcc42f2-8c2d-59df-8697-65abbcfb511d | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
dc08d80d-f82a-5187-b3bb-329dd5e6c534 | button | Area left clean & tidy | Yes, No
5a623759-4cda-574b-87cc-91137c9eda80 | tickbox | Leemark Sign-Off
06dd2bbf-e904-5fc6-932f-e7f2625a01be | tickbox | Builder Sign-Off
5cfd6968-23be-46ad-8a99-85f462a75025 | signoff | Sign-Off - click to Add signature(s)
01ec9506-7dbe-4129-abb0-efd3eddc1fe9 | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121) |  | LM-FOR-50-ITR-303.1 Fire Panel Installation (V.171121)
6bb57117-d607-4e97-8432-0d0e0c3f007f | section | Fire Indicator Panel
553b29c6-07ed-4b0e-9b90-67b9ad1aabd7 | checkpoint | Latest consented drawings checked & referenced
7f7edae2-26bd-51e9-bade-db3d11bffbf0 | textbox | Drawing & Revision #
da54eb71-681c-5fc9-a496-7aea86a26cfe | tickbox | Area clear, tidy and accessible
0a0af7dc-2bf0-5d3d-9cda-e33dfb7bf274 | note | Attach Photos/Comments below if any issues & send report to Builder
0b902877-fb68-4c2a-b4fc-a198cdc3f556 | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
c1d3081f-729e-483b-9f66-640d1497ffdb | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
fdceb9c4-a8e3-4ac4-991c-6c0221d824f3 | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
3107ee1a-f207-4efa-85c3-f6bad7fc67b6 | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
d85a73a5-93a5-4a26-9956-7062ffae6314 | section | Accessibility
ae1f4a02-d9d2-4fed-a505-41663970f5de | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
a467c0b3-e250-4eec-8173-a93af6b6a644 | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
4c4065ce-425a-44a2-a317-1ed541463e2d | checkpoint | Is the door absent of locks
8df6e816-a515-4d06-84ea-f80fd54e231e | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
af0881f3-3ff7-4878-a239-cea0a5d599f4 | checkpoint | A minimum clearance is maintained from the enclosure as shown
a70a048a-5293-4f3f-90a8-daadb980c747 | section | Power sources
91d893a1-cacf-4542-bbc1-adc495d7d4b6 | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
1ba674e0-89e0-4946-98d8-0a7a5a502804 | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
e0425041-389c-49c6-a4eb-78da83f94004 | checkpoint | The battery is not be tapped for intermediate voltages
a4a18ffd-6999-4a2a-bcb6-46b16da3e28a | checkpoint | All connections are made using suitable connectors
530a5667-428e-42df-bdc8-93359eb6b0d5 | section | Sub-Indicator Panels
70de2157-b9e3-40ae-a145-baa46a0d5efd | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
392687b8-6ccc-5e40-8e9e-7458407b5cd1 | button | (a) The SIP serves the entire building | Yes, No, N/A
cd7225fe-6315-55af-9764-42b2f82237bd | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
c17f0acf-7e05-57ff-b8d1-f39ffb28c073 | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
50da78cd-15a9-5310-9cf0-7c06ae43cf3f | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
b8f6046e-f522-542b-8692-bedd9ba64890 | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
ddc85797-a50e-4a68-8778-57d0e9e37f90 | section | Wiring
291edeba-f982-4d97-8f6c-17d8d5fc0108 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
37b3ccbb-0029-4455-86ab-16fe78f1d9a3 | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
21d77a8c-deeb-4404-adb7-b2a7bb61e2d1 | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
e1fc525a-293c-4006-8eeb-447a37d8fe88 | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
a298bdc2-4fd7-46a6-93fc-d0e86cf85bb4 | section | Completion
91953ccb-b822-490b-bc63-e13db316636e | checkpoint | Works completed to specification/drawings - Attach photos of work below
53e144f9-063e-537a-9744-005213c720b1 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
f360e4a3-abfd-57f3-a42f-6e53333d62e1 | button | Area left clean & tidy | Yes, No
453c3dd3-c41c-53da-b5ba-69a892b67511 | tickbox | Leemark Sign-Off
01b57fa2-3c2f-5f1b-bbb8-e4bfaad0aa96 | tickbox | Builder Sign-Off
3c6e22ca-6ae2-4e19-a588-a765c7dc9c13 | signoff | Sign-Off - click to Add signature(s)
3517ceb4-327c-4acd-a5a2-e7104115a71f | checklist | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121) |  | LM-FOR-50-ITR-303.2 Ewis Installation (V.171121)
90332357-a80f-443c-a731-4e4a7e52b71c | section | Cabling
e6722649-d832-44ad-a227-055b3336733d | checkpoint | Latest consented drawings checked & referenced
97c63483-a9bf-5765-a5ec-cc793051a5f1 | textbox | Drawing & Revision #
06d7243c-bba1-5a12-a67c-c56001c68cf5 | tickbox | Area clear, tidy and accessible
3af647ab-d9ec-5a98-9e6f-77ddf3ec8770 | note | Attach Photos/Comments below if any issues & send report to Builder
e2275427-2d07-4eff-86ae-cbe519ad979a | checkpoint | Have all cable supports been installed in the correct position with no obstructions
1954ee9f-5abe-40c2-886e-b4888cd78d48 | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
3114a0a8-27d3-4e38-8b22-a89bc6c74dfb | checkpoint | Have all cables been installed for speakers and horns
382e5259-3786-410d-8915-ede7e27947fa | checkpoint | Have all cables been installed for warden intercom points
bd5e504b-d992-40bb-90ff-92071a9d6992 | checkpoint | Have all cables been installed for emergency call points
5f5de254-7272-48c8-9976-27e108659835 | checkpoint | Have all cables been installed for strobes
201458c1-0233-4df0-8f9b-1d360dabba3a | checkpoint | Have all cables been installed for background music inputs
acc4aeff-3faf-4364-8f2b-445fef058a97 | checkpoint | Have all cables been installed for microphone inputs
7b989c27-74df-4988-91a0-de1a39d40646 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
31158eb2-3667-4fd1-bad5-5b18b7cdce0a | checkpoint | Have all cables been installed in the correct position for devices
22f1cfcb-8347-472d-8116-f5cd4a3846a6 | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
ac44972a-e49e-4fce-bae3-16cd10c98e75 | section | Cable Feeds
a9bb4df9-abf7-4c6d-b910-f2645b4cf445 | checkpoint | Have all cable supports been installed in the correct position with no obstructions
2c46efb9-757a-41a1-b14b-adbf3d895bb8 | checkpoint | Have all cable feeds been installed in the correct position
04d8b5bd-c814-4c3c-ae7b-6177bb7d8ece | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
b74de259-7b1d-4303-84ef-2fa858d2bc4c | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
e40ea6db-8900-45e0-8dcc-8e46251a68f3 | checkpoint | Have the modified cable trays been re-galvanized
f444a03f-1a81-42eb-86b1-963b5b076883 | section | Visual Check
b74260ec-500d-4ea9-a06d-c9628b6c39df | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
5fb56c9c-f74d-48a2-be2e-fccffd5daea0 | checkpoint | Check that no cables have been damaged
a21a1b85-18d0-4dc4-af7b-c6ebd791a49c | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
c7a07636-df85-455d-aceb-ad994f671066 | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
38c81130-a850-4f86-b1ea-98edc7edaa95 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
487eb9b8-7a14-41a0-83ba-90e9343de26e | checkpoint | Has photographic evidence been taken and recorded for all penetrations
9f446f59-ed8a-4671-8e48-49b94ddf43c4 | section | Completion
c91a1cec-5ce7-4dc4-b7cf-d41e47845c74 | checkpoint | Works completed to specification/drawings - Attach photos of work below
14685e4b-1775-5f8a-997d-e7ddec963eda | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
8efcfd51-4d2a-56cc-a414-321f93f6de6a | button | Area left clean & tidy | Yes, No
9a8d3e03-9636-5584-8a50-c0189692ee4a | tickbox | Leemark Sign-Off
589c09d1-a476-5aca-9eb6-357ecbca1a26 | tickbox | Builder Sign-Off
cd70137b-e422-4a5a-8c6b-f603a0e6d6f7 | signoff | Sign-Off - click to Add signature(s)
95c2a7ed-9af6-460b-bc01-7661deb94100 | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121) |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off (V.171121)
8d8db2fb-daf5-4959-a973-a99ee209625c | section | EWIS Fit-Off
f060c0ec-1029-4b86-948e-3f962c75bd84 | checkpoint | Latest consented drawings checked & referenced
92385a8c-cfa0-573d-9383-d67b453daa4c | textbox | Drawing & Revision #
f448cff2-0490-5176-8858-1396faa26ef9 | tickbox | Area clear, tidy and accessible
db4e3e8d-a395-5f2f-842a-f7a16aedf135 | note | Attach Photos/Comments below if any issues & send report to Builder
d06fb9a9-d69e-41ab-a50c-a997f52dbc70 | checkpoint | Have all devices been installed in the correct position with no obstructions
f03b12d5-a613-43f1-9003-9acf24d31b22 | checkpoint | Have all speakers / horns been installed in the correct location
5d9d42b1-1df1-4414-b609-675e030e47e1 | checkpoint | Have all warden intercom points been installed in the correct location
fe7cffa1-7046-4842-9998-bbec75ecac62 | checkpoint | Have all emergency call points been installed in the correct location
17f3ef39-d74c-44f0-8820-9d5637099ae3 | checkpoint | Have all strobes been installed in the correct location
8c8d5e21-6384-4c2c-97a2-cabbca517683 | checkpoint | Have all background music points been installed in the correct location
370eb34e-20fc-4b59-8d98-51912142182c | checkpoint | Have all microphone points been installed in the correct location
c002fa68-e3a6-4a79-8db9-740c82e629ce | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
7ce213dc-9742-43eb-87cf-afb58415d837 | checkpoint | Have all cables and conduits been installed in the correct position for devices
b59fa027-5567-4c9e-adf2-d99956a59fd5 | checkpoint | Have all devices been terminated for testing purposes
2e15efe9-6bae-49ae-906c-ba39496c713e | section | Cable Feeds
3fd6ec7d-5a62-4705-96ea-67c96a7add04 | checkpoint | Have all cable supports been connected to the first device
fc9d6d9a-a3e8-41c4-a366-d3a734772a08 | checkpoint | Have all end of lines been fitted and measured
406e2c35-a147-403e-8c83-e76c3abc518e | checkpoint | Have cables feeds been connected at the panel
e360f685-d0b5-4e0a-bdf8-892643ff5ea5 | section | Visual Check
3de24487-205a-4488-8d8d-544f1659914c | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
c7d65c72-6f5c-4824-bcfd-25714f7c3cb5 | checkpoint | Check that no cables or devices have been damaged
e7ce3469-fc92-4b87-a81e-cfd4930919e3 | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
f4e0691a-7c6e-40c9-b377-ca6c0c406b43 | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
6fd15379-c1a5-4ce2-90db-ce54a3d37b53 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
72f65b77-dcae-4464-85e9-88f5315a4994 | checkpoint | Has photographic evidence been taken and recorded for all penetrations
293c840e-edfa-4648-a215-8184c8758dd2 | section | Completion
7433483a-8ed2-46ae-9bd0-837b0c05129d | checkpoint | Works completed to specification/drawings - Attach photos of work below
61b8f43f-4508-5127-8410-ed6a7da0e103 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
3e761090-98a5-5e35-b23a-eac1e97100e5 | button | Area left clean & tidy | Yes, No
f2c3ab12-883a-5c00-91ec-476796288456 | tickbox | Leemark Sign-Off
8330483b-83cd-5e65-9c5f-62d1c81588c7 | tickbox | Builder Sign-Off
bdd71e2b-23bf-401c-8aa1-9a8affedf14e | signoff | Sign-Off - click to Add signature(s)
2a74e257-5cd7-4dcc-9a32-00b09cf4de56 | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121) |  | LM-FOR-50-ITR-303.4 Fire Detection Installation (V.171121)
6bacd03c-0492-40f3-b6b9-66ff74e58f68 | section | Cabling
7b1f9eb5-fd6a-45d9-8742-f777c4368afe | checkpoint | Latest consented drawings checked & referenced
6fbff271-109e-5777-9547-b0edbe219170 | textbox | Drawing & Revision #
bdf5879e-00c0-55c0-b542-85a4ca22a3ec | tickbox | Area clear, tidy and accessible
a6923396-5396-5bb8-be16-da84f8810a13 | note | Attach Photos/Comments below if any issues & send report to Builder
44cf56a7-6f07-42bf-a59d-1af9e3a0e63f | checkpoint | Have all cable supports been installed in the correct position with no obstructions
604dd32d-2b73-4103-9331-5d02efe74eae | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
fb109884-ef84-48be-970d-ed2d3c67a31a | checkpoint | Have all cables been installed for detectors
308321ca-49af-46b6-9a95-211b8ac5f61e | checkpoint | Have all cables been installed for sprinkler valve sets
381cebe0-fb9b-439b-925a-7bbdfd5cbe83 | checkpoint | Have all cables been installed for magnetic door holders
0e04feab-f0d4-42b0-be74-f96798c94a6b | checkpoint | Have all cables been installed for security fire trips
f9964cfd-4ba3-451e-8512-852a16146061 | checkpoint | Have all cables been installed for mechanical fire trips
3f2cab1f-cd19-4521-a94a-413b3065238c | checkpoint | Have all cables been installed for AS 1668 Fan Controls
d0bc0a5b-a522-40d1-8225-cfa9d99c2455 | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
6208ff02-a3b1-4e98-8aae-a025f67ced8c | checkpoint | Have all cables been installed in the correct position for devices
1257d795-936b-437d-ac28-3804c791f8a7 | checkpoint | Have all cables been joined through for testing purposes
72de37a2-a3f5-46ec-b4cb-546007a4653d | section | Cable Feeds
1f963707-10d8-4fa3-98ca-0530162aa019 | checkpoint | Have all cable supports been installed in the correct position with no obstructions
b45ae7e6-692d-476e-87dc-d678f646cc77 | checkpoint | Have all cable feeds been installed in the correct position
4a931018-8daa-4a58-bf4d-c836c1feadc0 | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
5a5da104-1f31-49e7-a8aa-869d5c52249e | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
5608fec1-4aec-48d3-b63a-86e221dc0be0 | checkpoint | Have the modified cable trays been re-galvanized
8660ba17-c7e6-44a8-940a-07c20c62edca | section | Visual Check
e1e38489-73ee-401b-af9e-8c5540c33ef4 | checkpoint | Check that no other services are run with or attached to fire detection cables
c3c383cb-fefa-4cf7-aceb-5e3c4acf3a6e | checkpoint | Check that no cables have been damaged
08154971-4a46-4f6b-b57d-b599d4b4fe00 | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
1c13a33c-3f9c-4af8-b8a9-adae722c05f0 | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
b2e52497-dda5-48a9-ad9b-9382b57a8be3 | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
d6d0d5e1-cc84-4678-8c89-bf30efb760d6 | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
d352e86f-1816-4871-9874-86be22ffb9c7 | section | Completion
b67eca91-8ce5-4a98-9c1e-d37030f76af8 | checkpoint | Works completed to specification/drawings - Attach photos of work below
dee85c66-915a-5d47-b01d-a2c6c4e247cf | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
6242d60d-23e9-5b16-8826-9ba4ecc0c6a8 | button | Area left clean & tidy | Yes, No
f84fd2b3-8962-5bd3-9b9f-d31e847431b1 | tickbox | Leemark Sign-Off
30532f31-8599-5cfc-834c-fd7d7c673af1 | tickbox | Builder Sign-Off
647edb0c-5e42-4dab-8116-3ce303b66457 | signoff | Sign-Off - click to Add signature(s)