## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8082c66f-cdaa-4d14-b86f-b25551e5541d | checklist | Document Attachment |  | Document Attachment
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90453b8e-7ed9-4263-b285-bb018486d177 | checkpoint | Please attach document
7dfbe181-e44e-45b1-bdc5-590d3e364540 | checklist | Equipment Delivery Verification |  | Equipment Delivery Verification
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ef426f77-c06d-44df-9d6d-9a391b91de96 | checkpoint | Delivery docket attached or photographed
17dac296-2a82-587f-8f42-3f2252dc8347 | textbox | Report Reference:
d67e8728-0837-5e46-a926-29e10dc7e199 | textbox | Date of Delivery:
50e7307e-5ba4-55a4-b537-fe1a968f8590 | textbox | Manufacturer/Supplier:
39af0452-ae4c-5701-860b-ca2b20e6572b | textbox | Equipment Description:
3c487adf-b619-5683-829e-07ceae851039 | textbox | Technical Approval Ref:
b6a0658a-d439-5f4f-a5fd-5756e11dacd8 | textbox | Drawing Approval Ref:
9ab9a0c3-2588-4b35-9d40-d5a38fe1b29d | checkpoint | Photo(s) of serial number(s)
b68f0b1c-bf7c-4061-8ca8-5bf3877ed71f | checkpoint | Approved by Supplier / Manufacturer
d5014300-8866-4ffc-bb86-7c64967b4a38 | checkpoint | Approved by Subcontractor Representative
81031cca-1046-4d47-a749-5e13d1269522 | checkpoint | Approved by Scentre Group
2c27e42f-0ef1-5178-8519-76f25da1a8c7 | textbox | Date/Time of Inspection:
985fa83b-f98f-41b1-8503-c05b1b357667 | checklist | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld) |  | ITP 1- In Ground Pressure Services - Polyethylene (Fusion Weld)
94909b0d-4271-4476-b924-58e1ff356372 | section | Survey & Set Out Works
eda5304d-c21d-4d83-8cd3-55155ed391b4 | checkpoint | Take dimensions off drawings and record any remarks / deviations
3bcaff08-56a4-4c06-b238-12249719291f | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
0829e0ae-291a-4380-8e07-4a94f6fa61fe | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
19cfb182-5c13-4f39-bb33-6e6ce657869d | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
e8425890-104f-4534-829d-96b30f462d9a | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
3d9359db-a0ae-410e-bd2f-dfeed8bbec0f | section | Excavation & Bedding Materials
ebc8729b-29c8-4d46-9d03-ded3a5ef6610 | checkpoint | Dig trenching to required depth as per AS 3500 minimum cover requirements
3e61b769-7000-464e-ae70-ab5887369346 | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
7eca74bd-907e-49ec-a16b-f7f119feda4a | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
d2d650c4-ba74-4f52-b817-23c6e8210481 | section | Install Pipework
41644829-8879-49b8-b79f-57f17959978e | checkpoint | Ensure that the pipe to be fused is the correct size for the electrofusion fitting being used
7900360d-1760-46cc-891b-0b56923b7978 | checkpoint | Ensure correct fitting is being used and leave in packaging until ready to install
5be83e4b-dfa1-4a9f-9af5-105a19039d3a | checkpoint | Cut the pipe ends as evenly and squarely as possible using made for purpose tools
36d23b42-8712-438e-bccd-78bde7fc6438 | checkpoint | Clean pipe end with isopropyl alcohol to an area that is at least 2 times the full length of the coupling on each pipe end
b73126d2-119b-4c34-be92-19c6c15479db | checkpoint | Scrape pipe end to an area that is at least 2 times the full length of the coupling using made for purpose scraping tool
321034a7-5bb9-46fc-a33e-b29dbce96fee | checkpoint | Ensure proper insertion depth of pipe end into electrofusion coupling
c8e7750b-9f87-42e6-8377-41b378f3e48f | checkpoint | Use assembly clamping if required
323d8090-7daf-426c-89b2-03f380f61876 | checkpoint | Complete weld as per welder/ manufacturer steps
f9478da0-e20d-44af-ba0a-db8bfb47bb0a | checkpoint | Ensure proper observation of cooling time
342405f1-3af4-41e7-9cc5-f1a380a8d638 | checkpoint | Use trace wire for plastic pipes
6d35db66-fa3c-4b27-a4ed-203a835fd4ae | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100 mm Spacing, 300mm for non potable
d33f0a3a-9462-4fdc-937b-dbb2cd682e06 | section | Test Pipework
1083297e-e7c6-4771-af52-096e21252e60 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
104aac43-1983-4b7d-a133-312eefc2446b | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
3e82a5ae-2cbd-4734-8ddd-17e18be990fe | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
a19c2a29-1fdf-47b7-8516-9490f1358e4e | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
65c9f269-0c3c-4175-a0d6-b0eb0be7ac7f | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
f0212904-ad64-4d7d-8214-2406649d8d24 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
537a4c2a-51da-4e4c-bc65-c5b9f0e29f50 | section | Inspect Pipework
0a837f8d-b242-496f-a6e2-0b7cc90a2141 | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
c9756a67-eab0-48c6-bf32-7932ee1b09f1 | signoff | Work verified by Scentre Group
429a8b0d-ff04-43b5-8fbb-3f0d276c052e | section | Backfill
6cf2f19f-987d-4849-b6cf-663d52ac5992 | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
8796e6c2-6903-4e8b-90e9-fc48b06d70d8 | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
33b69412-8d46-48e9-b17e-531e07a5ef67 | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
5c99bea1-23cb-4be5-8c64-8173799ea15c | section | Photographic Record
edf63ec1-c7bf-4972-9a96-ac4e7ba0e4b5 | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
b990b10f-ce19-4f4e-a4f9-f4b0204fb087 | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
2a85a354-dcfe-4d0f-85a8-0b4dcc6a264b | signoff | Work verified by McPherson Plumbing
942bb644-be9a-42d9-8cb1-81c4f2f4d0a3 | checklist | ITP 1- In Ground Pressure Services - Pressure PVC-U |  | ITP 1- In Ground Pressure Services - Pressure PVC-U
08edde21-de4f-4a41-a6e6-b4d0e50da13f | section | Survey & Set Out Works
49ee8321-1644-47a9-a0ab-dd28886216cc | checkpoint | Take dimensions off drawings and record any remarks / deviations
e4f47917-44b8-4456-b792-b3e2d1751906 | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
e0787ce6-17f4-4d82-9ca4-1b78819f7948 | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
b84ef708-2cd5-418f-acbf-f3b621cfe447 | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
b8523850-0296-49b0-ace1-6d5417d999db | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
f719bd14-39ed-45fc-8107-7e26c7b39656 | section | Excavation & Bedding Materials
100e5fed-97de-41b3-be09-38fad14692b9 | checkpoint | Dig trenching to required depth as per AS 3500 minimum cover requirements
6e4b6bcb-4b2b-4de4-a6c5-ab679308bada | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
87679695-f273-4d2e-b973-192052ed5b64 | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
2cef12a4-a588-4694-bb0f-f545f050ee12 | section | Install Pipework
fd9164af-b86a-4e2a-8d98-d2501b3c377a | checkpoint | Accurately measure length of pipe & cut square. Deburr inside & outside of cut end
99d47c3a-4cbf-4cac-bef8-5c4cf91b5fff | checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type P solvent cement
e0ff70c9-6988-4583-b3c7-bbf7417fe835 | checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold for 30 seconds
06958250-d990-43f5-aef2-00e7acd2a49b | checkpoint | Do not disturb joint for at least 5 minutes
a877aa2d-f0bd-4154-8f0e-5692904b04c2 | checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
e14559da-3881-4d27-9844-617bd0494e45 | checkpoint | Use trace wire for plastic pipes.
36237304-1fbc-4ec4-9715-bf0662d503e2 | checkpoint | Lay pipework on bedding material ensuring no sagging in pipework. Multiple pipes keep 100 mm Spacing, 300mm for non potable
9ab518f2-b494-4cf3-b937-a5f51a655e06 | section | Test Pipework
5516fa18-9b8c-45f4-92db-c4361346f7b2 | checkpoint | Please take a photo of plan title block to be taken. Ensure plan number & revision number visible
54a16218-e200-4645-8f66-66d535e37c68 | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
fec85ac3-3028-4831-9bce-228b0a1a2f26 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
f9a67242-8419-4301-a95a-3a36286e76c6 | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
8ca3d9ab-2838-4c0f-9e59-a57214cbbcef | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
70db6372-ac59-40b5-b7e0-080d922e3634 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
d6b4321c-ffab-46f3-836d-e8cbe0578ccb | section | Inspect Pipework
4be21a73-4ec7-441f-863b-5e4b6fa4265c | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
fe403dbd-e234-4098-8bce-39d7602adca9 | signoff | Work verified by Scentre Group
1a05e07e-07dd-4766-aaed-906a1dd21e21 | section | Backfill
93d05ade-88d2-47a6-b270-9f419cca877e | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
a7c977ab-568a-4068-9f79-12e784f8b857 | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
0bdb136b-5033-470b-9cfc-574c2dceb91f | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
9333e712-0d95-4277-bb25-b889f8487c4b | section | Photographic Record
aac60dc3-06c3-4949-8578-d3bf1af07e8d | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
6ddf377a-9875-499f-be68-1f544c7454d5 | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
36fc8298-a46b-40c2-8068-53f668d54a95 | signoff | Work verified by McPherson Plumbing
5db525c7-2c37-4e34-bcfb-6ee1e9791464 | checklist | ITP 2 - In Ground Drainage Services |  | ITP 2 - In Ground Drainage Services
c3db94e8-5fe8-4938-a4af-4580eefc1a49 | section | Survey & Set Out Works
e70c2663-9580-488d-95df-d6f6b90f3644 | checkpoint | Take dimensions off drawings and record any remarks / deviations
a4262970-42c4-40ce-bd6b-eb0d3223a087 | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
662a2e40-5543-4705-aef1-74b1d424461f | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark trench line
d2979262-5327-41db-bf0e-0274e83ad3b4 | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
53388298-0f53-4ed9-b49e-db21db6dced9 | checkpoint | Please take a photo of plan title block . Ensure plan number & revision number visible
27013773-d12b-4d4a-a6a9-02ee3a77e309 | section | Excavation & Bedding Materials
a26f12e8-3391-4e2e-b4ab-d2e7d9bbe2a2 | checkpoint | Dig trenching to required depth as per AS 3500 minimum cover requirements
d1fe9df5-9446-41e6-be34-bef6a7a57a22 | checkpoint | Ensure minimal over excavation (minimum 75mm below pipe invert)
621324be-5c51-4592-ad06-85cb45f05d56 | checkpoint | Lay & compact appropriate bedding material to required thickness, providing a consistent level surface
c16757b6-dfb4-40bc-b208-f907914a18a5 | section | Install Pipework
bae38a15-5e40-4fdd-98e2-7f29352394c7 | checkpoint | Lay pipework to appropriate invert and ensure correct alignment. Document inverts on As-Built
ed5bdbd7-8949-5297-8177-277b8d7cc62f | dropdown | Type of pipe | DWV PVC-U, HDPE
1c40b8d3-9c10-59e8-91f3-571d72f000e8 | dropdown | Inground Services Type | Sewer, Trade Waste, Stormwater, Rising Main
9734aa73-fe32-4606-bd3c-a6d486cd516c | checkpoint | Ensure pipe is scrapped with appropriate tool to expose bare pipe
53170c01-078f-4419-9687-1445c8d026af | checkpoint | Allow for all required inspection openings at change of direction and not more than 30 m intervals
426cc32f-6393-4d3f-8358-7253041afaa0 | checkpoint | Install turn up points as per grid Set Out or surveyor markings
e2bb3085-dd7b-4ded-8eb2-064df29cafee | checkpoint | Ensure required depth of cover and proximity from other services is achieved
216a1fed-a9c0-4b9b-b92c-173729fbbc51 | checkpoint | Belly Fill Pipework to keep in a stable position, but still visible for inspection
a5bc9397-c18e-408e-bb9e-469fab1fe142 | section | Test Pipework
b306c468-bea3-4765-9322-4822046c7405 | checkpoint | Photographic record to be kept of process. Take photos of water level before and after
83db2c6c-8038-4412-b827-486009f791dc | checkpoint | Hydrostatic test of pipework for a period of not less than 15 mins
51a1e2ef-a804-41c2-a531-19778919691e | section | Inspect Pipework
a70b5c70-6487-4f13-b2cd-2a46c7201f2b | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
215914ea-94d9-4113-b289-0801211cc45a | signoff | Work verified by Scentre Group
e6f2336f-471f-4211-9434-59a1aebdf7a9 | section | Backfill
5f94868b-f1de-4d5e-b983-56c8c6264e21 | checkpoint | Backfill pipework with appropriate material (sand/fine grained soil) not less than 75mm above the pipe soffit when compacted
b01d2ece-6632-4a85-ac6a-80c2283659e6 | checkpoint | Place layer warning tape that identifies the specific service 300mm above on compacted backfill directly above pipe
2f695781-d602-40ad-86f6-83269c89724f | checkpoint | Complete backfill in layers with appropriate material to existing ground level ensuring compaction is achieved via mechanical aids
528678e1-4218-42c8-a792-0b9985bff506 | section | Photographic Record
8fd34caf-7059-49ca-a1a3-560413d62e82 | checkpoint | Photographic record to be kept of process.Photos to include pipework belly filled and once overlay material installed
6fa63b13-9f58-4b18-a5e3-b4084be9c4c8 | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
d90856c9-b7f3-4605-8f8c-74628c46c611 | signoff | Work verified by McPherson Plumbing
ec5f79e0-33b9-434e-9203-88c65e38f271 | checklist | ITP 3 - In Ground Pits & Tanks |  | ITP 3 - In Ground Pits & Tanks
449f235a-2763-4349-b0c7-065ed4236000 | section | Survey & Set Out Works
c1a622cc-3668-4e98-9423-13d012e87281 | checkpoint | Take dimensions off drawings and record any remarks / deviations
11e15fcd-17d7-46ca-962f-a65c55448c88 | checkpoint | Review Dial Before You Dig information. Ensure not more than 30 days old.
d3ca23db-c84f-404f-b4ef-823cab22f1f7 | checkpoint | Refer to dimensions on drawings & note any changes. Clearly mark pit location
443fd8db-645c-4f79-8915-404fc9706b15 | checkpoint | Inform all personnel of existing services and mark with appropriate coloured paint
54d1fbcf-3fb6-461a-82ae-b850a4218abd | checkpoint | Please take a photo of plan title block. Ensure plan number & revision number visible
08fc3631-17d5-43a5-9028-952966409957 | section | Excavation & Bedding Materials
ab7be2ef-99cb-434d-a97c-abb4c82eb27b | checkpoint | Establish invert's & RL's and excavate to required depth
3e60e964-e1a9-4377-9156-b95e15bcce90 | checkpoint | Ensure minimal over excavation and as per tank/pit specifications
8373a772-f533-448b-9e9a-06f443123ea6 | checkpoint | Lay appropriate bedding material to required thickness, providing a consistent level surface
137403e3-e67a-4c10-82fe-ef525033d740 | checkpoint | Check bedding level to ensure that it corresponds correctly with pit finish height
8d27c6fd-5ee0-4f1b-8f37-b3d36774cc8f | checkpoint | Ensure required depth of cover and proximity from other services is achieved
2a575d3d-d073-4dd2-90cb-393318a06496 | section | Installation of Pit & Risers
fb61be11-039a-4b5a-b99c-d263b88ab124 | checkpoint | Lift in pit to appropriate level and ensure correct alignment as per plan. Document levels on As-Built
67d018f1-7abe-5455-b0af-eff43755b77a | dropdown | Type | Concrete Precast, Fibreglass, Plastic
47f58f0d-6c9f-4e8d-88c5-33e16190f72c | checkpoint | Seal pit and riser/ lid segments together using a site-approved non-shrink grout or mastic-type product
fb5cfd6a-c70e-4cc6-9d45-f1454bc715fc | checkpoint | Leave the segments undisturbed until the period of curing is completed
aafa68d0-be53-4bf2-b426-5146ce3fb59b | section | Installation of Pit Connection Pipework
9c7d4bb0-c31b-440f-8a03-806ffa1307e6 | checkpoint | Establish pipe invert levels entering the pit and mark out on the thin knockout section of the pit wall.
226feb6f-4fd9-4021-893e-9fe73a0322b5 | checkpoint | For concrete pits break is to be made in the centre of the knockout carefully widening the penetration to suit the pipe size
b53e512e-486f-4150-8a69-a5b7b08cb22d | checkpoint | For fiberglass pits/tanks use hole saw to suit pipe size
33def25b-75e9-4050-8216-97eff6cd57de | checkpoint | Pipe to be placed into the penetration and cut to the required engagement within the pit/tank
e6d22b37-33bd-4c65-be1f-dbd51890ce77 | checkpoint | Seal outside of pit/tank wall around pipe connection with cement mix or approved sealant
38bf080e-c1d2-4cfb-a0ee-2efef06df015 | section | Inspection
df31ff88-9e00-4327-97c8-60dec07e61a8 | checkpoint | Complete all required inspections by third parties (client, authorities etc) Name/Sign
51366338-9f2d-4e5e-9753-66de789a84af | signoff | Work verified by Scentre Group
fd041b6b-e4b8-42e7-9ad7-f8bbee7ab6a3 | section | Backfilling
0551e1d3-934c-4f72-8f76-f170e935acf5 | checkpoint | Backfill around pit sides with the same aggregate/ material that was used for the base of the pit/tank
08e1e47c-3a82-42fa-acb3-9e3ed36a452f | checkpoint | Complete backfill with appropriate material to existing ground level, ensuring that suitable compaction is achieved
1f044895-9131-46c4-b64c-70558b0d82ce | checkpoint | Photos to include backfill material around the pit/tank and the connection point
85697e1f-608a-4d92-9a96-c6f635fc62a5 | section | Pit Finishing
46524a15-d5c7-422e-bed5-a4db7f4a5600 | checkpoint | Seal inside of pit wall around pipe connection with cement mix or approved sealant to obtain a smooth surface consistent with pit
04244c53-b17b-4684-8303-a7bb747f3580 | checkpoint | Installation of step irons or ladders if required
5659772f-456f-4da6-b180-828eeaf7571d | checkpoint | Provide protection of lid/grate gatic lift points or threads during construction period
12fc5667-0342-4f52-b667-f473d01b9611 | checkpoint | Top the base of the pit to match the invert level of the pit outlet pipe where required. Record pit invert level on as-built
d939ca61-f47f-4346-9bb3-ae00ef87ab93 | checkpoint | Photos to include pit finished & clean and free of debris/construction rubbish
cc370c74-a486-46a4-a363-d62e9a66f4ad | section | Photographic Record
6586e5f8-fc0d-4546-9452-bfef6eada6fd | checkpoint | Photographic record to be kept of process.Photos to include entire installation process
aa2d2dc3-718a-4665-8444-b92da0b0e0a6 | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
c61f67a5-99fa-4502-9de3-8dbb69521703 | signoff | Work verified by McPherson Plumbing
26a9db6b-452b-4001-8550-cea442ec99b6 | checklist | ITP 4 - Set Out - Penetrations & Fire Collars |  | ITP 4 - Set Out - Penetrations & Fire Collars
a8e17721-1104-46ae-899f-7e1345e9b0b2 | section | Survey & Set Out Works
2120a661-cd53-46c7-9767-b670a170e185 | checkpoint | Take dimensions off drawings and record any remarks / deviations prior to installing
1b7d1915-324a-5520-9f0f-09281839bb6b | dropdown | Set Out | Survey Plotted, Manual Set Out
212f2753-afac-4899-8a3d-75d321dadfda | checkpoint | Photo of title block to include drawing number & revision
d305193f-3cf8-4882-9335-8243bb7ebb0c | section | Structural Interface
a4591699-f17e-4227-86c5-329deb6ed8c8 | checkpoint | Consult structural drawings to ensure no structural effect with penetration or cast in position
708ac6e5-3d57-410e-b167-6693caa746d5 | checkpoint | Ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings
db246e5b-13db-449e-8fdc-ae7b3c1d48a5 | checkpoint | Check that penetration does not clash with elements downstairs e.g. Walls, Beams ETC
cd351326-8bc8-41b5-9754-6a40deef886a | section | Fire Collar Installation
a0c83ab4-c926-4f6a-a1e5-a83c22c04d21 | checkpoint | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable
9c48a942-3008-515a-99e3-b21f16a5bf73 | dropdown | Fire Collar Type | Promat, Snap, Hilti, Other
fd2e6214-b184-4490-8d50-8fefb956d40e | section | Pipe Insertion to Collars
34f3a200-4df0-4a1f-8fb1-93c047b02d89 | checkpoint | Ensure pipe is fitted correctly
8d398997-3a22-472a-9982-d9e1a8fff727 | checkpoint | Ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. Pipe is easy to knock through
c868f8af-9644-46c3-a971-41ef37e45838 | section | Cast in Conduits
be9dbc2c-0ef4-406e-8712-18df9852dd7c | checkpoint | Ensure conduit is within wall or carcass range
7ef915bb-ccdb-441d-8467-7a9d9df59476 | checkpoint | Use 15/45 degree bends on all changes in direction
d0e93e54-0d42-42db-ba8d-3eaff3888495 | section | Cast in Balcony Outlets
edf11236-bdf0-49f4-9309-5430c6736450 | checkpoint | Ensure pipe is supported correctly without affecting balcony soffit
5fd0949e-7ac4-4a7e-b8c7-165d8514a140 | checkpoint | Ensure pipes are not damaged after top steel and set downs are installed.
0b799b27-7c33-4bac-826b-629eadfe3d5e | section | Safewaste or Puddle Flange Installation
63fce252-3182-41a2-a764-55ee8b445a20 | checkpoint | Ensure safewaste or puddle flange is installed to all required outlets
11e0af75-05e0-4cfe-8993-cca26424abd2 | checkpoint | Ensure safewaste or puddle flange is installed to the correct height
34c8acd0-fcab-4186-ad06-89ff2823317c | checkpoint | Spray all floor wastes to identify falls
58e16c46-6633-4b68-92be-995b2782dc7d | section | All Pipes & Casting Capped & Supported
d1d676c3-bd7e-4aad-b4f9-0d4951ca5cb5 | checkpoint | Ensure no open ends by installing dust cap or duct tape on risers
f7118b4d-554e-48ab-ae3a-80a2e2491612 | section | Pipe Sleeves
3ed1a035-bc5b-441f-b86e-838ff64a3bc7 | checkpoint | Ensure all sleeves installed in in situ walls at the correct height
6c749503-4b1c-4aa6-ae5b-a2ccdce4804a | section | Castin Downpipes
9fdf2746-99e3-4d81-9f9d-2e8f1bac9a3d | checkpoint | Ensure pipes are clear of any obstructions prior to extending riser
0f7bbf15-2b3e-40d6-bf77-e3ab0097fe85 | checkpoint | Ensure pipe is fitted correctly where agreed by structural engineer
5e96b90a-7927-4aed-9f5e-857e7ab0ce1a | checkpoint | Ensure pipes are wrapped where required
72d61f31-1b1f-4bd7-bcf1-1a69d7bc6f1a | checkpoint | Ensure downpipes capped and taped to riser
2a6361c7-690c-4587-8341-0e26eafaaca4 | checkpoint | Ensure pipe is filled with water for concrete pour where required
ff98d2c0-1327-412c-9459-886eb0a96de5 | section | Inspect Pipework
28046787-796a-4925-a490-28f759238c68 | checkpoint | Complete all required inspections by third parties (client, authorities, builder, etc)
baa67e3c-f7aa-4a9e-80f3-1314f0dac011 | signoff | Work verified by Scentre Group
2210d071-9e7d-434a-b00f-4e4c22ab799b | section | Photos
b7a686a4-06bf-4b83-8ba9-158752ed866f | checkpoint | Ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour
1933f8b0-353c-4e1d-86ec-bc31396ce375 | checkpoint | Works verified as conforming (McPherson Plumbing Representative) Name:
78c73295-eb47-4bbe-affc-add313113f8e | checklist | ITP 5 - Drainage Services DWV PVC-U |  | ITP 5 - Drainage Services DWV PVC-U
f00a9abe-d3ae-48cf-a4fe-3319864306cc | section | Setout & Location
220f75d5-e41d-4cd9-8ad3-614e17329f0d | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
c18b8d48-0ebf-48ec-958f-1b4097ac2ea1 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
2e309afd-858c-4b21-8372-0cfe66975738 | checkpoint | Review interfacing services and ensure no clashes
dbc1ff63-a514-4a61-8e60-a5116f2ebc3d | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
64ee5213-b6a2-4e1e-ae86-9ca0552d5f9f | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
a10fb1df-be09-5c5e-a8d9-5bc057c7559b | dropdown | Pressure Services | Suspended, Rough In, Risers
c45d0b98-3e06-5036-a913-5ef1336f0019 | dropdown | Type | Sewer, Stormwater, Trade Waste, Rising Man
6b64d198-a8a1-4de7-b69e-02315f7cb1af | section | Bracketing, fittings & Noggins
959c20ff-d42c-491b-8baf-16a5837222cb | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
8bda8862-15da-45fb-9ccf-d7013f85223f | checkpoint | Ensure correct brackets are used dependant on material selected
cda23918-c26b-46a0-9fa7-42ad2b73e4cf | checkpoint | See extract from AS 3500.1 for water services
0af486a6-291e-4bd1-aacf-1c9ec2020605 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
ed73cee0-3b3c-4376-9c87-45d628301440 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
fa637e04-73c0-49b3-b8ca-8abc8eba75d7 | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
fb9d37e2-c9b5-40ba-be7b-e5a548896f68 | section | Install Pipework
cde465d4-28f1-4a7d-8ede-8061f3528076 | checkpoint | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end
2ae6104b-e858-43f6-97aa-e5538512811e | checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type N solvent cement
7e20ddf0-befd-432c-bc02-e653bfd815ea | checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold until joint sets
72cbd570-bd0e-468c-ad67-52f2a2b01092 | checkpoint | Do not disturb joint for at least 5 minutes
80aec070-2091-4f96-b74e-710a0b0a3e91 | checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
84d471b3-99b7-4bc0-b496-02222388b323 | checkpoint | Allow for expansion joints & inspection openings as per as per AS3500
7bacc9d4-331e-427f-b60a-97c64969579f | section | Test Pipework
5e56d05f-b63f-4d89-a3b0-fd7bc5848363 | checkpoint | Plug and fill stack with water at expansion and gate and ensure plug is unable to release into pipe system
2beeaa32-a638-4d85-85c4-1bf50b03b5ce | checkpoint | Gravity test of pipework for a minimum of 15 mins
018825f1-43fb-4a50-bd50-329584efc059 | checkpoint | Tape gate and expansion and initial cap with date, stating 'TESTED'
1aa4ed20-57eb-46dc-8249-a9e4f635030d | checkpoint | Photograph of riser clearing showing testing info
7579f4e2-35e3-4ec8-be64-005aa6cef82b | section | Inspect Pipework
e347880a-660b-4d66-bc10-c06166e37be7 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
5d30c466-8117-4fb7-b509-98759ab4b7b2 | signoff | Work verified by Scentre Group
3c3653ec-e4c3-4509-a62b-479156c5c49f | section | Acoustic Installation & Pipe Identification
afdbe8e5-4a7c-4904-8989-9d38f5f14120 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
b78059a0-aea0-4f03-8d39-3c987b8ff5f6 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
ad1470e7-e807-4c2c-b18c-36556bcf54e3 | section | Photos
8cded8eb-3026-4d96-9df0-2bb1d1bb7e4b | checkpoint | Photographic record to be kept of process. Take photos of entire installation
91ed606d-4081-4f4f-82e7-d943bcf4b432 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
29cbfa99-2c66-4a73-9fbf-d321b4937ebb | signoff | Work verified by Scentre Group
aa48a2b9-8750-413f-9f68-d4695e94510c | checklist | ITP 5 - Drainage Services HDPE |  | ITP 5 - Drainage Services HDPE
cc3d6daf-6a96-4743-a1f1-34c5f2d1a0e1 | section | Setout & Location
68c1609b-cef4-49fd-b780-1d99ea87db1f | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
342a2cb4-78bb-4008-ab05-ed317d14b03f | checkpoint | Review wall set out plans and ensure pipe passes through wall square
12c6348a-af95-4cc0-be9f-7420b843a586 | checkpoint | Review interfacing services and ensure no clashes
f476def6-2a7c-43c3-aae3-f72c40b83d6f | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
1bed0b26-41e5-4624-b5aa-98b13bebb0d9 | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
a038bbe6-a22c-5e25-ab03-72c7ff330c82 | dropdown | Pressure Services | Suspended, Rough In, Risers
396f1eb3-5498-5b4d-852e-b7cdc9eccba6 | dropdown | Type | Sewer, Stormwater, Trade Waste, Rising Man
7a775b90-0905-45ee-b2a9-a29260a21040 | section | Bracketing, fittings & Noggins
dd1c57c8-2cc5-48cb-a122-e6bd738b7b12 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
b8c6bc87-986b-4c46-bb9e-b5c15f7d7e68 | checkpoint | Ensure correct brackets are used dependant on material selected
0d1be5aa-b365-4748-a123-154001188da7 | checkpoint | See extract from AS 3500.1 for water services
99b2b645-22d7-4010-be39-476d194b8b52 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
e3518e18-d6fb-4f49-a368-29a4d33ddc42 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
d59bc628-e305-46ee-b2a6-2e4f2e542d47 | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
2becb9c0-4b6b-4e8f-a720-8173b6bf6973 | section | Install Pipework
973c7d61-e19f-46f2-bff9-c825b929985c | checkpoint | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end and ensure pipes & fittings are dry
ac86a40b-1ac5-4eec-8e2e-e19485784fc0 | checkpoint | Ensure constant power supply to the electrofusion welder as fittings can only be welded once
c384236e-3323-45c8-ae43-d503302410bc | checkpoint | Scrape the pipe section to the length of the insertion depth with emery cloth or manual scraper, removing oxidised layer
eb85de2c-93ef-4947-a7db-9ef1686a9fbb | checkpoint | Mark the insertion depth on the pipe and insert into the coupling. Ensure pipe is secured from movement
70bae5a1-ce74-43db-aca6-817bfd2dbe78 | checkpoint | Weld the joint to the manufactures process and allow to cool before applying force or testing.
1386698c-a932-4ec6-86f2-1058d61d5ec9 | checkpoint | When welding has been performed correctly the protruding yellow or black indicator should be raised
63797473-feb8-419b-9627-85af9d46b1d8 | checkpoint | Allow for expansion joints & inspection openings as per as per AS3500
763d6db3-eb94-48c9-9d9e-699ec4ac17c8 | section | Test Pipework
88e66a81-77e3-410f-a57c-b1da1eca7c7f | checkpoint | Plug and fill stack with water at expansion and gate and ensure plug is unable to release into pipe system
df946b17-2148-4719-9c79-3f9b1eef26d6 | checkpoint | Gravity test of pipework for a minimum of 15 mins
35f4720d-8a50-48fb-b233-5d5e4f5110a1 | checkpoint | Tape gate and expansion and initial cap with date, stating 'TESTED'
582728be-d768-4284-8993-b496c2aa3751 | checkpoint | Photograph of riser clearing showing testing info
514627db-1061-4d56-8967-a24afce8519c | section | Inspect Pipework
15ca2914-fa31-4c3a-839e-20c865efd1e6 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
057f278d-826f-411a-9594-a2a47ec44d1d | signoff | Work verified by Scentre Group
92878255-4e4b-4e5b-923c-6b856dff2f1b | section | Acoustic Installation & Pipe Identification
29df9b3c-1afb-4e42-9de1-1cc8b332b4fc | checkpoint | Apply correct pipe identity stickers to indicate flow direction
22208392-cd32-4790-b269-0f90fe5895d8 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
78218eb7-c20d-4247-8975-c1b8bc85796e | section | Photos
136900eb-667e-4e2f-beb2-1edec9916c8e | checkpoint | Photographic record to be kept of process. Take photos of entire installation
cb7888cb-b563-4acd-813d-2e80d14d79ae | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
2e43170d-94f8-45a7-80ef-90f485025862 | signoff | Work verified by Scentre Group
90ee9edf-4aeb-42fd-8db1-ba9955ea90c2 | checklist | ITP 6 - Pressure Services - Brazed Copper |  | ITP 6 - Pressure Services - Brazed Copper
28362452-2dec-45d2-953b-191b88540c4a | section | Setout & Location
4fb39152-584a-41fe-9a98-5e4e24da7544 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
0e3e33d0-3c6f-4b95-ad32-bd8c49e988a8 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
ddb47e7a-d726-43c6-b293-ff1b6c5678dd | checkpoint | Review interfacing services and ensure no clashes
557729ef-a188-4f81-bd25-770ab69622ee | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
e1486ae5-f9b5-459a-92c9-366f353fd56c | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
ece26421-3c5b-53cc-868f-0057331d9595 | dropdown | Pressure Services | Suspended, Rough In, Risers
3bc2badf-43b7-57ee-9815-770f82bdf921 | dropdown | Type | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
1fdc6d35-2f21-460c-9222-ff4be304ed0e | section | Bracketing, fittings & Noggins
ac04093f-bd91-4a81-aebc-a51d22aaee3c | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
a798be67-2bad-42b7-9e1a-d35e7d7f0a8c | checkpoint | Ensure correct brackets are used dependant on material selected
ab28e8ba-3769-4800-9c60-ac983b6f4331 | checkpoint | See extract from AS 3500.1 for water services
e4555ac8-50bb-4abe-ba9b-549cc1733614 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
d86caf0e-1d83-4e2f-b54c-79d2d156034d | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
b67ec274-9d2c-4e5b-a618-763c84979b35 | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
722bac52-8cf0-4d36-a142-9f9aaaf75fdd | section | Install Pipework
29817b8e-0e6f-4a9e-9f96-224e5a714e72 | checkpoint | Measure accurate length & use appropriate copper tube cutter to ensure a clean square cut.
ae8bf885-f7b5-45fc-880d-ad0ff82def1c | checkpoint | Ream inside & outside of cut with reaming tool or file & clean with abrasive cloth
67d5917c-548f-420d-a889-6954d93749d2 | checkpoint | Ensure pipe is pushed in to full insertion depth. For brass to copper joints ensure flux is applied prior to insertion
478a6d47-336c-4344-adf6-07c56c82eb77 | checkpoint | Weld joint with correct amount of heat ensuring capillary action throughout & correct % silver solder is used. (min1.8)
19bfce7f-19a4-4ee8-8fee-703e75827d1e | checkpoint | Allow joint to cool naturally. Shock cooling may stress or crack the joint. Wipe off any left over flux residue
f919333e-1754-437e-b74e-f56276e3894c | checkpoint | Inspect the joint for soundness and pin holes
7c15ec5f-377c-4610-aebb-9ae118bb2bb9 | checkpoint | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework
66fbd944-107b-491f-bc8a-42092f8d2c6f | section | Test Pipework
cedc9f86-7a9d-4c1a-a48b-c1269d2e4c95 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
3f392617-4b15-4f09-be61-41ca9200af85 | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
6823f8ad-8e8b-4d2a-9e4c-65bb348c5630 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
2a3f2261-3a1b-4ef4-8daa-8de9c54cd4bf | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
a091ce0d-d58c-4aab-a016-52d5674509ae | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
001d060e-8127-426b-8ee2-b9ce5491b0f2 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
c3df78dd-e1d3-4e66-8ceb-bdb9769e9c30 | section | Inspect Pipework
982d3f49-7985-415e-9696-9613c66bc4f2 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
d34689f6-f7f3-4c9b-987f-23f98306a101 | signoff | Work verified by Scentre Group
af447046-81f4-4a3f-b148-3c6cddbdf12c | section | Pipe Insulation & Identification
215df49e-b7af-48c5-a961-3574333f757f | checkpoint | Apply correct pipe identity stickers to indicate flow direction
9650db0d-57a4-4a83-a203-b532fdd009c9 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
293b4fd8-6f1e-4ebf-bcd8-9c8c22740b94 | section | Photos
d8e953e6-b96d-4f00-999b-a41c28eef505 | checkpoint | Photographic record to be kept of process. Take photos of entire installation
f940fd29-be2d-4f97-bb64-116613da1fce | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
c42fe1ef-e270-47df-b007-182bf94534cc | signoff | Work verified by Scentre Group
cae5d199-4a14-4f45-be0c-fa34470c06be | checklist | ITP 6 - Pressure Services - PEX All |  | ITP 6 - Pressure Services - PEX All
de006e90-1e72-4f19-9ff3-1f41ac08804d | section | Setout & Location
fc7dac2f-8a2a-4867-83db-a841dae7a943 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
b1fc6059-f5c8-4d0d-ad2a-03f0321079ac | checkpoint | Review wall set out plans and ensure pipe passes through wall square
f13b0414-283a-437e-88cc-af89bcaec47c | checkpoint | Review interfacing services and ensure no clashes
78c788ca-572c-45fd-a914-83784e6bfc9a | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
b7333682-e0a0-46af-bc61-fcebf8091be3 | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
a38cb26b-3e13-5027-b614-f817a5c217dc | dropdown | Pressure Services | Suspended, Rough In, Risers
eb6ba2b9-87af-5c35-84a1-d410b8a16e7d | dropdown | Type | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
238f4952-2685-4b7f-91ce-99244cc73f70 | section | Bracketing, fittings & Noggins
f0fbbff9-b34f-4598-8d4e-290227fc6803 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
1bfd580d-5eb8-404f-aa8e-d0c8a101a4f9 | checkpoint | Ensure correct brackets are used dependant on material selected
9f5f61df-0767-4f64-8ed7-3592f200235a | checkpoint | See extract from AS 3500.1 for water services
8e9020c4-1624-4478-a0ff-bd135669da22 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
ed0da45c-826a-495e-b571-306f69e1c1c9 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
85fe59ea-45f3-4cc1-9171-83dabe74e5cb | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
f2c94b52-4ea3-44f4-a136-0138fd354af8 | section | Install Pipework
ff50dfdf-2359-436a-b2ff-958ffda38d6f | checkpoint | Ensure appropriately coloured pipework is installed (Hot= Red, Cold= Black,Yellow=Gas)
8147a2f8-8f85-4771-bfb0-ecc940e25531 | checkpoint | Visually inspect the inside of the fitting to ensure it is free of any dirt or grit
5733fb48-396b-42d4-93e1-46e63fbc73d6 | checkpoint | Cut pipe cleanly and squarely using PE-X Pipe Cutters.
088951a0-3c00-4be3-bb13-6838af8521c3 | checkpoint | Where required Deburr pipe end by inserting reaming tool fully into the pipe using a twisting action then rotate 2-3 full turns or until it moves freely within the pipe. Inspect to ensure sharp edges removed
a221c5cb-4a31-487f-8bc7-c0590cef8f4e | checkpoint | Push pipe into crimp fitting until the pipe is fully inserted and visible through the witness holes.
2c227911-81e8-4ef1-97f8-ff498a220d00 | checkpoint | Centralise Crimping Tool jaws over the sleeve and compress the jaws until they are fully enclosed around the fitting
3239c6b4-ca4a-4275-af47-d8d288dcf367 | checkpoint | Inspect the joint for soundness and correct crimp operation. Ensure pipe is still visible in witness hole
1835994c-b169-47da-bc84-1764edccc3e5 | checkpoint | Ensure pipework is not installed in the path of future fittings (sheeting screws, bathroom accessory fittings etc.)
ab685911-9106-459e-a694-3742b73a91c8 | checkpoint | Use crimp gauge to check joint is crimped to correct torque. Tighten or loosen torque on crimp tool if necessary
8ddd68fd-70c0-4a98-9c71-f3e49d02c4d6 | section | Test Pipework
7083b6f3-1e2a-4eba-af30-e144a6d77117 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
3960a24c-d246-4eee-94f9-a09897488d9a | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
02ad5b4a-6acb-46b5-8acc-9c15ac64a0eb | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
d36eae4e-48e7-4d3f-964f-84d157cc00e4 | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
b5cedbed-c2ff-4ae7-82d5-498f931fd63b | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
ee0e446d-3191-498f-b047-75f1c286d636 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
1f3a1296-46bb-4dd8-99b1-cb5f85d25e6e | section | Inspect Pipework
2f5f40fb-94fe-4745-b2a6-2757def48f97 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
9568f6f1-aff7-402d-9de1-7dd9de14e1c7 | signoff | Work verified by Scentre Group
610daae4-864f-4d76-a864-a7b203afb919 | section | Pipe Insulation & Identification
ae0c7ab3-9c03-48e0-a5c9-634b28112cc3 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
5f57ee01-8cbe-4069-a516-5327301e2f52 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
9b6952d4-6027-4e46-8932-2e245f4dd9ca | section | Photos
255a226a-e8a0-4b30-bc73-5fc70a34c50a | checkpoint | Photographic record to be kept of process. Take photos of entire installation
bd1bd657-cc34-47bb-b7d2-16d8c47099de | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
0ebf3247-87ba-4089-b3ae-f71313e476ec | signoff | Work verified by Scentre Group
f6c02f23-2d6b-494e-8290-6ea2e7567d7d | checklist | ITP 6 - Pressure Services - Polyethylene |  | ITP 6 - Pressure Services - Polyethylene
9f6727d9-9e61-4967-91e9-a1c17b845572 | section | Setout & Location
5c49d3af-778b-4d6c-9cb5-76b791ba157d | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
f3287b9a-fefc-40fd-9e15-a76cea9f2338 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
2ae4b29a-25bd-49d1-b79b-7687faca24d8 | checkpoint | Review interfacing services and ensure no clashes
f2753c19-09be-4e09-b5ba-72a3824a832b | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
548a2e51-7fb5-4164-9389-fa5416ba69bf | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
af6ff878-1501-592f-acae-a94c540c9e9c | dropdown | Pressure Services | Suspended, Rough In, Risers
fe96e4cd-e45d-5319-a159-28bce4fcb791 | dropdown | Type | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
d8e434f2-a0e6-40be-857b-c71176f3c812 | section | Bracketing, fittings & Noggins
13b25029-2f5a-437a-877c-fbb7ca1b9cdd | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
79f4326e-ddf0-40f4-bdfc-0d8d9b52e80f | checkpoint | Ensure correct brackets are used dependant on material selected
9365fb37-5176-40d0-ae62-e54d1e0eded4 | checkpoint | See extract from AS 3500.1 for water services
444b4d4b-ac25-491c-908a-2902e9d4e7cf | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
2dc784d9-698d-41a3-acaa-1ad0fef886f9 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
03034560-2503-4e86-95e2-587f3ad94746 | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
529ad62d-d120-48d3-9872-ddf50955344d | section | Install Pipework
1a663b99-d72d-47e4-9017-4b2fbd38f892 | checkpoint | Ensure that the pipe to be fused is the correct size for the electrofusion fitting being used
3f9b00dc-5c4f-45f5-b76f-85a2656b14be | checkpoint | Ensure correct fitting is being used and leave in packaging until ready to install
3ab4a5c4-2445-4093-b3de-2510bbe5e958 | checkpoint | Cut the pipe ends as evenly and squarely as possible using made for purpose tools
7f589d0b-6a86-41d6-ae3e-f8d25c641058 | checkpoint | Clean pipe end with isopropyl alcohol to an area that is at least 2 times the full length of the coupling on each pipe end
098e6dba-d418-4bbc-a6e1-a648a2a455ae | checkpoint | Scrape pipe end to an area that is at least 2 times the full length of the coupling using made for purpose scraping tool
0bbd0710-d7e6-4bdf-bc4f-5ecd46bc031c | checkpoint | Ensure proper insertion depth of pipe end into electrofusion coupling
797456ae-ac4c-46a6-9130-1c4bd9d58936 | checkpoint | Use assembly clamping if required
22fdac64-81c7-4738-bbf9-5746a844ea99 | checkpoint | Complete weld as per welder/ manufacturer steps
4bf4bae6-554d-42af-b36e-e3d2cf604727 | checkpoint | Ensure proper observation of cooling time
3180b747-f066-47f5-b021-758375000ca2 | checkpoint | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework
ce4b1797-f924-4f75-bca3-73c1499fa46b | section | Test Pipework
1c172848-5866-4c82-a861-84b910e75257 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
b28c7ff8-7b9d-4066-bfa1-e530a1526bd8 | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
39baef35-bde6-48ef-96f1-3569fcaa0bca | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
be445748-a11b-44c1-8910-904362e3f333 | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
8a0567db-6284-4c72-9e9f-488ab14abbe0 | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
effbec0a-9616-4b37-919b-18d2d9fecab3 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
8dd09da7-8929-4600-90c5-129e752ffbe0 | section | Inspect Pipework
837f8099-65ef-4e9f-a653-c188ded721e0 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
5da327ef-cab4-4856-9999-8fa5e541ad13 | signoff | Work verified by Scentre Group
4ce15909-20fd-41cf-9061-5c32df1d2649 | section | Pipe Insulation & Identification
39a71286-7150-40f7-b472-c7641991bbdf | checkpoint | Apply correct pipe identity stickers to indicate flow direction
62365634-9bc4-4690-a482-7e269592e6be | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
af3c04d8-4cfa-49f7-939b-9b876f917984 | section | Photos
aacd63c6-5408-4127-b34c-6d700c7b93ed | checkpoint | Photographic record to be kept of process. Take photos of entire installation
e6d59232-eb76-4fb7-b69e-f75fab613d3c | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
89d13d46-ef8c-47e7-b96e-01a38e5bea8e | signoff | Work verified by Scentre Group
bacc126d-0b03-449d-92da-edb8c76df450 | checklist | ITP 6 - Pressure Services - Press Copper / Press Stainless Steel |  | ITP 6 - Pressure Services - Press Copper / Press Stainless Steel
9f6cde1c-f5fc-453c-b974-b51b97b99e48 | section | Setout & Location
b6e1ab0c-f9d7-445a-9a74-82796360f5e8 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
d0444dc6-9be5-4d43-965e-91c9401e6fd9 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
dc591f76-9dad-41ed-b158-8eae8ed3e50e | checkpoint | Review interfacing services and ensure no clashes
85d59d6a-bd67-44fe-9174-fa0fe1d31b35 | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
c6bcc742-8c2e-467b-911b-f3197c044ad8 | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
0cc35a6a-a0ad-511e-8fff-cde3309636e4 | dropdown | Type of pipe | Press Copper, Press Stainless Steel
a2efc93b-1ac4-51fe-8898-0c4775a717c3 | dropdown | Pressure Services | Suspended, Rough In, Risers
104d3df5-9cfd-55dc-940b-e782ccfc5b04 | dropdown | Type / Service | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
c1f2184b-6146-4d8d-b05b-add53d907ce1 | section | Bracketing, fittings & Noggins
f51d0f00-6248-4ad6-9a2c-e5044e013162 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
ce281481-63ae-46ae-be53-141999e94345 | checkpoint | Ensure correct brackets are used dependant on material selected
d930d897-8c5b-43c4-8a3e-40cf9db12dc8 | checkpoint | See extract from AS 3500.1 for water services
db59d668-c3c6-4ea8-b094-25a1229172ee | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
31423f62-b109-460b-a03a-b9c1c12ce064 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
f16d28df-16ba-46a7-99b3-eaaaf4ab948c | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
342696fe-9ba7-47c4-9e9e-de3cfc313964 | section | Install Pipework
5488a274-50e2-4fff-a9da-7b06405444cd | checkpoint | Select appropriate tool for brand being used. Only use batteries supplied with tool & with not less than 40% charge
c97ab8c2-7179-4040-9031-e6c23325caaf | checkpoint | Use appropriate copper tube cutter to ensure a clean square cut.
5a728288-c323-48f0-8ebb-4ca6c5b0a455 | checkpoint | Ensure cut end is clean and free from any scratches or damage such as dents or deformity.
12b56784-2397-4bb3-9a0b-39cf3d94e3f5 | checkpoint | Ensure that the internal and external tube end is completely free from burrs or sharp edges by using a deburring tool
8bd10f3f-ec3a-4b5d-900f-4f08df0e4441 | checkpoint | Before inserting the tube, check O-Rings for correct placement and that they are free of damage or debris.
64d13908-c9bf-4de9-bc98-2158700ca3ad | checkpoint | Apply insertion depth mark with pen to the tube prior to insertion into the fitting.
b7535f72-2668-4f20-9b6d-79e7d91c084b | checkpoint | Tube to be inserted Parallel into the fitting , ensuring the insertion mark is visible and in line with fitting end
be56d2cb-2752-4c81-a70f-866c03b1a291 | checkpoint | Place jaw over the fitting, correctly aligned and positioned and activate tool to press the joint
b6e72cdf-2101-4c1c-b99f-6f11b099b096 | checkpoint | Tool should complete the correct cycle and the jaw ends should fully close on completion.
6e1002da-80ba-4313-99af-85ab625935b0 | checkpoint | If the tool does not complete the required cycle during operation the fitting should be cut out, replaced then repressed.
3030b9f3-0407-4a8b-8d2e-b23cddd15fa5 | checkpoint | No fitting should be pressed more than once
ecd3fdad-3987-4469-bc89-a47b5b1a978d | checkpoint | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework
633fdac1-b0f2-4d15-bb36-9bac6a625f88 | section | Test Pipework
6eaa0aab-bfd0-44d5-af03-1e6d1466c643 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
a80e9b65-7231-45e5-9482-36213204d6ab | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
326589cd-c1e9-4724-86c2-527effe55fd2 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
56483d2a-376e-441b-8ad2-d04235247ac5 | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
e1f4d5bd-1db6-42fe-8ecd-23d1685c7938 | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
6d4eaa65-97aa-4b55-962b-43bb6c97a7e9 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
55faf2f2-bb7d-4798-aadf-7387b736b139 | section | Inspect Pipework
0f08ada0-66d3-47ed-9335-c8d593f112df | checkpoint | Complete all required inspections by third parties (client, authorities etc)
afd6db31-6a2c-4ad0-ade7-d6bdc8573689 | signoff | Work verified by Scentre Group
7ea79753-2d31-4220-849b-a4f6926c3afe | section | Pipe Insulation & Identification
9d9d788c-bdd1-44c9-aad0-e6c8acb27df5 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
e186f00f-c9aa-453c-b5c9-d894e77d8800 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
61308564-012b-4593-845e-b9e3300058dd | section | Photos
dd9250b9-e8fc-46b7-8eb9-ab528229a1a3 | checkpoint | Photographic record to be kept of process. Take photos of entire installation
fc5a831b-9801-49bc-853b-3f4c8d335a81 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
e61f55fb-ff54-466b-8175-7482b611976b | signoff | Work verified by Scentre Group
b9df9c2f-86a7-42ff-893d-b1b4f783adb0 | checklist | ITP 6 - Pressure Services - PVC-U |  | ITP 6 - Pressure Services - PVC-U
18b91a6d-05af-4ce3-b1a8-4fa6ab4f125b | section | Set Out Works
da1c8b12-b3a5-4f0e-81a2-6eba19b986b2 | checkpoint | Take dimensions off drawings and record any remarks / deviations on as built drawings
1ecd35d6-c05d-4c02-b263-c029702ce77f | checkpoint | Review wall set out plans and ensure pipe passes through wall square
a0b5c06e-0456-4a56-8def-62c477d51737 | checkpoint | Review interfacing services and ensure no clashes
ee0705bc-add1-4160-9b15-24c6b23e1a80 | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
8670a5c1-87b1-4fd7-808d-4e8a99e38d66 | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
0f1bbce7-088a-462f-848b-e070bd92ae89 | checkpoint | Photograph of plan title block to be taken. Ensure plan number & revision number visible
0f3461b1-88de-4b72-9711-ef7f2395872e | section | Bracketing, Fixings & Noggins
e9efde4f-c10c-408e-9673-0acef0d40fb0 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
f7c429c8-d71d-488d-8ae7-5dd8eec8fcae | checkpoint | Ensure correct brackets are used dependant on material selected
11a0c1cb-cec4-45ff-8e16-0aac554b2fc3 | checkpoint | See extract from AS 3500.1 for water services
cacd22f9-1950-4ba1-bd4d-c69f2972fac7 | checkpoint | Ensure correct fixings are used as per pipe weights, element exposure & project specification
732e000e-a8f2-4205-abf4-426f18abb84d | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
ebde540a-28ed-46ee-bb64-8d3038b02e7a | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
c8267873-2da5-4f60-9b41-181be9532104 | section | Install Pipework
a6d46615-5ef7-4108-9a24-f5c5e848c38d | checkpoint | Accurately measure length of pipe & cut square. Deburr inside & outside of cut end
59b378af-e933-44e0-83e5-f4a0ee510e7d | checkpoint | Ensure sockets are primed and clean and apply a sufficient amount of Type P solvent cement
d662aaf4-cc6e-4418-b07a-7a7b27434a33 | checkpoint | Gently insert the pipe and fitting to full depth with a quarter turn & hold for 30 seconds
1d7865a3-0ca4-4901-991e-6f06108a8b5e | checkpoint | Do not disturb joint for at least 5 minutes
9030cf0f-1751-49ac-a528-b01426dfb6d6 | checkpoint | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing
4aab8277-bfb9-41a6-9792-d8911ba60b25 | checkpoint | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework
764fda50-8ff1-477e-b0b4-57e0f9cbaa71 | checkpoint | Test Pipework
179caaa0-e8f2-4ec0-a91e-99a1beece71b | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
1aa0a2d6-8523-4939-b468-42e0c618b05b | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
d8f89778-d0f1-4e1a-9e68-7c2af6277b20 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
3d1832f1-8fdf-492d-a2e6-9cda020063b1 | checkpoint | For reduced pressure water systems test pipework to manufacturers specification kpa & time period
ba7a97d5-3a1c-4ccf-bb07-11a739a4991e | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
d5190c8c-1baa-4423-8ba6-750d61ce51b0 | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
f66cf0d7-d9e4-451f-bc84-c76de49903f0 | section | Inspect Pipework
2000082f-aba9-495d-9f3e-7cc0e0687e8f | checkpoint | Complete all required inspections by third parties (client, authorities, builder, etc)
bb8aadaf-43d8-4ebc-bcb0-9765ec6f9477 | checkpoint | Pipe Insulation & Identification
d520204c-fe27-4eda-a160-99097f46f071 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
fddd9e90-ef71-4143-945d-6e19a66e0740 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
b6852d6c-9d14-408d-bf20-23bcef72d978 | section | Photographic Record
63975648-b4a8-40e0-b1a1-9f6258b9fb72 | checkpoint | Photographic record to be kept of process. Take photos of entire installation before sheeting
6ae6c956-1f2e-43d6-ab4b-0ab79f96191f | checkpoint | Works verified as conforming (McPherson Plumbing Representative):
b8a74deb-a7f6-4720-a2fa-cd3bdb458520 | checklist | ITP 6 - Pressure Services - Roll Groove |  | ITP 6 - Pressure Services - Roll Groove
8561f941-9f6a-4cd9-9872-066851b433d2 | section | Setout & Location
24e7ec8b-b96b-4165-96f8-9acf1e528702 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
f0f854f5-47fb-48e8-8b22-cd67d977bbd9 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
4cb4ff62-ac2f-444a-ab51-74766fd3325d | checkpoint | Review interfacing services and ensure no clashes
5a4b68d8-2262-4035-bbd5-d5b61ae6c508 | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
f0d1ca44-99f0-43af-9745-0eb80f77e138 | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
27826aef-334d-5341-8d1f-ef91a1ee2ec6 | dropdown | Pressure Services | Suspended, Rough In, Risers
491a4302-3051-5473-9f4c-cc17be447320 | dropdown | Type | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
49c084de-1289-47e1-aa04-e69c55e4d033 | section | Bracketing, fittings & Noggins
916e6c92-7706-48d2-a02b-77b613cf7d55 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
7834dd42-2550-4d18-9085-6cd4933014e7 | checkpoint | Ensure correct brackets are used dependant on material selected
43c12217-aeca-441c-95a9-c72e9c1808ad | checkpoint | See extract from AS 3500.1 for water services
b617998a-3f84-4fc2-8627-44b6ca5f7284 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
01ed2fe0-a5fc-46cd-b8fd-42f273ac8272 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
5e5037b4-2e39-491c-8b6d-c0d3f6c4e87b | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
9672dfaa-f4ad-449e-89aa-959c6b249df3 | section | Install Pipework
65c24dad-ac24-410a-96e8-e8bace8d7b70 | checkpoint | Where practical, arrange for pipework to be pre-cut and grooved off site
3d10a367-087b-4030-840a-78ea64568e42 | checkpoint | Ensure pipe is cut squarely with a fit for purpose tool
52bde302-1077-4c73-8176-df85caece523 | checkpoint | Assure manufactured roll grooved ends of pipework are measured for appropriate circumference using approved tape measure
bdf172f5-f635-4bc8-8669-f531306754b4 | checkpoint | Ensure pipe cut on-site is grooved to required depth & check with approved tape measure
e71458ad-9cc8-4a4c-bfff-a7ee2b7004ab | checkpoint | Ensure pipe length is correct. Don't use coupling to pull incorrect pipe lengths together
69ce8a00-4931-44c6-aafe-58f7b27142d2 | checkpoint | Lubricate and install inner coupling for connection of pipe and fittings, ensuring it is lapped over each connection point
cd44a422-5391-4bc2-8125-da310d8d5871 | checkpoint | tighten outer metal band gradually and evenly to a torque of the manufacturer's specification
92ff57ea-1ad6-45e3-85b8-6606ca1e4bcd | checkpoint | Ensure a gap no more than 2 mm is evident on joining portions of outer coupling
5f2ddd84-a940-4d89-b725-eac176b36fb7 | checkpoint | Inspect fitting / pipe after roll groove collar tightening to ensure it is square and aligned
294371cb-a712-4bf5-80b9-d8b54bb0c75e | section | Test Pipework
58ed5798-2490-4e6b-a1b1-9a69e70dd0a2 | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
5ca39935-2a14-4d0b-b074-55fa87ea5da9 | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
559b5e54-e681-45c3-bb78-bc8e979e2932 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
77612ab7-4fee-47d9-a7ad-75ceff75ed2a | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
893d443f-ca96-4d9e-a2f3-1c5a15896bff | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
d1edf835-859c-41fa-a611-a1765b5ac41e | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
2e6ea6f0-009c-47a1-af88-912b7274a5ac | section | Inspect Pipework
697f9624-b757-4b39-b9ac-0a7f3123e282 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
a5e75534-6c75-41b9-ac30-5800af98259b | signoff | Work verified by Scentre Group
7a0362cc-9bae-4abe-a3b5-8200c9efc8d6 | section | Pipe Insulation & Identification
ebf50ee9-5604-49a5-aa4e-27bb9b9d89b5 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
9417b881-ebf2-45f5-b0e2-d52f5c675d95 | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
d2e89a24-0e6b-4ac6-9e8b-3fca9cea0924 | section | Photos
24dc5877-25d3-4c5c-96cd-fa614fd690b4 | checkpoint | Photographic record to be kept of process. Take photos of entire installation
039aa444-10d8-40d0-9946-fd2eca057d2a | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
4bd2eef8-5f7b-4fcf-b34e-313d843afaa3 | signoff | Work verified by Scentre Group
a9e64ef1-4ddf-486a-988e-3026260d40cc | checklist | ITP 6 - Pressure Services - XLPE Sleeve Type |  | ITP 6 - Pressure Services - XLPE Sleeve Type
ea131d74-dcdd-4612-9c7a-2a733b249940 | section | Setout & Location
e8e91bab-b21e-4fc8-96db-e800a8c989a9 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
41d5a368-4d86-48c4-ac0d-4988bf971354 | checkpoint | Review wall set out plans and ensure pipe passes through wall square
4cc4dc14-9ceb-46b0-a0b6-8d8f57a97932 | checkpoint | Review interfacing services and ensure no clashes
4cef0248-a6f4-4e91-8ab9-341f52ee6c52 | checkpoint | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern)
660de213-cafe-4ef4-b7da-26fa2ec3758a | checkpoint | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating
0c90a8fa-367a-550e-bdbf-e40860dfec48 | dropdown | Pressure Services | Suspended, Rough In, Risers
ee1b1ab9-c01d-5c7a-900a-67db17d56fb4 | dropdown | Type | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
b87735df-46c2-40b7-aaa8-28a6b4f48b91 | section | Bracketing, fittings & Noggins
143bb0a2-9ec1-4a68-ba19-002db5bd9396 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
c05db42e-a300-4f7e-af36-06c9705f6253 | checkpoint | Ensure correct brackets are used dependant on material selected
cc14ef58-0b8d-4466-afb7-526267f77ac4 | checkpoint | See extract from AS 3500.1 for water services
dc32ea7a-b09f-4093-88af-ca9925cbcce5 | checkpoint | Ensure correct fittings are used as per pipe weights, element exposure & project specification
0609efec-4cfb-4ada-963e-01c257f30be7 | checkpoint | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel)
52f7091c-9523-4705-93dd-034288c37e05 | checkpoint | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required
2dd875a6-4138-4ffa-9ff2-00beabad6e2f | section | Install Pipework
0d2641bf-361d-4b52-a8c3-a39985b97435 | checkpoint | Ensure appropriately coloured pipework is installed (Hot= Red, Cold= Black)
4ea7e4db-35f6-4ab2-ad9b-35cc2fa766a4 | checkpoint | Cut pipe cleanly and squarely using PE-X Pipe Cutters. Place beveled end of the sleeve facing outwards toward joint
d0229e0a-d9ea-4549-a6bc-329bb3b20b23 | checkpoint | Expand the pipe twice only using the approved Expanding Tool
982fb4a0-9d39-47bf-b723-ab9b8f990c70 | checkpoint | Insert the fitting into the expanded end of the pipe until the fitting reaches the pipe stop.
26a99a9d-527d-4745-9e8f-2eb20672b102 | checkpoint | Slide the jointing sleeve towards the fitting. Position the jointing sleeve and the fitting squarely within the jaws of the Compression Tool.
cd7e7c7d-6445-4d9f-9a87-2d6e02f342c6 | checkpoint | Draw the sleeve towards the fitting by closing the jaws of the Compression Tool until the sleeve reaches the shoulder of the fitting.
7e7e10ec-89ce-4922-8100-e2de2103d259 | checkpoint | Ensure pipework is not installed in the path of future fittings (sheeting screws, bathroom accessory fittings etc.)
e272e188-ff58-42e8-80f0-e3d9b7a929bb | checkpoint | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework
0a53ba87-9e57-4be6-89a6-1ea776c0979e | section | Test Pipework
035fa45f-57dc-4684-97e5-59a019598bac | checkpoint | Photographic record to be kept of process. Take photos of gauges before and after
7e8a15d4-6fa1-43b1-aff4-8cc37295eb09 | checkpoint | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1
151d1de2-302e-4190-9b11-6893114ce645 | checkpoint | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines
cffaf785-e262-497b-b0ab-ef1d51809597 | checkpoint | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period
0d02abb0-e733-4589-9e3b-5fbe417baf2f | checkpoint | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period
a00a19f6-1f40-48e4-9b79-f15f5f112fcd | checkpoint | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure
3c600b67-a9e8-4482-a0d3-78d7d2dc8bf7 | section | Inspect Pipework
7bc29a21-8f6c-450b-980b-504e50173f01 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
d9010e62-5ba8-445e-94b6-0bc658cc822c | signoff | Work verified by Scentre Group
e5152c80-1c96-4948-8b3c-43b5a9bbe8f5 | section | Pipe Insulation & Identification
9ceef893-9d18-4049-a182-466da12770e9 | checkpoint | Apply correct pipe identity stickers to indicate flow direction
ca35566a-89c4-417e-9d31-bee9a3f92d2d | checkpoint | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification
74dc4030-85b7-4a33-ab2b-51e8bd898ab6 | section | Photos
a946df79-97b3-46a8-90ab-d7486e48922c | checkpoint | Photographic record to be kept of process. Take photos of entire installation
9decd616-d32f-4442-b5cd-44178cdb50be | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
e1b5fe39-a25e-4495-a239-498cb10cf385 | signoff | Work verified by Scentre Group
cb312255-419b-446b-a5e5-55c9ec07ab52 | checklist | ITP 7 - Meters & Valves |  | ITP 7 - Meters & Valves
edf7d964-e911-4c46-9315-162a54ddbbca | section | Setout & Location
6f5b5d79-d86f-4420-96b2-32ef1452b86a | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
ad039742-1cf0-4aaa-bf8a-1605279abc0c | checkpoint | Setout of meter/valve installed as per authority & project requirements, Height & specials
69648885-beec-4192-8b43-c019db3f00ea | checkpoint | Setout of meter/valve installed as per project requirements, Height & specials
d371bcd0-e1aa-4374-bb43-e9b18f2f1f1b | checkpoint | Meter located as per Authority requirements
519e3a83-816b-5621-9c13-ddf146ad3572 | dropdown | Hydraulic Service Meter Valves | Metering, Temperature, Pressure, Testing, Control
ea8ad058-7c2f-504f-b6c1-334c9432cc10 | dropdown | Service | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services
5e38dadf-2929-45b6-90b9-943c60de0aaf | section | Bracketing, fittings & Supports
57a30769-da87-460c-a584-cdfb7f383592 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
52b867ef-c33d-4204-aae9-fc88eacd8226 | checkpoint | Ensure correct brackets are used dependant on pump selected
c9e51f3f-60ec-437d-9133-74d867a67e58 | checkpoint | Pipework supported independently of pump assembly
92839f43-ee46-4814-bd41-7e2b58aba19f | checkpoint | Ensure correct fittings are used as per pump/plant weights, element exposure & project specification
9deafe84-b671-4f08-b236-59288f4b1cb1 | checkpoint | Ensure acoustic mounts/brackets are used as per acoustic spec
40339e1f-350f-46da-8db2-29b6894c79e9 | section | Install of Valves / Meters
f2e683c6-72de-4f40-91ff-9504ad9617be | checkpoint | Flush all lines where possible prior to installation
c7e94a09-b59b-4a2e-890e-548d7e4a8906 | checkpoint | Install Valve/ Meter as per authority/manufacturer's requirements
1960126e-7778-4e2e-891b-f8acac57b404 | checkpoint | Mounting of valve/ meter at a serviceable height and location where required as well as vertical & plumb
3a2fd2ef-866f-4022-b5cc-9193e7683023 | checkpoint | Valve Installed as per standards (Height, proximity to other services/ walls etc)
327d806b-39f1-47b1-a78b-3dbfcff5b525 | checkpoint | Unions, Isolation Valves, Strainers, Drains etc installed where required for servicing & as per manufacturer's specification
c0e4a1e5-c0fc-4050-994f-f7aca39460ef | checkpoint | Teflon joints used over loxeal where servicing is required (loxeal used on male threads only)
ff092d81-a562-4c4c-b494-b7d81e26243c | checkpoint | Isolation valves installed as per meter/valve requirements
d52bf736-7d8f-4a3c-90a1-b0fefd0f9241 | checkpoint | Petes Plug Valves installed as per Authority Requirements
7469ca4a-3af2-4662-9376-894ae700a155 | checkpoint | Valve/ Meter installed in the correct orientation (check for directional arrow)
4e17a013-4f9c-436a-b41a-f008562c0fb0 | checkpoint | Install identification/service tags to authority/project specifications
1ed10b5d-b788-40da-9a0f-4e8d1b5d57f6 | section | Testing
e8928267-0cbb-4ae0-8645-a11631fa08b5 | checkpoint | Pressure Reduction valve tested for accuracy on outlet pipework as per manufacturer's specification
4ed58093-4f6d-485b-a1c1-6778507a74b3 | checkpoint | Tempering valve outlet temperature checked for 50 degrees max or as per manufacturer/ project requirements
63447628-528b-451c-bbfc-4b4db747d04c | checkpoint | Check that no leaks on unions or valve threads
8ef824ed-b17c-41a4-bdd2-f4b532190908 | checkpoint | Test valve and commision as per manufacturer's requirements
a460f05a-143a-4cff-b31f-01c7c6193dc7 | checkpoint | Clean all strainers/dirt box from debris
cb9d531f-aedf-4b62-8409-2bbffe30fef3 | section | Inspect Pipework
b20b8989-62b5-4f6b-9b5a-c2ff8be2f627 | checkpoint | Complete all required inspections by third parties (client, authorities etc)
0f00d546-9445-4d0a-825e-5d25be3d3252 | signoff | Work verified by Scentre Group
6664c473-2c92-4d08-8182-ed3f772a61c3 | section | Photos
218bf378-b293-4a83-b55b-47d706c5c259 | checkpoint | Photographic record to be kept of process. Take photos of entire installation
48117986-72cc-43fe-9340-bd3eaa2c8b24 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
7711d7f1-c528-4c87-9e9e-4d50f6214cce | signoff | Work verified by Scentre Group
130bbc38-90a4-4e3d-961d-cf438d8df5ac | checklist | ITP 8 - PC Plant & Pump |  | ITP 8 - PC Plant & Pump
b6bb5d3e-f2cd-46b5-8527-1064aaf98a19 | section | Setout & Location
9dc77bec-0333-445b-8437-71a62695d1a8 | checkpoint | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block
c7ce5f17-c9cb-4b47-9cc3-63b090547c54 | checkpoint | Set Out of Pump/ Plant installed as per authority requirements, Height & specials
4c87ade8-89b0-5881-a6ac-f5653b348ab8 | dropdown | Service | Potable Cold Water, Hot Water, Non-Potable Cold Water, Fire Services, Gas Services, Sewer, Stormwater
f30eba03-abae-494e-aa94-76079405cd80 | section | Bracketing, fittings & Supports
c81b639d-89ae-4825-836b-125b43468144 | checkpoint | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard
0022e2a2-3502-4c7a-b33e-58b554509dae | checkpoint | Ensure correct brackets are used dependant on pump selected
06fead94-22ed-4888-8287-98e28ede462f | checkpoint | Pipework supported independently of pump assembly
49fa423f-77bd-4f20-a093-1504de62cf71 | checkpoint | Ensure correct fittings are used as per pump/plant weights, element exposure & project specification
394dadc1-0489-4f9d-8b07-26235bc6b14b | checkpoint | Ensure acoustic mounts/brackets are used as per acoustic spec
ae691d9f-aa40-48cc-922f-cd7a095eabef | section | Install of Pumps / Plant
50e5f643-ce80-4496-9a2c-97481694fe99 | checkpoint | Installed as per manufacturer requirements & specifications
baffef38-6151-49b6-8d52-cb0866d7f3af | checkpoint | Installed as per Authority requirements & specifications
fc2f9d90-063d-45d5-ac50-1258062c0eb0 | checkpoint | Mounting of Pump/Plant/Valves at a serviceable height where required
a01aa1f8-2e05-4661-9c33-68207d5b8023 | checkpoint | Installed in a tradesman like manner vertical & plumb
422a408b-f937-4056-b3b0-f099366e2642 | checkpoint | Ventilation & Flooring installed as per authority/australian standards & manufacturer requirements
67a8b39a-3668-4721-bb3d-8963b2e35fc2 | checkpoint | Unions, Isolation Valves, Strainers, Drains etc installed where required for servicing & as per manufacturer's specification
94e2c78e-8bab-408c-b843-f18f5d9368f0 | checkpoint | Installed on membraned plinth as per manufacturer/project requirements
278587bc-e67d-40c7-abf9-2ee0f6224498 | checkpoint | Isolation valves installed as per Manufacturer/Project requirements
8572ad19-4f7c-4df6-9f3e-0946da80a828 | checkpoint | Petes Plug Valves installed as per Authority Requirements
fc6dd6a7-04ba-45d6-b795-c27236ca5e0d | checkpoint | Temperature Gauges installed as per Project/Manufacturer Requirements
cf91c232-3e81-4549-b73d-8c1f69d457ac | checkpoint | Non-return valves installed as per Project/Manufacturer Requirements
355702e4-09a2-4a27-ac93-6c1bfe3a0fda | checkpoint | Pressure Gauges installed as per Project/Manufacturer Requirements
9c391b7b-b771-42d8-82f6-b991549672fd | checkpoint | Auto air release Valves installed as per Project/Manufacturer Requirements
89dd1a7d-694a-44a6-984f-8a7c83214215 | checkpoint | Pump installed in the correct orientation (check for directional arrow)
c240fc2b-557f-464c-abfe-74415937985b | checkpoint | Install identification tags to authority/project specifications
0cb90434-37c7-41f0-ae46-e6a5018fb965 | checkpoint | Install pipework identification as per AS 1345
b4dcb5ee-5ce4-4ef6-824e-4c18bd0b1672 | section | Testing & Commissioning
d0cf9bc5-9754-45a6-8c06-6419f357a1b4 | checkpoint | Testing & Commissioning as per manufacturer's specification
b530b42c-d9db-4ff4-a2cd-6b6f8857b870 | checkpoint | Testing & Commissioning by supplier Attached
1f8f3006-a093-45da-a602-a02cd532a670 | checkpoint | All air removed from system and strainers cleaned
d28802c6-1028-4c45-b846-f09e64fc2dd8 | checkpoint | Permanent Power supplied to plant / pump
c691e535-13f7-4905-a973-155c3202523c | checkpoint | All safety shut off devices installed & commissioned
5dadd1c4-3295-4396-8297-333294b567a2 | checkpoint | Clean all plant & equipment before handover
0cf10a63-9656-4332-b63f-c06390d28fd7 | checkpoint | All drains cleaned of construction debris in the case of plant failure
fa6c6f3b-0155-43c0-a34d-6bf1775825b4 | section | Inspect Pipework
72af1379-4f3a-4cae-b72c-7b9174688fbe | checkpoint | Complete all required inspections by third parties (client, authorities etc)
7244eb12-f99d-4278-98db-a1d88496bbe4 | signoff | Work verified by Scentre Group
1207e88d-713a-4df9-8593-08ebf1d09cd7 | section | Photos
808aaa68-a29d-4644-9084-42880589700b | checkpoint | Photographic record to be kept of process. Take photos of entire installation
6f896740-3c96-4d71-89da-6fecfc03acc1 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
45395ec4-681f-4f2f-8905-617d58c431fe | signoff | Work verified by Scentre Group
7416298a-52bf-46be-b4b2-4a9a827e7dbc | checklist | ITP 9 - PC Installation & Commissioning |  | ITP 9 - PC Installation & Commissioning
3c24e0cc-54a5-4132-a591-02d68c75f11a | section | Water
2ad4e10f-98f3-4e42-ba5f-e563be9198b0 | checkpoint | Water Meters Installed - Cold, Hot, Non - Potable, Gas - Take picture of meters
cbcac08c-0581-4def-9739-8115ae02f65d | checkpoint | Time taken to get hot water at most disadvantaged fixture
3b5714a6-e2c0-44ab-be0f-bd8e75f20c52 | checkpoint | Hot & Cold water isolation valve test for cross connection
4832b479-ea4a-419c-8766-fbc9001d467e | checkpoint | Non-Potable water isolation valve test for cross connection
173c7c6e-f746-445f-8c56-74dfbd16b8fa | checkpoint | Tempering valve set to required temperature (50 max for residential for tmv use ITP #9) Set temp -
15e5ea8a-e35d-445b-8654-d3f6ba9e64cf | checkpoint | Pressure reduction valves set to required pressure (500 kpa max for fixtures) Take picture of valves and comment (Cold Water PRV KPA, Hot Water PRV KPA)
5ad41bc3-3fff-429d-88c2-568169b281f7 | section | Kitchen
644caf7d-69f5-4c18-8883-68a76d232d59 | checkpoint | Sink Installed - Secure & damage free (photo)
14bc6468-e338-4aa8-89a5-c7cdee720d98 | checkpoint | Mixer Installed - Tested/ secured/ cross connection check/ aerator clear/ damage free, ( photo )
d53cc0e3-8988-4dc4-ae75-2f33cfe0a3a4 | checkpoint | Trap installed & tested, Tundish Installed & test
ec0dd46e-d6ee-4a92-aa35-788817729a36 | checkpoint | AAV installed with allowance for servicing/replacement
0ac78aed-8d7c-4d0c-a2f0-d1d61df61c87 | checkpoint | Dishwasher Installed
5d30c091-7e4a-4d1b-83a1-52fa763945ca | checkpoint | DW QA - Cycle Run / Water Connection Ok/tight/secured / Waste Connection- Ok/tight/secured/drilled out
71f252dc-d607-47bd-bddd-8efb6453c62f | checkpoint | Zip Tap - Commission zip tap & unit as per zip commisioning process
b7976c00-7a30-47d4-abde-c40a7c1575c1 | checkpoint | Zip Tap - Check zip unit for no leaks & power on
da4bb2f0-d2a0-4eab-8b88-d178a03c7b6f | section | Winter Garden / Balcony
7503cee2-3eab-4895-827d-36af1ac1fde6 | checkpoint | External Hose Tap Installed - Potable, Non-Potable - Installed plumb and damage free
f6cf24ed-1704-4716-8aa7-50df603bf3d7 | checkpoint | Balcony Outlet - Clear & Free of debris (photo)
76357667-1527-4126-8be9-255f4c73d71e | checkpoint | Gas Cooktop Installed - Secured & damage free (photo)
e7e6d722-de16-4140-af07-40204c116faf | checkpoint | Gas Flexi / Isolation Valve / Regulator / Loxeal used on all parallel threads / Gas tape on reg thread (photo)
631c394b-7d57-4103-bb96-f89d89b661d1 | checkpoint | Purge & Commision cook top as per manufacturer's specifications and AS5601
e955bd6b-4efe-460c-9f63-d251b81bbf95 | checkpoint | Bayonet points installed - Internal / External / Installed plumb & damage free
a39c5255-c318-412f-a08e-e4d6d120caad | section | Laundry
7103db05-a7bb-4ddf-9117-517c97b1318a | checkpoint | Tub/Sink Installed - Secure & damage free (photo)
0a7eaa45-0bcd-43dd-87ff-5ab37f4edaca | checkpoint | Mixer Installed - Tested/ secured/ cross connection check/ aerator clear/ damage free, ( photo )
e358f772-b9af-4e74-919a-728e77d92f10 | checkpoint | Trap installed & tested, Tundish Installed & test
83b04a6e-8f92-4199-9a52-887ebf984a0f | checkpoint | AAV installed with allowance for servicing/replacement
b086488a-5d1a-4898-b3c8-d77052d5460e | checkpoint | Washing Machine Installed
4916bece-62a8-41b7-a94f-0b2b4e330db2 | checkpoint | WM QA - Cycle Run / Water Connection Ok/tight/secured / Waste Connection- Ok/tight/secured/drilled out
f3b4ff28-0f71-4181-80bf-3e9268b89427 | checkpoint | Floor Waste - Clear & Free from debris (photo)
ea39d27b-f75c-446d-8e33-49c46ed5993b | section | Main Bathroom
8f607876-0c98-453c-a87c-112345282e83 | checkpoint | Floor Waste - Clear & Free from debris (photo)
ec7532c1-732f-494f-9bf2-11c6bf9bf67c | checkpoint | WC Installed - / Silicone / Seat - Secure & damage free (photo)
cd3f47cf-10da-4e79-96ce-40a233aa1f07 | checkpoint | Flush Plate installed Plumb and damage free (photo)
f859acb7-56dd-4e4a-a2f7-b538bc86adf0 | checkpoint | WC Tested (minimum 10 flushes and inspect under pan for leaks)
788645b5-900e-4312-ad25-fe3c93ad8c9b | checkpoint | Basin Installed / Silicone - Secure & damage free (photo)
26d0d2b7-daaf-4bd0-9e06-d4d407ca7a7f | checkpoint | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
89826bd0-91a4-4681-a229-8f079d2b2c18 | checkpoint | Plug & Waste Installed / Trap installed & tested / Tundish Installed
f6730446-1e24-4114-8e9e-7ce86abe4020 | checkpoint | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head
d5a37f86-cf4c-4f28-a695-377c68bfd5bf | checkpoint | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
94a8fc95-03e0-4d1c-b5be-140509a1f9d4 | checkpoint | Shower Waste - Clear & Free from debris (photo)
15524b43-a179-4d7b-b5b1-ee8e07753093 | checkpoint | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo)
be54de85-0def-4cfd-ae14-fb15da5399a6 | checkpoint | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
ddd470a1-21a0-4676-b7ad-2b65ff9cd5ee | checkpoint | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked
b1e7d381-737d-4027-925e-ed97fa97f4eb | checkpoint | Photos Uploaded or saved to appropriate location
a02cc162-28dc-4040-b36d-d4d8dba57ded | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
3247d124-f6e0-4a8f-85e7-ab3fc87197a1 | signoff | Work verified by Scentre Group
13d1b563-6eb1-4626-9d9e-1f398fd6dee7 | section | Ensuite Bathroom 1
e4cdc5ea-8cb2-4298-83f2-16c76a9e3575 | checkpoint | Floor Waste - Clear & Free from debris (photo)
fd1a32ce-df63-4ac8-abac-d3e2722b1641 | checkpoint | WC Installed - / Silicone / Seat - Secure & damage free (photo)
579d216b-0b64-4475-8a26-a3f9266cde7e | checkpoint | Flush Plate installed Plumb and damage free (photo)
14447584-69f0-4d00-b6bb-c03f8d5cc0bb | checkpoint | WC Tested (minimum 10 flushes and inspect under pan for leaks)
7ba494a1-b3a4-4cf6-a391-2fea0fb1b6da | checkpoint | Basin Installed / Silicone - Secure & damage free (photo)
eedde43a-5652-4176-87f2-bcba43bc0455 | checkpoint | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
1cff6d34-8111-4b17-8f81-1b93374ef250 | checkpoint | Plug & Waste Installed / Trap installed & tested / Tundish Installed
ebb04353-5d93-4dec-9939-3d30d2d3fe9c | checkpoint | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head
32f0921f-d6f8-4733-b8ed-ae1a49a102a4 | checkpoint | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
d0c28e9d-8a5d-4441-82cc-aeda51667ee3 | checkpoint | Shower Waste - Clear & Free from debris (photo)
cd598b8b-ad61-4bf3-ab16-4761115ffaa3 | checkpoint | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo)
cb75617a-531f-4a9b-b4b8-9eb86677d055 | checkpoint | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
a48c383f-bc1e-488c-9c5b-7318b622a8f9 | checkpoint | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked
c72e87a8-dbaf-459a-97fc-a57c257fddd5 | checkpoint | Photos Uploaded or saved to appropriate location
df79f99c-51bc-4abb-99f4-8a0a17150593 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
f6a88e14-553d-4a38-bb98-12bdab818c17 | signoff | Work verified by Scentre Group
90773800-bc38-4a5b-a10f-0331acd77c0b | section | Ensuite Bathroom 2
b6f3bbbc-9782-4db9-b98c-7ae22e7c5bfb | checkpoint | Floor Waste - Clear & Free from debris (photo)
5cf8537a-7247-47cd-8cf3-256ac472e85d | checkpoint | WC Installed - / Silicone / Seat - Secure & damage free (photo)
d6df2f92-91e3-4cc2-a799-1eddcd0694c5 | checkpoint | Flush Plate installed Plumb and damage free (photo)
1decbd14-e82d-49e4-a1d4-32bb1c60375b | checkpoint | WC Tested (minimum 10 flushes and inspect under pan for leaks)
925b0bc1-034a-4e99-a04a-1d282836f69a | checkpoint | Basin Installed / Silicone - Secure & damage free (photo)
5a61d24e-9e95-4ed8-8bf2-4973a8a8dcd9 | checkpoint | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
18d129a6-3e5e-468a-939a-8122fa271788 | checkpoint | Plug & Waste Installed / Trap installed & tested / Tundish Installed
2abe3f09-56ec-4de1-ae7f-19782d6f88a2 | checkpoint | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head
4e8d07d0-9eaa-4412-84b8-705ca9d3056e | checkpoint | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
bb79691c-c94e-45c2-9e59-1884bf6e041e | checkpoint | Shower Waste - Clear & Free from debris (photo)
2660a966-5c65-4710-8b43-8f3407ef75de | checkpoint | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo)
7ade9a81-bbe6-44d3-9226-e58853c7bc76 | checkpoint | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
e2726d2c-96ac-4de6-9cd8-98dbea2efc93 | checkpoint | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked
a0c985f1-60f6-4292-bd8a-622202389d64 | checkpoint | Photos Uploaded or saved to appropriate location
bbcf4056-03a9-42e6-9e26-91f3f5196e3e | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
31095bac-5002-49a6-8895-4c769a148887 | signoff | Work verified by Scentre Group
eddf7307-2c50-478c-bd1a-f107025d33c3 | section | Powder Room Bathroom
c13f6c42-9a93-4cd2-88b6-0e25427b9f4f | checkpoint | Floor Waste - Clear & Free from debris (photo)
0804e1d8-575d-4ccd-8a7c-d286fbfcc720 | checkpoint | WC Installed - / Silicone / Seat - Secure & damage free (photo)
e2d3695e-af94-4773-81c4-dac536aaefb6 | checkpoint | Flush Plate installed Plumb and damage free (photo)
8f8a01dc-226a-41d4-82d9-bdef1e4aeba5 | checkpoint | WC Tested (minimum 10 flushes and inspect under pan for leaks)
94577539-a690-43e1-a4bc-a4e7c754f504 | checkpoint | Basin Installed / Silicone - Secure & damage free (photo)
2ddd9fc2-d6ad-47b0-839a-4e5cd3a4f232 | checkpoint | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo )
4a0a90bc-8918-47a0-995d-95fb1225e453 | checkpoint | Plug & Waste Installed / Trap installed & tested / Tundish Installed
aca6074d-d149-42a0-a78c-c10bbf3cb969 | checkpoint | Photos Uploaded or saved to appropriate location
ff5e01ce-80f1-4b9b-9543-7716b8f58870 | checkpoint | Works verified as conforming (McPherson Plumbing Representative)
e844ca45-feef-4579-bad9-94e0357f031c | signoff | Work verified by Scentre Group
1b327cf0-610d-4e2c-8f89-33920c691539 | checklist | Subcontractor ITP |  | Subcontractor ITP
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
67976100-8012-48e1-abcd-344b5c90f1b6 | checkpoint | Attach subcontractor ITP