## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Set Out - Penetrations & Fire Collars
| Scope |  |  | Set Out - Penetrations & Fire Collars
Rows
|  | Level 13 | dynamic | Level 13 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 14 | dynamic | Level 14 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 15 | dynamic | Level 15 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 16 | dynamic | Level 16 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 17 | dynamic | Level 17 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 18 | dynamic | Level 18 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 19 | dynamic | Level 19 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 20 | dynamic | Level 20 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 21 | dynamic | Level 21 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 22 | dynamic | Level 22 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 23 | dynamic | Level 23 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 24 | dynamic | Level 24 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 25 | dynamic | Level 25 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 26 | dynamic | Level 26 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 27 | dynamic | Level 27 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 28 | dynamic | Level 28 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 29 | dynamic | Level 29 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 30 | dynamic | Level 30 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 31 | dynamic | Level 31 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 32 | dynamic | Level 32 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 33 | dynamic | Level 33 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 34 | dynamic | Level 34 | Set Out - Penetrations & Fire Collars | Site QA
|  | Level 35 | dynamic | Level 35 | Set Out - Penetrations & Fire Collars | Site QA
Columns
|  | Take dimensions off drawings & record remarks/deviations |  | survey & set out works | take dimensions off drawings and record any remarks / deviations prior to installing
|  | Set Out | Set Out | survey & set out works | take dimensions off drawings and record any remarks / deviations prior to installing
|  | Photo of title block to incl. drawing no. & revision |  | survey & set out works | photo of title block to include drawing number & revision
|  | No structural effect with penetration/cast in pos. |  | structural interface | consult structural drawings to ensure no structural effect with penetration or cast in position
|  | Pipework within set downs & beams are cast in/out |  | structural interface | ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings
|  | Penetration does not clash with elements downstairs |  | structural interface | check that penetration does not clash with elements downstairs e.g. walls, beams etc
|  | Fire collar installed as per manufacturer's specs. |  | ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable | fire collar installation
|  | Fire Collar Type | Fire Collar Type | ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable | fire collar installation
|  | Pipe fitted correctly |  | ensure pipe is fitted correctly | pipe insertion to collars
|  | Pipe fitted to maximise efficiency of next work sequence |  | ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. pipe is easy to knock through | pipe insertion to collars
|  | Conduit within wall/carcass range |  | ensure conduit is within wall or carcass range | cast in conduits
|  | Use 15/45 degree bends on all changes in direction |  | use 15/45 degree bends on all changes in direction | cast in conduits
|  | Pipe supported correctly without affecting balcony soffit |  | cast in balcony outlets | ensure pipe is supported correctly without affecting balcony soffit
|  | Pipes not damaged after top steel & set downs installed |  | cast in balcony outlets | ensure pipes are not damaged after top steel and set downs are installed.
|  | Safewaste/puddle flange installed to all req. outlets |  | ensure safewaste or puddle flange is installed to all required outlets | safewaste or puddle flange installation
|  | Safewaste/puddle flange installed to correct height |  | safewaste or puddle flange installation | ensure safewaste or puddle flange is installed to the correct height
|  | Spray all floor wastes to identify falls |  | safewaste or puddle flange installation | spray all floor wastes to identify falls
|  | No open ends by installing dust cap/duct tape on risers |  | ensure no open ends by installing dust cap or duct tape on risers | all pipes & casting capped & supported
|  | All sleeves installed in in situ walls at correct height |  | ensure all sleeves installed in in situ walls at the correct height | pipe sleeves
|  | Pipes clear of any obstructions prior to extending riser |  | ensure pipes are clear of any obstructions prior to extending riser | castin downpipes
|  | Pipe fitted correctly where agreed by structural eng. |  | ensure pipe is fitted correctly where agreed by structural engineer | castin downpipes
|  | Pipes wrapped where required |  | ensure pipes are wrapped where required | castin downpipes
|  | Downpipes capped & taped to riser |  | ensure downpipes capped and taped to riser | castin downpipes
|  | Pipe is filled with water for concrete pour where req. |  | ensure pipe is filled with water for concrete pour where required | castin downpipes
|  | All required inspections by third parties |  | complete all required inspections by third parties (client, authorities, builder, etc) | inspect pipework
|  | Photos taken of entire installation |  | photos | ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour
|  | Works verified as conforming |  | photos | works verified as conforming (mcpherson plumbing representative) name:
Jump Form - Penetrations & Fire Collars
| Scope |  |  | Jump Form - Penetrations & Fire Collars
Rows
|  | Jump Form - Penetrations & Fire Collars | dynamic | Jump Form - Penetrations & Fire Collars | Site QA
Columns
|  | Take dimensions off drawings & record any remarks/deviations prior to installing |  | Take dimensions off drawings and record any remarks / deviations prior to installing | Survey & Set Out Works
|  | Set Out | Set Out | Take dimensions off drawings and record any remarks / deviations prior to installing | Survey & Set Out Works
|  | Photo of title block to include drawing number & revision |  | Photo of title block to include drawing number & revision | Survey & Set Out Works
|  | Consult structural drawings to ensure no structural effect w/ penetration/cast in position |  | Consult structural drawings to ensure no structural effect with penetration or cast in position | Structural Interface
|  | Ensure pipework within set downs & beams are cast in/out of set downs where req. & indicated on penetration drawings |  | Ensure pipework within set downs and beams are cast in/out of set downs where required and indicated on penetration drawings | Structural Interface
|  | Check that penetration does not clash w/ elements downstairs |  | Check that penetration does not clash with elements downstairs e.g. Walls, Beams ETC | Structural Interface
|  | Ensure that fire collar is installed as per manufacturer's specifications & spatially acceptable |  | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable | Fire Collar Installation
|  | Fire Collar Type | Fire Collar Type | Ensure that fire collar is installed as per manufacturer's specifications and is spatially acceptable | Fire Collar Installation
|  | Ensure pipe is fitted correctly |  | Ensure pipe is fitted correctly | Pipe Insertion to Collars
|  | Ensure pipe is fitted to maximise the efficiency of the next sequence of work |  | Ensure pipe is fitted to maximise the efficiency of the next sequence of work e.g. Pipe is easy to knock through | Pipe Insertion to Collars
|  | Ensure conduit is within wall/carcass range |  | Ensure conduit is within wall or carcass range | Cast in Conduits
|  | Use 15/45 degree bends on all changes in direction |  | Use 15/45 degree bends on all changes in direction | Cast in Conduits
|  | Ensure pipe is supported correctly without affecting balcony soffit |  | Ensure pipe is supported correctly without affecting balcony soffit | Cast in Balcony Outlets
|  | Ensure pipes are not damaged after top steel & set downs are installed. |  | Ensure pipes are not damaged after top steel and set downs are installed. | Cast in Balcony Outlets
|  | Ensure safewaste/puddle flange is installed to all req. outlets |  | Ensure safewaste or puddle flange is installed to all required outlets | Safewaste or Puddle Flange Installation
|  | Ensure safewaste/puddle flange is installed to the correct height |  | Ensure safewaste or puddle flange is installed to the correct height | Safewaste or Puddle Flange Installation
|  | Spray all floor wastes to identify falls |  | Spray all floor wastes to identify falls | Safewaste or Puddle Flange Installation
|  | Ensure no open ends by installing dust cap/duct tape on risers |  | Ensure no open ends by installing dust cap or duct tape on risers | All Pipes & Casting Capped & Supported
|  | Ensure all sleeves installed in in situ walls at the correct height |  | Ensure all sleeves installed in in situ walls at the correct height | Pipe Sleeves
|  | Ensure pipes are clear of any obstructions prior to extending riser |  | Ensure pipes are clear of any obstructions prior to extending riser | Castin Downpipes
|  | Ensure pipe is fitted correctly where agreed by structural engineer |  | Ensure pipe is fitted correctly where agreed by structural engineer | Castin Downpipes
|  | Ensure pipes are wrapped where req. |  | Ensure pipes are wrapped where required | Castin Downpipes
|  | Ensure downpipes capped & taped to riser |  | Ensure downpipes capped and taped to riser | Castin Downpipes
|  | Ensure pipe is filled w/ water for concrete pour where req. |  | Ensure pipe is filled with water for concrete pour where required | Castin Downpipes
|  | Complete all req. inspections by third parties |  | Complete all required inspections by third parties (client, authorities, builder, etc) | Inspect Pipework
|  | Ensure photos are taken of entire installation inc fire collars & casting prior to concrete pour |  | Ensure photos are taken of entire installation inc fire collars and casting prior to concrete pour | Photos
|  | Works verified as conforming (McPherson Plumbing Representative) Name: |  | Works verified as conforming (McPherson Plumbing Representative) Name: | Photos
Drainage Services
| Scope |  |  | Drainage Services
Rows
|  | Level 13 | dynamic | Level 13 | Drainage Services | Site QA
|  | Level 14 | dynamic | Level 14 | Drainage Services | Site QA
|  | Level 15 | dynamic | Level 15 | Drainage Services | Site QA
|  | Level 16 | dynamic | Level 16 | Drainage Services | Site QA
|  | Level 17 | dynamic | Level 17 | Drainage Services | Site QA
|  | Level 18 | dynamic | Level 18 | Drainage Services | Site QA
|  | Level 19 | dynamic | Level 19 | Drainage Services | Site QA
|  | Level 20 | dynamic | Level 20 | Drainage Services | Site QA
|  | Level 21 | dynamic | Level 21 | Drainage Services | Site QA
|  | Level 22 | dynamic | Level 22 | Drainage Services | Site QA
|  | Level 23 | dynamic | Level 23 | Drainage Services | Site QA
|  | Level 24 | dynamic | Level 24 | Drainage Services | Site QA
|  | Level 25 | dynamic | Level 25 | Drainage Services | Site QA
|  | Level 26 | dynamic | Level 26 | Drainage Services | Site QA
|  | Level 27 | dynamic | Level 27 | Drainage Services | Site QA
|  | Level 28 | dynamic | Level 28 | Drainage Services | Site QA
|  | Level 29 | dynamic | Level 29 | Drainage Services | Site QA
|  | Level 30 | dynamic | Level 30 | Drainage Services | Site QA
|  | Level 31 | dynamic | Level 31 | Drainage Services | Site QA
|  | Level 32 | dynamic | Level 32 | Drainage Services | Site QA
|  | Level 33 | dynamic | Level 33 | Drainage Services | Site QA
|  | Level 34 | dynamic | Level 34 | Drainage Services | Site QA
|  | Level 35 | dynamic | Level 35 | Drainage Services | Site QA
Columns
|  | Check dimensions on drawings and record any remarks/deviations on as built drawings & take photo of title block |  | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block | Setout & Location
|  | Review wall set out plans and ensure pipe passes through wall square |  | Review wall set out plans and ensure pipe passes through wall square | Setout & Location
|  | Review interfacing services and ensure no clashes |  | Review interfacing services and ensure no clashes | Setout & Location
|  | Always set out off metre mark where applicable and when possible transfer for later reference |  | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern) | Setout & Location
|  | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating |  | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Pressure Services | Pressure Services | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Type | Type | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Install Brackets as req., check alignment and spacing as per manufacturer's spec. & applicable Australian Standard |  | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard | Bracketing, fittings & Noggins
|  | Ensure correct brackets are used dependant on material selected |  | Ensure correct brackets are used dependant on material selected | Bracketing, fittings & Noggins
|  | See extract from AS 3500.1 for water services |  | See extract from AS 3500.1 for water services | Bracketing, fittings & Noggins
|  | Ensure correct fittings are used as per pipe weights, element exposure & project spec. |  | Ensure correct fittings are used as per pipe weights, element exposure & project specification | Bracketing, fittings & Noggins
|  | Ensure all Noggins are installed prior to sheeting of walls |  | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel) | Bracketing, fittings & Noggins
|  | Ensure supports are installed min 600mm from penetrations through slabs/walls where insulation is req. |  | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required | Bracketing, fittings & Noggins
|  | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end |  | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end | Install Pipework
|  | Ensure sockets are primed and clean and apply a sufficient amount of Type N solvent cement |  | Ensure sockets are primed and clean and apply a sufficient amount of Type N solvent cement | Install Pipework
|  | Gently insert the pipe and fitting to full depth w/ a quarter turn & hold until joint sets |  | Gently insert the pipe and fitting to full depth with a quarter turn & hold until joint sets | Install Pipework
|  | Do not disturb joint for at least 5 minutes |  | Do not disturb joint for at least 5 minutes | Install Pipework
|  | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing |  | Wipe away any excess glue and inspect joint for soundness. Allow to cure for 24 hours before pressure testing | Install Pipework
|  | Allow for expansion joints & inspection openings as per as per AS3500 |  | Allow for expansion joints & inspection openings as per as per AS3500 | Install Pipework
|  | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end and ensure pipes & fittings are dry |  | Accurately measure length of pipe & cut square. De-burr inside & outside of cut end and ensure pipes & fittings are dry | Install Pipework
|  | Ensure constant power supply to the electrofusion welder as fittings can only be welded once |  | Ensure constant power supply to the electrofusion welder as fittings can only be welded once | Install Pipework
|  | Scrape the pipe section to the length of the insertion depth w/ emery cloth/manual scraper, removing oxidised layer |  | Scrape the pipe section to the length of the insertion depth with emery cloth or manual scraper, removing oxidised layer | Install Pipework
|  | Mark the insertion depth on the pipe and insert into the coupling. Ensure pipe is secured from movement |  | Mark the insertion depth on the pipe and insert into the coupling. Ensure pipe is secured from movement | Install Pipework
|  | Weld the joint to the manufactures process and allow to cool before applying force/testing |  | Weld the joint to the manufactures process and allow to cool before applying force or testing. | Install Pipework
|  | When welding has been performed correctly the protruding yellow/black indicator should be raised |  | When welding has been performed correctly the protruding yellow or black indicator should be raised | Install Pipework
|  | Plug and fill stack w/ water at expansion and gate and ensure plug is unable to release into pipe system |  | Plug and fill stack with water at expansion and gate and ensure plug is unable to release into pipe system | Test Pipework
|  | Gravity test of pipework for a minimum of 15 mins |  | Gravity test of pipework for a minimum of 15 mins | Test Pipework
|  | Tape gate and expansion and initial cap w/ date, stating 'TESTED' |  | Tape gate and expansion and initial cap with date, stating 'TESTED' | Test Pipework
|  | Photograph of riser clearing showing testing info |  | Photograph of riser clearing showing testing info | Test Pipework
|  | Complete all req. inspections by third parties |  | Complete all required inspections by third parties (client, authorities etc) | Inspect Pipework
|  | Apply correct pipe identity stickers to indicate flow direction |  | Apply correct pipe identity stickers to indicate flow direction | Acoustic Installation & Pipe Identification
|  | Apply thermal insulation to any hot water pipework. Thickness & type as per project spec. |  | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification | Acoustic Installation & Pipe Identification
|  | Photographic record to be kept of process. Take photos of entire installation |  | Photographic record to be kept of process. Take photos of entire installation | Photos
|  | Works verified as conforming (McPherson Plumbing Representative) |  | Works verified as conforming (McPherson Plumbing Representative) | Photos
Pressure Services
| Scope |  |  | Pressure Services
Rows
|  | Level 13 | dynamic | Level 13 | Pressure Services | Site QA
|  | Level 14 | dynamic | Level 14 | Pressure Services | Site QA
|  | Level 15 | dynamic | Level 15 | Pressure Services | Site QA
|  | Level 16 | dynamic | Level 16 | Pressure Services | Site QA
|  | Level 17 | dynamic | Level 17 | Pressure Services | Site QA
|  | Level 18 | dynamic | Level 18 | Pressure Services | Site QA
|  | Level 19 | dynamic | Level 19 | Pressure Services | Site QA
|  | Level 20 | dynamic | Level 20 | Pressure Services | Site QA
|  | Level 21 | dynamic | Level 21 | Pressure Services | Site QA
|  | Level 22 | dynamic | Level 22 | Pressure Services | Site QA
|  | Level 23 | dynamic | Level 23 | Pressure Services | Site QA
|  | Level 24 | dynamic | Level 24 | Pressure Services | Site QA
|  | Level 25 | dynamic | Level 25 | Pressure Services | Site QA
|  | Level 26 | dynamic | Level 26 | Pressure Services | Site QA
|  | Level 27 | dynamic | Level 27 | Pressure Services | Site QA
|  | Level 28 | dynamic | Level 28 | Pressure Services | Site QA
|  | Level 29 | dynamic | Level 29 | Pressure Services | Site QA
|  | Level 30 | dynamic | Level 30 | Pressure Services | Site QA
|  | Level 31 | dynamic | Level 31 | Pressure Services | Site QA
|  | Level 32 | dynamic | Level 32 | Pressure Services | Site QA
|  | Level 33 | dynamic | Level 33 | Pressure Services | Site QA
|  | Level 34 | dynamic | Level 34 | Pressure Services | Site QA
|  | Level 35 | dynamic | Level 35 | Pressure Services | Site QA
Columns
|  | Check dimensions on drawings and record any remarks/deviations on as built drawings & take photo of title block |  | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block | Setout & Location
|  | Review wall set out plans and ensure pipe passes through wall square |  | Review wall set out plans and ensure pipe passes through wall square | Setout & Location
|  | Review interfacing services and ensure no clashes |  | Review interfacing services and ensure no clashes | Setout & Location
|  | Always set out off metre mark where applicable and when possible transfer for later reference |  | Always set out off metre mark where applicable and when possible transfer for later reference (e.g inside inwall cistern) | Setout & Location
|  | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating |  | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Pressure Services | Pressure Services | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Type | Type | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Type of pipe | Type of pipe | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Type/Service | Type / Service | Review wall set out plans and ensure that bare pipe only is passing through fire rated walls to allow for fire rating | Setout & Location
|  | Install Brackets as req., check alignment and spacing as per manufacturer's spec. & applicable Australian Standard |  | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard | Bracketing, fittings & Noggins
|  | Ensure correct brackets are used dependant on material selected |  | Ensure correct brackets are used dependant on material selected | Bracketing, fittings & Noggins
|  | See extract from AS 3500.1 for water services |  | See extract from AS 3500.1 for water services | Bracketing, fittings & Noggins
|  | Ensure correct fittings are used as per pipe weights, element exposure & project spec. |  | Ensure correct fittings are used as per pipe weights, element exposure & project specification | Bracketing, fittings & Noggins
|  | Ensure all Noggins are installed prior to sheeting of walls |  | Ensure all Noggins are installed prior to sheeting of walls (e.g wall hung basin/shower rail/ fire hose reel) | Bracketing, fittings & Noggins
|  | Ensure supports are installed min 600mm from penetrations through slabs/walls where insulation is req. |  | Ensure supports are installed min 600mm from penetrations through slabs or walls where insulation is required | Bracketing, fittings & Noggins
|  | Measure accurate length & use appropriate copper tube cutter to ensure a clean square cut |  | Measure accurate length & use appropriate copper tube cutter to ensure a clean square cut. | Install Pipework
|  | Ream inside & outside of cut w/ reaming tool/file & clean w/ abrasive cloth |  | Ream inside & outside of cut with reaming tool or file & clean with abrasive cloth | Install Pipework
|  | Ensure pipe is pushed in to full insertion depth. For brass to copper joints ensure flux is applied prior to insertion |  | Ensure pipe is pushed in to full insertion depth. For brass to copper joints ensure flux is applied prior to insertion | Install Pipework
|  | Weld joint w/ correct amount of heat ensuring capillary action throughout & correct % silver solder used |  | Weld joint with correct amount of heat ensuring capillary action throughout & correct % silver solder is used. (min1.8) | Install Pipework
|  | Allow joint to cool naturally. Shock cooling may stress/crack the joint. Wipe off any left over flux residue |  | Allow joint to cool naturally. Shock cooling may stress or crack the joint. Wipe off any left over flux residue | Install Pipework
|  | Inspect the joint for soundness & pin holes |  | Inspect the joint for soundness and pin holes | Install Pipework
|  | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework |  | When installing non-potable services ensure pipework is not installed within 100 mm of any parallel drinking service pipework | Install Pipework
|  | Select appropriate tool for brand being used. Only use batteries supplied w/ tool & w/ not less than 40% charge |  | Select appropriate tool for brand being used. Only use batteries supplied with tool & with not less than 40% charge | Install Pipework
|  | Use appropriate copper tube cutter to ensure a clean square cut |  | Use appropriate copper tube cutter to ensure a clean square cut. | Install Pipework
|  | Ensure cut end is clean & free from any scratches/damage such as dents/deformity |  | Ensure cut end is clean and free from any scratches or damage such as dents or deformity. | Install Pipework
|  | Ensure that the internal & external tube end is completely free from burrs/sharp edges by using a deburring tool |  | Ensure that the internal and external tube end is completely free from burrs or sharp edges by using a deburring tool | Install Pipework
|  | Before inserting the tube, check O-Rings for correct placement & that they are free of damage/debris |  | Before inserting the tube, check O-Rings for correct placement and that they are free of damage or debris. | Install Pipework
|  | Apply insertion depth mark w/ pen to the tube prior to insertion into the fitting. |  | Apply insertion depth mark with pen to the tube prior to insertion into the fitting. | Install Pipework
|  | Tube to be inserted Parallel into the fitting , ensuring the insertion mark is visible & in line w/ fitting end |  | Tube to be inserted Parallel into the fitting , ensuring the insertion mark is visible and in line with fitting end | Install Pipework
|  | Place jaw over the fitting, correctly aligned & positioned & activate tool to press the joint |  | Place jaw over the fitting, correctly aligned and positioned and activate tool to press the joint | Install Pipework
|  | Tool should complete the correct cycle & the jaw ends should fully close on completion. |  | Tool should complete the correct cycle and the jaw ends should fully close on completion. | Install Pipework
|  | If the tool does not complete the req. cycle during operation the fitting should be cut out, replaced then repressed |  | If the tool does not complete the required cycle during operation the fitting should be cut out, replaced then repressed. | Install Pipework
|  | No fitting should be pressed more than once |  | No fitting should be pressed more than once | Install Pipework
|  | Ensure appropriately coloured pipework is installed |  | Ensure appropriately coloured pipework is installed (Hot= Red, Cold= Black) | Install Pipework
|  | Cut pipe cleanly & squarely using PE-X Pipe Cutters. Place beveled end of the sleeve facing outwards toward joint |  | Cut pipe cleanly and squarely using PE-X Pipe Cutters. Place beveled end of the sleeve facing outwards toward joint | Install Pipework
|  | Expand the pipe twice only using the approved Expanding Tool |  | Expand the pipe twice only using the approved Expanding Tool | Install Pipework
|  | Insert the fitting into the expanded end of the pipe until the fitting reaches the pipe stop |  | Insert the fitting into the expanded end of the pipe until the fitting reaches the pipe stop. | Install Pipework
|  | Slide the jointing sleeve towards the fitting. Position the jointing sleeve & the fitting squarely within the jaws of the Compression Tool |  | Slide the jointing sleeve towards the fitting. Position the jointing sleeve and the fitting squarely within the jaws of the Compression Tool. | Install Pipework
|  | Draw the sleeve towards the fitting by closing the jaws of the Compression Tool until the sleeve reaches the shoulder of the fitting |  | Draw the sleeve towards the fitting by closing the jaws of the Compression Tool until the sleeve reaches the shoulder of the fitting. | Install Pipework
|  | Ensure pipework is not installed in the path of future fittings |  | Ensure pipework is not installed in the path of future fittings (sheeting screws, bathroom accessory fittings etc.) | Install Pipework
|  | Where practical, arrange for pipework to be pre-cut & grooved off site |  | Where practical, arrange for pipework to be pre-cut and grooved off site | Install Pipework
|  | Ensure pipe is cut squarely w/ a fit for purpose tool |  | Ensure pipe is cut squarely with a fit for purpose tool | Install Pipework
|  | Assure manufactured roll grooved ends of pipework are measured for appropriate circumference using approved tape measure |  | Assure manufactured roll grooved ends of pipework are measured for appropriate circumference using approved tape measure | Install Pipework
|  | Ensure pipe cut on-site is grooved to req. depth & check w/ approved tape measure |  | Ensure pipe cut on-site is grooved to required depth & check with approved tape measure | Install Pipework
|  | Ensure pipe length is correct. Don't use coupling to pull incorrect pipe lengths together |  | Ensure pipe length is correct. Don't use coupling to pull incorrect pipe lengths together | Install Pipework
|  | Lubricate & install inner coupling for connection of pipe & fittings, ensuring it is lapped over each connection point |  | Lubricate and install inner coupling for connection of pipe and fittings, ensuring it is lapped over each connection point | Install Pipework
|  | tighten outer metal band gradually & evenly to a torque of the manufacturer's spec. |  | tighten outer metal band gradually and evenly to a torque of the manufacturer's specification | Install Pipework
|  | Ensure a gap no more than 2 mm is evident on joining portions of outer coupling |  | Ensure a gap no more than 2 mm is evident on joining portions of outer coupling | Install Pipework
|  | Inspect fitting/pipe after roll groove collar tightening to ensure it is square & aligned |  | Inspect fitting / pipe after roll groove collar tightening to ensure it is square and aligned | Install Pipework
|  | Photographic record to be kept of process. Take photos of gauges before and after |  | Photographic record to be kept of process. Take photos of gauges before and after | Test Pipework
|  | Pump test pipework to req. kpa and time period as per AS 3500 & AS5601.1 |  | Pump test pipework to required kpa and time period as per AS 3500 & AS5601.1 | Test Pipework
|  | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines |  | For water test pipework to 1500 kpa for a period of not less than 30 mins. Ensure no air left in pipelines | Test Pipework
|  | For reduced pressure water systems test pipework to manufacturer's spec. kpa & time period |  | For reduced pressure water systems test pipework to manufacturer's specification kpa & time period | Test Pipework
|  | For Gas Installations Test pipework to min 7 Kpa/1.5 times the working pressure whichever is greater for min 5 min period |  | For Gas Installations Test pipework to min 7 Kpa or 1.5 times the working pressure whichever is greater for min 5 min period | Test Pipework
|  | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins/specified time & pressure |  | For Fire Service Installations Test pipework to min 1700 Kpa for 30 mins or specified time & pressure | Test Pipework
|  | Complete all req. inspections by third parties |  | Complete all required inspections by third parties (client, authorities etc) | Inspect Pipework
|  | Apply correct pipe identity stickers to indicate flow direction |  | Apply correct pipe identity stickers to indicate flow direction | Pipe Insulation & Identification
|  | Apply thermal insulation to any hot water pipework. Thickness & type as per project spec. |  | Apply thermal insulation to any hot water pipework. Thickness & type as per project specification | Pipe Insulation & Identification
|  | Photographic record to be kept of process. Take photos of entire installation |  | Photographic record to be kept of process. Take photos of entire installation | Photos
|  | Works verified as conforming (McPherson Plumbing Representative) |  | Works verified as conforming (McPherson Plumbing Representative) | Photos
Meter & Valves
| Scope |  |  | Meter & Valves
Rows
|  | Meter & Valves | dynamic | Meter & Valves | Site QA
Columns
|  | Check dimensions on drawings and record any remarks/deviations on as built drawings & take photo of title block |  | Check dimensions on drawings and record any remarks / deviations on as built drawings & take photo of title block | Setout & Location
|  | Setout of meter/valve installed as per authority & project reqs., Height & specials |  | Setout of meter/valve installed as per authority & project requirements, Height & specials | Setout & Location
|  | Setout of meter/valve installed as per project reqs., Height & specials |  | Setout of meter/valve installed as per project requirements, Height & specials | Setout & Location
|  | Meter located as per Authority reqs. |  | Meter located as per Authority requirements | Setout & Location
|  | Hydraulic Service Meter Valves | Hydraulic Service Meter Valves | Meter located as per Authority requirements | Setout & Location
|  | Service | Service | Meter located as per Authority requirements | Setout & Location
|  | Install Brackets as req., check alignment and spacing as per manufacturer's spec. & applicable Australian Standard |  | Install Brackets as required, check alignment and spacing as per manufacturer's specification & applicable Australian Standard | Bracketing, fittings & Supports
|  | Ensure correct brackets are used dependant on pump selected |  | Ensure correct brackets are used dependant on pump selected | Bracketing, fittings & Supports
|  | Pipework supported independently of pump assembly |  | Pipework supported independently of pump assembly | Bracketing, fittings & Supports
|  | Ensure correct fittings are used as per pump/plant weights, element exposure & project spec. |  | Ensure correct fittings are used as per pump/plant weights, element exposure & project specification | Bracketing, fittings & Supports
|  | Ensure acoustic mounts/brackets are used as per acoustic spec |  | Ensure acoustic mounts/brackets are used as per acoustic spec | Bracketing, fittings & Supports
|  | Flush all lines where possible prior to installation |  | Flush all lines where possible prior to installation | Install of Valves / Meters
|  | Install Valve/ Meter as per authority/manufacturer's reqs. |  | Install Valve/ Meter as per authority/manufacturer's requirements | Install of Valves / Meters
|  | Mounting of valve/ meter at a serviceable height and location where req. as well as vertical & plumb |  | Mounting of valve/ meter at a serviceable height and location where required as well as vertical & plumb | Install of Valves / Meters
|  | Valve Installed as per standards |  | Valve Installed as per standards (Height, proximity to other services/ walls etc) | Install of Valves / Meters
|  | Unions, Isolation Valves, Strainers, Drains etc installed where req. for servicing & as per manufacturer's spec. |  | Unions, Isolation Valves, Strainers, Drains etc installed where required for servicing & as per manufacturer's specification | Install of Valves / Meters
|  | Teflon joints used over loxeal where servicing is req. |  | Teflon joints used over loxeal where servicing is required (loxeal used on male threads only) | Install of Valves / Meters
|  | Isolation valves installed as per meter/valve reqs. |  | Isolation valves installed as per meter/valve requirements | Install of Valves / Meters
|  | Petes Plug Valves installed as per Authority reqs. |  | Petes Plug Valves installed as per Authority Requirements | Install of Valves / Meters
|  | Valve/ Meter installed in the correct orientation |  | Valve/ Meter installed in the correct orientation (check for directional arrow) | Install of Valves / Meters
|  | Install identification/service tags to authority/project specs. |  | Install identification/service tags to authority/project specifications | Install of Valves / Meters
|  | Pressure Reduction valve tested for accuracy on outlet pipework as per manufacturer's spec. |  | Pressure Reduction valve tested for accuracy on outlet pipework as per manufacturer's specification | Testing
|  | Tempering valve outlet temperature checked for 50 degrees max or as per manufacturer/project reqs. |  | Tempering valve outlet temperature checked for 50 degrees max or as per manufacturer/ project requirements | Testing
|  | Check that no leaks on unions or valve threads |  | Check that no leaks on unions or valve threads | Testing
|  | Test valve and commision as per manufacturer's reqs. |  | Test valve and commision as per manufacturer's requirements | Testing
|  | Clean all strainers/dirt box from debris |  | Clean all strainers/dirt box from debris | Testing
|  | Complete all req. inspections by third parties |  | Complete all required inspections by third parties (client, authorities etc) | Inspect Pipework
|  | Photographic record to be kept of process. Take photos of entire installation |  | Photographic record to be kept of process. Take photos of entire installation | Photos
|  | Works verified as conforming (McPherson Plumbing Representative) |  | Works verified as conforming (McPherson Plumbing Representative) | Photos
Temperature Control Devices
| Scope |  |  | Temperature Control Devices
Rows
|  | Temperature Control Devices | dynamic | Temperature Control Devices | Site QA
Columns
|  | Document attached |  | Please attach document
Back Flow Prevention Devices
| Scope |  |  | Back Flow Prevention Devices
Rows
|  | Back Flow Prevention Devices | dynamic | Back Flow Prevention Devices | Site QA
Columns
|  | Document attached |  | Please attach document
PC Commissioning & installation
| Scope |  |  | PC Commissioning & installation
Rows
|  | PC Commissioning & installation | dynamic | PC Commissioning & installation | Site QA
Columns
|  | Water Meters Installed - Cold, Hot, Non - Potable, Gas - Take picture of meters |  | Water Meters Installed - Cold, Hot, Non - Potable, Gas - Take picture of meters | Water
|  | Time taken to get hot water at most disadvantaged fixture |  | Time taken to get hot water at most disadvantaged fixture | Water
|  | Hot & Cold water isolation valve test for cross conn. |  | Hot & Cold water isolation valve test for cross connection | Water
|  | Non-Potable water isolation valve test for cross conn. |  | Non-Potable water isolation valve test for cross connection | Water
|  | Tempering valve set to req. temperature Set temp - |  | Tempering valve set to required temperature (50 max for residential for tmv use ITP #9) Set temp - | Water
|  | Pressure reduction valves set to req. pressure |  | Pressure reduction valves set to required pressure (500 kpa max for fixtures) Take picture of valves and comment (Cold Water PRV KPA, Hot Water PRV KPA) | Water
|  | Sink Installed - Secure & damage free |  | Sink Installed - Secure & damage free (photo) | Kitchen
|  | Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Mixer Installed - Tested/ secured/ cross connection check/ aerator clear/ damage free, ( photo ) | Kitchen
|  | Trap installed & tested, Tundish Installed & test |  | Trap installed & tested, Tundish Installed & test | Kitchen
|  | AAV installed with allowance for servicing/replacement |  | AAV installed with allowance for servicing/replacement | Kitchen
|  | Dishwasher Installed |  | Dishwasher Installed | Kitchen
|  | DW QA - Cycle Run/Water conn. Ok/tight/secured/Waste conn.- Ok/tight/secured/drilled out |  | DW QA - Cycle Run / Water Connection Ok/tight/secured / Waste Connection- Ok/tight/secured/drilled out | Kitchen
|  | Zip Tap - Commission zip tap & unit as per zip commisioning process |  | Zip Tap - Commission zip tap & unit as per zip commisioning process | Kitchen
|  | Zip Tap - Check zip unit for no leaks & power on |  | Zip Tap - Check zip unit for no leaks & power on | Kitchen
|  | External Hose Tap Installed - Potable, Non-Potable - Installed plumb & damage free |  | External Hose Tap Installed - Potable, Non-Potable - Installed plumb and damage free | Winter Garden / Balcony
|  | Balcony Outlet - Clear & Free of debris |  | Balcony Outlet - Clear & Free of debris (photo) | Winter Garden / Balcony
|  | Gas Cooktop Installed - Secured & damage free |  | Gas Cooktop Installed - Secured & damage free (photo) | Winter Garden / Balcony
|  | Gas Flexi/Isolation Valve/Regulator/Loxeal used on all parallel threads/Gas tape on reg thread |  | Gas Flexi / Isolation Valve / Regulator / Loxeal used on all parallel threads / Gas tape on reg thread (photo) | Winter Garden / Balcony
|  | Purge & Commision cook top as per manufacturer's specs. & AS5601 |  | Purge & Commision cook top as per manufacturer's specifications and AS5601 | Winter Garden / Balcony
|  | Bayonet points installed - Internal/External/Installed plumb & damage free |  | Bayonet points installed - Internal / External / Installed plumb & damage free | Winter Garden / Balcony
|  | Tub/Sink Installed - Secure & damage free |  | Tub/Sink Installed - Secure & damage free (photo) | Laundry
|  | Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Mixer Installed - Tested/ secured/ cross connection check/ aerator clear/ damage free, ( photo ) | Laundry
|  | Trap installed & tested, Tundish Installed & test |  | Trap installed & tested, Tundish Installed & test | Laundry
|  | AAV installed with allowance for servicing/replacement |  | AAV installed with allowance for servicing/replacement | Laundry
|  | Washing Machine Installed |  | Washing Machine Installed | Laundry
|  | WM QA - Cycle Run/Water conn. Ok/tight/secured/Waste conn.- Ok/tight/secured/drilled out |  | WM QA - Cycle Run / Water Connection Ok/tight/secured / Waste Connection- Ok/tight/secured/drilled out | Laundry
|  | Floor Waste - Clear & Free from debris |  | Floor Waste - Clear & Free from debris (photo) | Laundry
|  | Main Bathroom - Floor Waste - Clear & Free from debris |  | Floor Waste - Clear & Free from debris (photo) | Main Bathroom
|  | Main Bathroom - WC Installed -/Silicone/Seat - Secure & damage free |  | WC Installed - / Silicone / Seat - Secure & damage free (photo) | Main Bathroom
|  | Main Bathroom - Flush Plate installed Plumb & damage free |  | Flush Plate installed Plumb and damage free (photo) | Main Bathroom
|  | Main Bathroom - WC Tested |  | WC Tested (minimum 10 flushes and inspect under pan for leaks) | Main Bathroom
|  | Main Bathroom - Basin Installed/Silicone - Secure & damage free |  | Basin Installed / Silicone - Secure & damage free (photo) | Main Bathroom
|  | Main Bathroom - Basin Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Main Bathroom
|  | Main Bathroom - Plug & Waste Installed/Trap installed & tested/Tundish Installed |  | Plug & Waste Installed / Trap installed & tested / Tundish Installed | Main Bathroom
|  | Main Bathroom - Shower Installed - Mixer Trim Kit/Rail/Hand Shower & Hose/Rose/Rain Head |  | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head | Main Bathroom
|  | Main Bathroom - Shower Set Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Main Bathroom
|  | Main Bathroom - Shower Waste - Clear & Free from debris |  | Shower Waste - Clear & Free from debris (photo) | Main Bathroom
|  | Main Bathroom - Bath Installed - Inset/Free Standing/Silicone - Secure & damage free |  | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo) | Main Bathroom
|  | Main Bathroom - Bath Mixer Installed - Wall/Floor/Tested/secured/cross conn. check/aerator clear/damage free |  | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Main Bathroom
|  | Main Bathroom - Plug & Waste Installed/Trap installed & tested/Bath Filled & Leak Checked |  | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked | Main Bathroom
|  | Main Bathroom - Photos Uploaded or saved to appropriate location |  | Photos Uploaded or saved to appropriate location | Main Bathroom
|  | Main Bathroom - Works verified as conforming |  | Works verified as conforming (McPherson Plumbing Representative) | Main Bathroom
|  | Ensuite Bathroom 1 - Floor Waste - Clear & Free from debris |  | Floor Waste - Clear & Free from debris (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - WC Installed -/Silicone/Seat - Secure & damage free |  | WC Installed - / Silicone / Seat - Secure & damage free (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Flush Plate installed Plumb & damage free |  | Flush Plate installed Plumb and damage free (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - WC Tested |  | WC Tested (minimum 10 flushes and inspect under pan for leaks) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Basin Installed/Silicone - Secure & damage free |  | Basin Installed / Silicone - Secure & damage free (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Basin Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Plug & Waste Installed/Trap installed & tested/Tundish Installed |  | Plug & Waste Installed / Trap installed & tested / Tundish Installed | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Shower Installed - Mixer Trim Kit/Rail/Hand Shower & Hose/Rose/Rain Head |  | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Shower Set Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Shower Waste - Clear & Free from debris |  | Shower Waste - Clear & Free from debris (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Bath Installed - Inset/Free Standing/Silicone - Secure & damage free |  | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Bath Mixer Installed - Wall/Floor/Tested/secured/cross conn. check/aerator clear/damage free |  | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Plug & Waste Installed/Trap installed & tested/Bath Filled & Leak Checked |  | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Photos Uploaded or saved to appropriate location |  | Photos Uploaded or saved to appropriate location | Ensuite Bathroom 1
|  | Ensuite Bathroom 1 - Works verified as conforming |  | Works verified as conforming (McPherson Plumbing Representative) | Ensuite Bathroom 1
|  | Ensuite Bathroom 2 - Floor Waste - Clear & Free from debris |  | Floor Waste - Clear & Free from debris (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - WC Installed -/Silicone/Seat - Secure & damage free |  | WC Installed - / Silicone / Seat - Secure & damage free (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Flush Plate installed Plumb & damage free |  | Flush Plate installed Plumb and damage free (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - WC Tested |  | WC Tested (minimum 10 flushes and inspect under pan for leaks) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Basin Installed/Silicone - Secure & damage free |  | Basin Installed / Silicone - Secure & damage free (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Basin Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Plug & Waste Installed/Trap installed & tested/Tundish Installed |  | Plug & Waste Installed / Trap installed & tested / Tundish Installed | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Shower Installed - Mixer Trim Kit/Rail/Hand Shower & Hose/Rose/Rain Head |  | Shower Installed - Mixer Trim Kit / Rail / Hand Shower & Hose /Rose/Rain Head | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Shower Set Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Shower Set Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Shower Waste - Clear & Free from debris |  | Shower Waste - Clear & Free from debris (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Bath Installed - Inset/Free Standing/Silicone - Secure & damage free |  | Bath Installed - Inset / Free Standing / Silicone - Secure & damage free (photo) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Bath Mixer Installed - Wall/Floor/Tested/secured/cross conn. check/aerator clear/damage free |  | Bath Mixer Installed - Wall / Floor / Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Plug & Waste Installed/Trap installed & tested/Bath Filled & Leak Checked |  | Plug & Waste Installed / Trap installed & tested / Bath Filled & Leak Checked | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Photos Uploaded or saved to appropriate location |  | Photos Uploaded or saved to appropriate location | Ensuite Bathroom 2
|  | Ensuite Bathroom 2 - Works verified as conforming |  | Works verified as conforming (McPherson Plumbing Representative) | Ensuite Bathroom 2
|  | Powder Room Bathroom - Floor Waste - Clear & Free from debris |  | Floor Waste - Clear & Free from debris (photo) | Powder Room Bathroom
|  | Powder Room Bathroom - WC Installed -/Silicone/Seat - Secure & damage free |  | WC Installed - / Silicone / Seat - Secure & damage free (photo) | Powder Room Bathroom
|  | Powder Room Bathroom - Flush Plate installed Plumb & damage free |  | Flush Plate installed Plumb and damage free (photo) | Powder Room Bathroom
|  | Powder Room Bathroom - WC Tested |  | WC Tested (minimum 10 flushes and inspect under pan for leaks) | Powder Room Bathroom
|  | Powder Room Bathroom - Basin Installed/Silicone - Secure & damage free |  | Basin Installed / Silicone - Secure & damage free (photo) | Powder Room Bathroom
|  | Powder Room Bathroom - Basin Mixer Installed - Tested/secured/cross conn. check/aerator clear/damage free |  | Basin Mixer Installed - Tested/ secured/ cross connection check / aerator clear/ damage free, ( photo ) | Powder Room Bathroom
|  | Powder Room Bathroom - Plug & Waste Installed/Trap installed & tested/Tundish Installed |  | Plug & Waste Installed / Trap installed & tested / Tundish Installed | Powder Room Bathroom
|  | Powder Room Bathroom - Photos Uploaded or saved to appropriate location |  | Photos Uploaded or saved to appropriate location | Powder Room Bathroom
|  | Powder Room Bathroom - Works verified as conforming |  | Works verified as conforming (McPherson Plumbing Representative) | Powder Room Bathroom