## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
95d50195-4288-4b00-940b-b10f405b6a72 | checklist | RR-SEPD-BESS-FIC-008-01 - Cable Trench Culverts |  | RR-SEPD-BESS-FIC-008-01 - Cable Trench Culverts
2ae94fac-561a-432d-8071-ba6b5e9b9a2b | section | Part 1 – Preliminaries (photos where applicable)
f21cc7e0-39c7-4ccb-a536-c948ec59d2f4 | checkpoint | Review of approved construction drawings and specifications
cb718378-383f-5835-95d2-5c20776940f5 | note | All drawings and specifications approved and up to date
0c33a736-e9af-58b8-93f8-379b0fa71445 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
5d932a5c-6dfc-4449-a3ed-9855e52d5dc1 | checkpoint | Verification of permits
b9dbdf1f-67ce-52d6-b284-890eaf6300ed | note | All relevant permits (GDA/GDP) in place
92e51176-1803-54ff-92f3-67688631082d | note | Specifications/Drawings Reference - GDA/GDP
072fd7b3-4fe8-4373-9e8f-82f46a26f103 | checkpoint | Site access and safety preparation
403612cb-5062-5499-9766-951f4b397228 | note | Site access cleared and made safe
19e8ccda-224d-5ab6-9c42-14c3055972f7 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
3b128f99-24ab-4c90-add9-bb43e3519cf7 | checkpoint | Safety inductions and toolbox talks
94fd209b-98e4-5cf2-a00b-444a9f7ab0b9 | note | All personnel inducted; safety briefings completed
8994113f-b292-5bc7-b9e5-1ab57ac56390 | note | Specifications/Drawings Reference - Induction record
9db54fbd-9bf1-4432-956b-e876d8ac618b | checkpoint | Environmental controls in place
7018b55a-89bb-5924-9968-58b83cdc1318 | note | Dust, noise, and sediment barriers installed and functioning
3dd6cb84-4212-5f30-b575-31493717f25a | note | Specifications/Drawings Reference - SEPD environmental requirements
e33c085a-3bca-4233-a37b-ab36cac92bde | section | Part 2 – Excavation and trenching (photos where applicable)
658def57-c7ff-47d2-9df8-4fa67221fae0 | checkpoint | Trench depth and width comply with design
b1c07366-bb72-59b5-a7e6-80af239e93a5 | note | Set-out verified and matches IFC drawings
58dd21b1-4135-5e15-963a-4bcb3be9fb06 | note | Specifications/Drawings Reference - Site IFC Drawings AS/NZS 3500
959efc0f-348e-4f1c-bed8-8fbaef869bc8 | checkpoint | Stable trench walls (benching, battering)
82933834-21a5-5116-a62a-6835df7b8279 | note | Trenches deeper than 1.5m require benching or battering unless certified by a geotechnical engineer.
b734c6e7-b81b-51d1-a2af-89c126ae084e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006 AS 4744
b29fa775-7f37-4d2f-a2b4-593babb15f8a | checkpoint | Culverts inspected for defects before installation
548bdc19-2861-5de5-8476-a35228514d09 | note | Material certs from manufacturer and visual inspection
97cd703d-75c4-5538-bd1d-c9a0e29c6dae | note | Material to align with design drawings and load rating
719698d4-7e9e-59b6-91ac-a133358f760f | note | Specifications/Drawings Reference - Manufacturer certifications
085d368f-3229-4375-8767-fb7c205334ea | checkpoint | No water accumulation in trenches
1fb8e1fc-4f09-535f-879b-4bc035141d63 | note | No standing water or excessive moisture inside the trench.
d9ddb00d-2c66-5d64-8660-e6b3990eb1c9 | note | Specifications/Drawings Reference - AS/NZS 3500
c2d3c094-aead-418d-9a28-dbde934d62ad | checkpoint | Spoil stockpiles located at least 1m from trench edges
45cb9963-bd3f-52b1-aa54-4cacaa87a5ce | note | Stockpiles away from excavation to maintain safety of batters
9a94baa1-7ee0-54fe-908d-e89cc38f01f2 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
7362176b-b0e0-4232-a32d-523bd17b6440 | checkpoint | Correct bedding material used (sand, gravel, etc.)
a96b7642-5d74-5777-8324-d0821307f218 | note | Material complies with particle size, moisture content, MMDD
4b0ba86d-72a1-5f89-bf33-fa49705fe909 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Test material results
bf88ab8c-9727-465b-a341-eb6b1842a126 | checkpoint | Bedding installed and screeded to correct heights
6bbfbaa4-582f-5a74-9dba-1090c3d65ebf | note | Installed to design levels & alignment +-20mm
4ff5f106-d37a-536f-adbe-0f802a51f654 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
1fa1b70f-c4ec-4581-9594-b6cd63fe898a | section | Part 3 – Culvert Installation (photos where applicable)
bd2be6b0-d0a3-4252-ac5f-60b135ebd759 | checkpoint | Culverts laid at correct grade and alignment
95e009dc-8ce5-5ee1-8834-c7ab7f810c7a | note | Levels and grading match design tolerances (+/- 20mm)
5a66f055-242c-5dc0-b7db-e2f464030749 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006, Survey Report
f7955b7c-1f2f-42aa-98d0-15d904ee9705 | checkpoint | Joints between culverts sealed as specified
d4077d6b-9c37-5c21-9ef7-35fd2e22ecf5 | note | Joints must be fully engaged and sealed as per manufacturer specifications:
| note | — 10mm nominal gap
| note | — Backing rod or equivalent installed
| note | — Bostik SealnFlex P590 installed between culverts
| note | — Proofex S Tape installed over sealant
1e3a822c-6fc8-5b67-920a-3588d01e4f1e | note | Specifications/Drawings Reference - Manufacturer specifications
48085826-5f20-4c07-bf16-cdc949c11b3e | checkpoint | Concrete Lid Installation
fa901a0c-3756-5b72-b46e-738969ce988d | note | Installed on top of packers and sealan
9cdeee9a-b520-564b-aecc-0558a829b346 | note | Specifications/Drawings Reference - AS/NZS 3500
e18fb33f-9cb9-4e82-9bb7-4520ae41af56 | checkpoint | Joints between lids sealed as specified
d13f0369-1381-50e1-bbc2-fa380b52a341 | note | Joints must be fully engaged and sealed as per manufacturer specifications:
| note | — Nominal 10mm gap
| note | — Backing rod or equivalent installed
| note | — Bostik SealnFlex P590 installed to outside longitudinal joint both sides of lid
| note | — Bostik SealnFlex P590 installed to outside tranversal joints in-between lids
25f596d7-394b-5bda-a229-74d4e28426fe | note | Specifications/Drawings Reference - Manufacturer specifications
42b075cd-4474-421e-aac7-1c1dbfc24a85 | checkpoint | Reinforcement Protection
2d9816a9-24dd-5851-8333-5717b12e0bca | note | Apply 5mm layer of Megapoxy P1 or approved equivalent
617fba79-934d-5004-8133-6bfe65b6d5fd | note | Specifications/Drawings Reference - Manufacturer Specifications
d9f763bc-f094-4c48-a608-6199003fb9b4 | section | Part 4 – Backfilling and compaction (photos where applicable)
0fd7f223-59db-4a4d-ad61-24a93effd044 | checkpoint | Initial backfill material placed evenly around culverts
5791cb97-0f7b-5e72-a59f-727bf18db83c | note | Backfill installed evenly in controlled lifts on either side of culverts
1baab585-5e09-5a2f-96d7-4c03ee0f924c | note | Specifications/Drawings Reference - Geotechnical report AS/NZS 3725
0b029630-caa0-4b7b-9048-ca07dd378d8b | checkpoint | No large rocks or debris in backfill
d41b5c7f-a996-5230-9f4e-ab6c8e29f512 | note | No rocks or debris in backfill
27f7ccac-afb5-5acd-aeda-27bb24ac63c5 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
f6b120c2-963a-4db8-9c2c-9e2fc959a8fd | checkpoint | Backfilling in controlled layers (300mm lifts)
3dc94cf5-7329-58c6-98d4-25c9a7c073ba | note | Backfilling activities to be conducted as per:
| note | — Stab sand mass fill if access or program constraints requires it
| note | — Site won fill with uniform layers of maximum 300mm thickness
24a29b4c-b186-518b-a233-b954794915aa | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
21da1d1e-bb3e-4fe7-968d-382d924bab43 | checkpoint | Compaction tests performed and passed.
8ee89392-06e9-5b1b-bbf0-c2b724128d94 | note | Compacted as per specifications
4979a7a9-25cd-5c39-ab6c-78ee9ce56cb9 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 AS 1289
29b505bf-0c4d-4972-aa13-65cf8d142efe | checkpoint | Surface reinstated as per project specs (concrete, asphalt, topsoil)
f57fdebb-b048-56a0-9a5d-f3de848a8217 | note | Backfill to match existing ground levels with ±10mm tolerance.
9fe5965a-ca7e-5e3a-a2ec-93052d5e0919 | note | Specifications/Drawings Reference - IFC drawings
4be28d8b-d60a-485a-a5ab-9e22f25a021b | section | Part 5 – Final inspections and acceptance (photos where applicable)
d3c22932-3cd2-4762-b776-6c9d902c10a5 | checkpoint | As-built survey verification
309c4f39-e779-54f4-87d2-21a0d6dca33b | note | As-built levels and layout of installed structures match design and comply with tolerances
4230e8db-6b2d-57b6-bf12-bdce8bb5d98b | note | Specifications/Drawings Reference - As-Built Drawings, Survey Report WBS-SS-CI-SPC-0006
41055941-19f8-49ca-a431-053927524bc6 | checkpoint | Final inspection & Punch List sign-off
0251ef89-221e-53fe-890f-7ac74ea2d72e | note | Works inspected with the client and Punch List items (if applicable) closed out
602fe3cb-2adb-50ed-9227-be6a3eed1d0e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
dc515c72-64d9-4e36-9169-a00eaa55a822 | section | Document Sign-off
f596c94b-2621-4d11-bacd-3f5cbe0f9f30 | checkpoint | Prepared by:
2f5a64e9-0e9c-5938-a1da-f0c932f10fdf | textbox | ROBAR - Name:
1701c3c6-917b-5e9e-bbca-eba40cf67f97 | textbox | ROBAR - Position:
ac1e971d-b668-536d-ae2e-8b9d70390dc6 | date | Date:
cda45600-ac76-4bcb-9186-bd678f84cbe0 | signoff | Add Signature