## Table 1
Bechtel Processing Pad – INSPECTION AND TEST PLAN
Details
ITP Activity: |  |  | Subgrade Preparation | [8 empty] | Project: |  |  |  |  | EVA Copper |  |  |  |  | Date Lot Opened:
ITP Number: |  |  | EVAMP001-THS- QA-ITP-0013 |  |  |  | Rev. No. |  |  | A |  | Contract Number: | [9 empty] | Date Lot Closed:
Lot Number: | [11 empty] | Client: |  |  |  |  | Harmony
Location or Area: |  |  | Processing Pad | [8 empty] | Client Reference: | [9 empty] | JSA/SWMS Ref:
Chainage / Coordinates: | [11 empty] | Contractor / Subcontractor / Supplier: | [9 empty] | SOP Reference:
No. | Inspection / Test Point |  |  | Responsibility |  |  | Method |  |  | Conformance Criteria |  |  |  | Specification Clause |  | Frequency |  |  | Verification from Thiess / Inspector (H/W/R/M) |  |  |  |  | Records or Comments
[19 empty] | THIESS (Initial) |  |  | Inspector (Initial)
1 | Pre-Construction
1 | Drawings supplied most current IFC Retrieved from InEight |  |  | ENG |  |  | Visual |  |  | Reviewed drawing register |  |  |  | Reviewed drawing register |  | Prior to works |  |  | HP |  |  | W
2 | Management Plans submitted and approved as per PMP |  |  | ENG |  |  | Visual |  |  | Approved Package MP’s |  |  |  | Approved Package MP’s |  | Prior to works |  |  | HP |  |  | W
3 | Inspection Test Plan (ITP) submitted and approved |  |  | ENG |  |  | Visual |  |  | Approved ITP revision |  |  |  | Approved ITP revision |  | Prior to works |  |  | HP |  |  | W
4 | Lot Register/ WBS submitted and approved |  |  | ENG |  |  | Visual |  |  | Approved WBS |  |  |  | Approved WBS |  | Prior to works |  |  | W |  |  | W
5 | Check existing services and dial before you dig |  |  | ENV/ENG |  |  | Visual |  |  | Approved erosion and sediment control plan |  |  |  | EVAMP001-EVA- EN-PLA-0001 |  | Prior to works |  |  | HP |  |  | HP
6 | Underlying lot & ITP signed off and conforming |  |  | ENG |  |  | Visual |  |  | Topsoil stripping ITP signed off |  |  |  | Approved QMP |  | Prior to works |  |  | HP |  |  | W
2 | Construction
7 | Removal and replacement of unsuitable material |  |  | SV |  |  |  | Visual |  | Where directed by the client’s representative remove and replace unsuitable material and dispose to waste at an approved location or as shown on the drawings. |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 rev0 Clauses 3.5.6 Unsuitable Material & 3.5.7 Disposal of Materials |  | As required |  |  | HP |  |  | HP
8 | CBR values of subgrades under pavements, buildings & structures |  |  | ENG |  |  |  | Test |  | The materials exposed at subgrade level of cuttings are to have a minimum CBR of 3. If CBR >3: CBR 2 excavate 150 mm below subgrade level and replace with compacted selected fill (minimum CBR 10). CBR 1 excavate 250 mm below subgrade level and replace with compacted selected fill (minimum CBR 10) |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 rev0 Clause 3.9.4.1 Subgrade Preparation for Structures & Pavement |  | Not Specified |  |  | HP |  |  | W
9 | Subgrade preparation under foundations for structures |  |  | ENG |  |  |  | Test |  | Area to be ripped to 300mm in depth, moisture conditioned and compacted to not less than 100% of the maximum dry density (standard compaction) |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 rev0 Clauses 3.9.3 Compaction Standards, 3.9.4.1 Subgrade Preparation for Structures & Pavement |  | Normal Level of Testing: 1/500m2 3/visit Reduced Level of Testing: 1/1000m2 3/visit |  |  | HP |  |  | W
10 | Subgrade preparation under roadways & earthpads |  |  | ENG |  |  |  | Test |  | Area to be ripped to 150mm in depth, moisture conditioned and compacted to not less than 98% of the maximum dry density (standard compaction). |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 Clauses 3.9.3 Compaction Standards, 3.9.4.1 Subgrade Preparation for Structures & Pavement |  | Normal Level of Testing: 1/500m2 3/visit Reduced Level of Testing: 1/1000m2 3/visit |  |  | HP |  |  | W
11 | Proof-roll subgrade surface |  |  | SV |  |  |  | Test |  | All subgrades and foundations shall be proof rolled using a 10,000L water truck loaded to 8 tonnes with dual tyres minimum pressure 600kPa driving at 3- 10km/h. Any areas that show signs of visible movement to be rejected and reworked. |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 rev0 Clause 3.9.4.1 Subgrade Preparation for Structures & Pavement |  | As required |  |  | HP |  |  | HP
12 | Surface level check/ and survey pick-up |  |  | Surv |  |  |  | Survey/ Test |  | Vertical Tolerances: General Earthworks +/-25mm Road subgrades, buildings/structures pads -25mm to +0mm Horizontal Tolerances: Road width -0mm to +250mm Grade Tolerances: Road +/-0.25% Pads +/-0.25% |  |  |  | EVAMP001-BEC- 3920-CV-SPE- 0001 rev0 Clause 3.11 Construction Tolerance |  | As required |  |  | HP |  |  | HP
3 | Post Construction
13 | Works completed and update ITP/ Lot Register/ MDR and close out of GDP |  |  | ENG |  |  |  | Visual |  | GDP permits closed. ITP closed. Approved MDR |  |  |  | - EVAMP001- BEC-3920-CV- SPE-0001 rev0 - EVA PMP |  | As required |  |  | HP |  |  | HP
☐ Conformance to Specification | [5 empty] | ☐ Requires Re-Work: (Provide Details): | [14 empty] | ☐ Non-Conformance |  |  |  | NCR No:
Approved by THIESS QA Representative | [6 empty] | Date |  |  |  | Approved by THIESS Project Manager | [6 empty] | Date |  | Approved by Client | [6 empty] | Date
Name (print): | [10 empty] | Name (print): | [8 empty] | Name (print):
Signature: | [10 empty] | Signature: | [8 empty] | Signature:
RESPONSIBILITY |  |  |  |  | METHOD | [7 empty] | VERIFICATION TYPE | [5 empty] | ITP REVISIONS
Symbol |  | Legend |  |  | Symbol |  |  |  | Legend |  |  |  | Symbol |  | Legend |  |  |  | Rev No. |  | Amendment Details |  | Date |  |  | Approver
C |  | Client |  |  | W |  |  |  | Written |  |  |  | HP |  | Hold
SV |  | THIESS Supervisor |  |  | A |  |  |  | Application |  |  |  | W |  | Witness
Eng |  | THIESS Engineer |  |  | D |  |  |  | Design |  |  |  | R |  | Review
Surv |  | Surveyor |  |  | S |  |  |  | Survey Data |  |  |  | M |  | Monitor
SC |  | Subcontractor |  |  | V |  |  |  | Visual
PM |  | Project Manager |  |  | T |  |  |  | Test
CM |  | Construction Manager |  |  | C |  |  |  | Certificate
MC |  | Material Controller |  |  | TA |  |  |  | Test / Approval
ENV |  | Enviro officer |  |  | M |  |  |  | Measure
Please transfer information into THIESS Data System ‘Inspection and Test’ Register.