## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Bath Street Stormwater Renewal |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561466 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | DR | DCC Operations Rep | TBC
Contract Number: | 9240 |  |  |  |  | C | Check | CR | Cust. Representative | Rolly Hill (Fluent)
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 1 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Ductile Iron watermain install as part of enabling works |  |  |  |  | I | Inspection | PM | Project Manager | Mike Kemp
Discipline: | Watermain |  |  |  |  | M | Monitor on Random Basis | PE | Project Engineer | Nathan Bullin
Specification: | [5 empty] | O | Operation | QE | Quality Engineer | Calisa McLeary
[6 empty] | R | Review | QM | QA Manager
Drawings: | [5 empty] | S | Subcontractor | SP | Supervisor | Brad Macaskill
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary |  | Date: | 2024-04-26 |  | W | Witness Point | SV | Surveyor | Eroni Vari
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Material Delivery | Inspect for damage and wear, Confirm items are correct as per drawings and Specifications | - DI Pipes shall be DN150 PN35 with cement mortar or concrete lining - material and fittings are approved as per contract specification | Photos,delivery docket, MDD results for backfill materials | On Delivery | Visual | C | PE/QE
3.2 | Set out | Allignment set out completed by an approved surveyor marked allignment | Set out matches drawings, 2D data and linework provided or aggreed with the Engineer | Survey marks, photos | Prior to commencement of works | Visual, Instrumental | H | SV/QE/PE/CR
3.3
3.4
3.5
3.6
3.7
3.8
3.9
3.10

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Trench Excavation | -excavate to acheive required depth to invert as per drawing C4500 - Floor of trench to be even across width and length | - Allow 100mm for bedding - Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500 | Photos | During Installation | Visual | V | SP/QE/PE
4.2 | Foundation | Scala tests on base of trench | minimum of 2 blows per 100mm | test results | During installation, per 20m | Visual, On site test | H | SP/QE
4.3 | Ductile Iron Pipe Installation | Pipes installed and positioned as per design | - Pipe not damaged during installation - Pipe is centrally located within trench - Pipe levels are within tolerance and according to the drawings | Photos, Survey of position for asbuilt | During installation | Visual | V | SP/QE
4.4 | Embedment zone | Embedment material shall be AP20 or approved by the Engineer in writing | - min 100mm bedding - 100mm overlay | Photos | During Installation | Visual | V | SP/QE
4.5 | Backfill and Compact | - Backfill material shall be AP65 - Backfill in 200mm layers of compacted material - Compaction testing one test every two layers as required - conductive signal strip to be laid at 300mm above pipe | 95% MDD in roads, paths, and pavements | Photos, Compaction test results | During Installation, compaction testing per 50m of pipeline | Visual, On Site test | H | SP/QE/PE
4.6
4.7
4.8
4.9
4.10

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Pressure Testing (non-PE pipeline) | non PE pipelines to be tested in accordance with specifications | Specification WM 4.6.1: No Thrust block failures, No visible leaks, Do not exceed make-up water limit. | Test Records | Before commisioning | On-Site Test | H | QE/CR/PE/DR
5.2 | Disinfection | Disinfection to be completed in accordance with specifications | Specification WM 4.11: | Test Records | Before commisioning | On-Site Test | H | QE/CR/PE/DR
5.3 | As-Built |  | Engineer Approval | QA records | at completion |  | H | CR/PM
5.4
5.5
5.6
5.7
5.8
5.9
5.10
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: