## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-0001 - DI Watermain | itp |  |  |  |  | ITP-0001 - DI Watermain
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
label | Acceptance Criteria - DI Pipes shall be DN150 PN35 with cement mortar or concrete lining
label | ○ Material and fittings are approved as per contract specification
label | Verifying Document - Photos, delivery docket, MDD results for backfill materials
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Allow 100mm for bedding
label | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Scala tests on base of trench
label | Acceptance Criteria - minimum of 2 blows per 100mm
label | Verifying Document - test results
label | Frequency - During installation, per 20m
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 4.3 - Ductile Iron Pipe Installation
label | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe is centrally located within trench
label | ○ Pipe levels are within tolerance and according to the drawings
label | Verifying Document - Photos, Survey of position for asbuilt
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.4 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
label | Acceptance Criteria - Min 100mm bedding
label | ○ 100mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.5 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill material shall be AP65
label | ○ Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above pipe
label | Acceptance Criteria - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pressure Testing (non-PE pipeline)
label | Inspection Point: Quality Control Activity - Non PE pipelines to be tested in accordance with specifications
label | Acceptance Criteria - Specification WM 4.6.1: No Thrust block failures, No visible leaks, Do not exceed make-up water limit.
label | Verifying Document - Test Records
label | Frequency - Before commisioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 5.2 - Disinfection
label | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
label | Acceptance Criteria - Specification WM 4.11:
label | Verifying Document - Test Records
label | Frequency - Before commisioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 5.3 - As-Built
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date:
checklist | ITP-0002 - PE Watermain | itp |  |  |  |  | ITP-0002 - PE Watermain
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
label | Acceptance Criteria - Pipes shall be DN63 PN16 PE80
label | ○ Material and fittings are approved as per contract specification
label | Verifying Document - Photos,delivery docket, MDD results for backfill materials
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Allow 100mm for bedding
label | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Scala tests on base of trench
label | Acceptance Criteria - minimum of 2 blows per 100mm
label | Verifying Document - test results
label | Frequency - During installation, per 20m
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 4.3 - Pipe Installation
label | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
label | Acceptance Criteria - Pipe not damaged during installation
label | ○ Pipe is centrally located within trench
label | ○ Pipe levels are within tolerance and according to the drawings
label | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.4 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
label | Acceptance Criteria - Min 100mm bedding
label | ○ 100mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.5 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above pipe
label | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pressure Testing (PE pipeline)
label | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
label | Acceptance Criteria - Specification WM 4.7.5: No Thrust block failures, No visible leaks, Do not exceed make-up water limit
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 5.2 - Disinfection
label | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
label | Acceptance Criteria - Specification WM 4.11:
label | Verifying Document - Test Records
label | Frequency - Before commissioning
label | Inspection Type (Visual, other) - On-Site Test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 5.3 - As-Built
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date:
checklist | ITP-0003 - Ducting | itp |  |  |  |  | ITP-0003 - Ducting
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
label | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
label | Acceptance Criteria - Items are approved as per contract specification or as agreed by the engineer
label | ○ DCC approved
label | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
label | Frequency - On Delivery
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
checkpoint | 3.2 - Set out
label | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
label | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
label | Verifying Document - Survey marks, photos
label | Frequency - Prior to commencement of works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Excavate to achieve required depth as per Drawing C4600,C4500
label | ○ Floor of trench to be even across width and length
label | Acceptance Criteria - Allow 100mm for bedding
label | ○ Allow for minimum cover of 600mm.
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.2 - Foundation
label | Inspection Point: Quality Control Activity - Scala tests on base of trench
label | Acceptance Criteria - minimum of 2 blows per 100mm
label | Verifying Document - test results
label | Frequency - During installation, per 20m
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - H
holdpoint | HOLD POINT
checkpoint | 4.3 - Install Duct
label | Inspection Point: Quality Control Activity - Ducting installed and positioned as per design
label | Acceptance Criteria - Duct not damaged during installation
label | ○ Minimum of 150mm horizontal and vertical clearence from other services or as specified on Drawings C4600, C4500
label | Verifying Document - Photos, Survey of position for asbuilt, weld records (if required)
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - V
checkpoint | 4.4 - Embedment zone
label | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
label | Acceptance Criteria - Min 100mm bedding
label | ○ 100mm overlay
label | Verifying Document - Photos
label | Frequency - During Installation
label | Inspection Type (Visual, other) - Visual, measurement check
label | Inspection: Key - V
checkpoint | 4.5 - Backfill and Compact
label | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
label | ○ Compaction testing one test every two layers as required
label | ○ Conductive signal strip to be laid at 300mm above duct
label | Acceptance Criteria - 95% MDD in roads, paths, and pavements
label | Verifying Document - Photos, Compaction test results
label | Frequency - During Installation, compaction testing per 50m of pipeline
label | Inspection Type (Visual, other) - Visual, On Site test
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As built
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
holdpoint | HOLD POINT
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date: