## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | e4f0a5e4-1222-4758-8162-94735cdd3394 |  | checklist | Lift Lobby Outside Air Supply |  |  |  |  | Yes | Lift Lobby Outside Air Supply | 03e7aebd-fa4c-4710-9a0f-4fdfd39873b8
checkpoint-group | 337acbc5-c928-494a-9f0c-9c905474bff7 |  | section | General
checkpoint-status | b7b7a04e-8d34-4480-8754-b4aa063a575b |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 4f8e1371-693e-49c1-aace-79b61b52bbbb |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | a4ee08bb-15b5-4477-8673-8eacb2a26bc2 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-group | 534aeda5-abea-4995-b635-ea1b4b5558e2 |  | section | Fire Damper
checkpoint-status | d37d3b3c-fe93-414e-ac8d-c34c6b3e1d9f |  | checkpoint | Penetration through wall is correct size and ready for installation
checkpoint-status | 32fb5000-d993-4694-98ba-b6e503e2fd3f |  | checkpoint | FD sleeve fitted to wall
checkpoint-status | 0e4d3c17-d1de-4dba-8a3a-0b9f5854dc7d |  | checkpoint | Fire Damper label filled out and located where visible from access panel
checkpoint-status | 22218ac6-44d9-44fe-8f92-cd27aeb7e03e |  | checkpoint | Access panel marked out
checkpoint-status | 997ce903-701f-498f-99c1-32db783bb637 |  | checkpoint | 8. Access panel installed by others
checkpoint-group | a0f98821-9aa9-4e1a-aa15-25fd0594af51 |  | section | Flex and Grille
checkpoint-status | 0741bcb2-6b12-4e26-ad27-0bba0adad0a6 |  | checkpoint | Flex installed and adequately supported (with Gutterguard)
checkpoint-status | 85941532-5070-47a4-b534-7cfa6be63dda |  | checkpoint | Grille installed
checkpoint-group | 8889290a-8c11-494d-8e48-79cce8cacc5d |  | section | Handover
checkpoint-status | 50575a98-0356-4687-a50b-155f701afd20 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-flat | 1fbe8be6-298b-419b-ab6b-d38a6c29679c |  | checklist | Fire Penetration |  |  |  |  | Yes | Fire Penetration | 36bd349b-a1d9-4d0e-afe8-45f13972987b
checkpoint-status | f5099020-2643-4283-8f30-7639ec44ac62 |  | checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No AO101
checklist-flat | 35e5ad92-cd26-48e7-b2e5-e98ee0a9355c |  | checklist | Site Diary |  |  |  |  | Yes | Site Diary | 4aca0381-4c41-4af9-839b-3ba5b6779ce9
checkpoint-status | 3fa9e58e-3c1f-457f-8860-3910c11c0066 |  | checkpoint | Areas of work accessible for the day
text | f74a2cfb-4f1b-5d53-8ef8-d36c31187648 |  | textbox | Number of workers on site
text | 5fb8d7c2-2c1c-50c9-a3bf-785a1e928b57 |  | textbox | HSR on site today enter name
text | b6ddf98c-1561-5604-97c2-dd5f53d5ec5c |  | textbox | First Aider on site today enter name
text | 1388511e-5f25-5f7c-9eb4-c7ee72e7a690 |  | textbox | Injury on site today enter name
checkpoint-status | 24cb2969-e2dd-46eb-9c8d-f94fd270579c |  | checkpoint | Work area - Take a photo & add a comment
checklist-sectioned | ada09071-79ac-4f32-9543-e19513739a9c |  | checklist | OAF |  |  |  |  | Yes | OAF | 4b270d80-53d4-427f-9c2b-b0b1212fa842
checkpoint-group | 7b99a482-3117-4c12-ac03-237e4a2b4ed9 |  | section | General
checkpoint-status | 87a7c841-a54b-4c2a-9344-78d85f0ad42a |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | f3b574a8-6ca2-4cd3-b453-7163b231fcb2 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 82821283-1806-4d8f-970a-4d5bfd15203f |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | d3a3cfe1-2f37-4f2f-bcfb-cc5e9cd42732 |  | checkpoint | Correct Fan Installed
checkpoint-status | 0e70a926-eb85-4439-905c-8d28a61db920 |  | checkpoint | Fan installed for correct direction of Air Flow
checkpoint-status | 2bbba2bc-4096-4304-b394-06f1a2b25394 |  | checkpoint | Anti Vibration Mounts Installed
checkpoint-group | 325f6f78-8069-47cf-874e-bf696ebd5d2c |  | section | Ductwork
checkpoint-status | 4c09a9dd-120d-4cd0-9ade-bb3d39dc9558 |  | checkpoint | Flex connection to duct work
checkpoint-status | 926518ad-18ca-4544-a902-2584ca540da0 |  | checkpoint | Duct work installed with clearance from other services
checkpoint-status | fd078305-11c8-4727-99bf-f914efb3a226 |  | checkpoint | Duct work adequately supported
checkpoint-status | ee6dc7b7-8083-450c-ba13-d56844623009 |  | checkpoint | Duct work sealed through walls
checkpoint-status | f24b2b11-0a01-49b7-be30-1bbbcadabf2c |  | checkpoint | Flex installed and adequately supported (Gutter Guard)
checkpoint-status | 0475eb22-bda7-4ca3-a2ce-bcaa0224c5bc |  | checkpoint | Provision for Access
checkpoint-status | f9c754dc-9091-469b-8364-666f2f7e37d6 |  | checkpoint | Grille installed
checkpoint-group | c678721e-ee45-4d70-a319-8f2dd999c4e9 |  | section | Electrical
checkpoint-status | a08e6d6f-25e6-4808-adae-470522dd437f |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-status | 9eaabf24-b279-4e72-b02d-85d58a7e39a4 |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-group | eb27c679-7eb3-48d6-a65c-dd26dc29a454 |  | section | Handover
checkpoint-status | c93d095b-6a17-4971-bad8-35896e2726ce |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-flat | 0710ea60-eacc-44d7-8788-ad3ce48f3f3c |  | checklist | Car Park Supply & Exhaust Grilles ITP |  |  |  |  | Yes | Car Park Supply & Exhaust Grilles ITP | 4f8908b1-b3fb-40d2-addf-5710011247e5
checkpoint-status | fc6030b5-fc2b-41d2-a5bb-654672f2246c |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | a25155f7-df22-446b-a44f-f05d18772cfb |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 8a417c55-0b12-4140-a356-3c43b98e6811 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | 753f0788-1c8d-45ec-af4e-d02aead4c758 |  | checkpoint | Correct size and number of grilles installed (with OBD)
checkpoint-status | 3626f992-b7a8-472e-b59d-64f1b5444208 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | 6c48adb0-e713-469f-8b05-d8b859877f1b |  | checklist | Roof Mounted Outside Air Fan |  |  |  |  | Yes | Roof Mounted Outside Air Fan | 5800fca9-1c5b-4514-a5e8-ff44b229d413
checkpoint-group | 9694172d-83d2-434e-92de-3232f9600e02 |  | section | General
checkpoint-status | fc8cf6c5-a4f7-40c8-854b-ef9ad3efdb9d |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 1c4cec57-62a8-4b1a-a152-939593c97737 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 60439640-7d74-4eb6-8e8e-9b95de0a60dd |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | e1400a6c-24c8-4997-9e71-4b02d4aca089 |  | checkpoint | Correct Fan Installed
checkpoint-status | 3f8b495c-cad0-4cbf-8076-695467dbed9b |  | checkpoint | Fan installed for correct direction of Air Flow
checkpoint-status | bf410077-fab8-4b37-9640-8893d85ebfe7 |  | checkpoint | Anti Vibration Mounts Installed
checkpoint-group | ab99c22c-3a4d-482f-8279-199ce02ed201 |  | section | Ductwork
checkpoint-status | 6611af59-cbc8-4e04-8743-5a045023c847 |  | checkpoint | Dropper installed in shaft and sealed to hob
checkpoint-status | 767469ed-ecd0-465e-9891-66204fa6f7ec |  | checkpoint | Fan sealed to duct with foam tape
checkpoint-status | 50771f27-247f-4313-b35a-d408fd0a9abc |  | checkpoint | Overflashing installed
checkpoint-status | 6b080d8a-0012-48cf-9a31-5829318e6d5c |  | checkpoint | Fan secured to duct with a minimum of 4 screws
checkpoint-group | 6e65d496-19a4-49b2-94fc-a59631ba7d7f |  | section | Electrical
checkpoint-status | 2f1e0e01-d431-4f75-b902-e908f78c6bfc |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-status | abfdfd43-eba5-4cde-831b-67fd3dec02c4 |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-group | 20661d5c-4293-43c6-9283-89fc2bd0360c |  | section | Handover
checkpoint-status | 2fe40137-1dc0-47c3-a101-28f5d3d3f323 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | efe78731-533a-4875-ad64-d24f60cf635e |  | checklist | High Wall Split ITP |  |  |  |  | Yes | High Wall Split ITP | 58978d5a-6640-425a-b212-0b0450383bb4
checkpoint-group | 9c452be3-290f-4097-8be5-c205f330b65f |  | section | General
checkpoint-status | 0e82abc5-7412-4974-af84-4948eeaafe73 |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | bd97c745-090d-41b4-890d-aeef06522d78 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | c6b6120c-6d7d-4bad-b55f-be2bd7916e2d |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-group | a081df53-67b0-4f82-9824-0de347f7e11e |  | section | Pipework
checkpoint-status | e4bfb2aa-b454-4ceb-aca8-4f910529411d |  | checkpoint | Pipework roughin complete
checkpoint-status | ae221565-81c1-40ab-9119-391787d062a1 |  | checkpoint | Drain roughin - Pressure Pipe - Green Glue
checkpoint-status | 1fb5f9c7-a88c-453e-8dde-8bb5c3dd1fcc |  | checkpoint | Drain Test - min 1L
checkpoint-group | 793094fe-65b7-45b1-9e87-74864b8ab517 |  | section | Fan Coil Unit
checkpoint-status | 80155509-e26b-4a7d-9b65-a40150db4b54 |  | checkpoint | Correct Fan Coil Installed
checkpoint-status | 4e779e4d-fd1b-4571-b5ef-5dcb67ff5a7a |  | checkpoint | Drain terminated to tundish
checkpoint-group | 1c7bf4e4-f331-41dd-8ec2-73fd0426d756 |  | section | Electrical
checkpoint-status | d8a707ab-660a-4c42-87a5-89526844d6af |  | checkpoint | Electrical interconnect roughed in
checkpoint-status | 567ee030-69ec-48ce-aecd-9f823ae4bf00 |  | checkpoint | Fan coil and condenser terminations complete
checkpoint-status | a3dfccef-d4e2-4fb3-95cc-eb387120ca6a |  | checkpoint | Electrical supply roughed in by others
checkpoint-status | 733c59b3-8140-44ea-b105-15233001bf76 |  | checkpoint | Isolator installed adjacent to condenser by others
checkpoint-status | fac9a22c-83aa-4821-8d64-dd9d9e12f0bc |  | checkpoint | Power available
checkpoint-group | abbae998-639a-4f17-996d-0af0ac71229a |  | section | Condenser
checkpoint-status | dbfc5063-2581-40af-96d0-c7e556aeb281 |  | checkpoint | Floor and Wall finishes complete. Tundish complete
checkpoint-status | 6cc801a7-93e7-405a-9849-02642230b656 |  | checkpoint | Correct Condenser installed
checkpoint-status | 9e8ae8f7-17f0-4fc5-9582-3536694b0447 |  | checkpoint | Condenser mounts installed
checkpoint-status | d7bee806-fd71-4322-9104-e0ce79680b2f |  | checkpoint | Drain terminated to tundish
checkpoint-status | 650bbb41-01b6-461b-b1fd-44ad4c09390c |  | checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint-status | 2f4f3846-e896-4e63-adf4-90141be91ed3 |  | checkpoint | System evacuated
checkpoint-status | 614697db-450a-4ae0-81bd-a2bb6ef09bb0 |  | checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
checkpoint-group | afe22128-3ddf-4602-9b5d-aff8eb04a82a |  | section | Handover
checkpoint-status | a7e41359-3e47-4269-8d23-108c0b814330 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | ed32ca85-0eba-44b9-a7f5-7147b23710bf |  | checklist | Ducted AC System ITP |  |  |  |  | Yes | Ducted AC System ITP | 58bb387e-00f5-4d62-b617-4634c0f66bf0
checkpoint-group | f17932a3-3f5a-493d-b950-883e57c07dfc |  | section | General
checkpoint-status | 006e0f23-9c35-466c-8e50-790f67de0f0d |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 3deb4d18-77a3-412a-8fa4-93b1d7590f71 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | dd3545e2-2773-4995-9841-6cd8e126d780 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-group | 0c8c6bf7-7e71-47c3-be04-f62d37a9c3a4 |  | section | Pipework
checkpoint-status | a633763e-22eb-4901-810f-53a55c2d3626 |  | checkpoint | Pipework roughin complete
checkpoint-status | 4dbc0048-97ec-4ca9-acdd-35c7bee541ce |  | checkpoint | Drain roughin - Pressure Pipe - Green Glue
checkpoint-status | bf1e3576-4621-4f9f-94b3-9715b5458eda |  | checkpoint | Drain Test - min 1L
checkpoint-group | 542a2ba3-5383-4814-9d3d-f36d20d9812e |  | section | Fan Coil Unit
checkpoint-status | 9617385a-485e-4b79-b51a-5fa2266564ec |  | checkpoint | Correct Fan Coil Installed
checkpoint-status | b381defa-cc4b-4824-8c91-75bc6168fbec |  | checkpoint | R/A Plenum with filters installed
checkpoint-status | d8fe29dc-afcc-4dbe-af3c-b736c6ed6ad0 |  | checkpoint | Anti Vibration mounts fitted to FCU and R/A plenum
checkpoint-status | 2b819f7c-ae66-4807-9dbb-c0c01d743f17 |  | checkpoint | Supply Air plenum installed with flex connection
checkpoint-status | 5f38842b-290f-4818-8727-6e8fb768cb09 |  | checkpoint | R/A and S/A connections lagged
checkpoint-status | 45e12457-b34e-4e84-987e-0d3a0dc150d7 |  | checkpoint | Drain roughin from FCU to tundish point - horizontal runs insulated
text | 5239a451-a61f-5583-8fde-6bd499b6d968 |  | textbox | Number of filters
checkpoint-group | 65389d9c-d5de-4894-9038-4f52f699d5ac |  | section | Ductwork
checkpoint-status | 58273c95-94ab-4854-bd95-83a85d1b5d60 |  | checkpoint | Duct work installed with clearance from other services
checkpoint-status | 352ede2a-b138-47e8-9a4d-be0b8395c36d |  | checkpoint | Duct work adequately supported
checkpoint-status | a4400d0f-4365-4618-803a-697664c43a66 |  | checkpoint | Duct work sealed through walls
checkpoint-status | aaeab3be-d99f-4fe3-b6e5-67ce33631205 |  | checkpoint | Dampers 100% open
checkpoint-status | 09aa8fc3-da34-4e30-b40f-7f824d753981 |  | checkpoint | Flex installed and adequately supported (with Gutterguard)
checkpoint-status | ab92fe42-f7d5-489c-85f6-90b2b961e42e |  | checkpoint | Access panel installed (by others)
checkpoint-status | f0ef45db-5ea9-4ddf-9d7b-b1dc5d9b152d |  | checkpoint | Grilles installed
checkpoint-group | 53946edb-b0e9-4ee1-9705-d65fff018ef5 |  | section | Electrical
checkpoint-status | 7c70ae0f-7b6e-416b-993f-0d5c02427d1d |  | checkpoint | Electrical interconnect and Outside Air Fan roughed in
checkpoint-status | c92bc2cc-9c01-4774-a1fd-6aa1d85f654a |  | checkpoint | Fan coil and condenser terminations complete
checkpoint-status | f660e990-ec6f-4c11-92e3-64e9cbacf357 |  | checkpoint | Electrical supply roughed in by others
checkpoint-status | d5421382-07b7-46e6-9839-656b716d21b9 |  | checkpoint | Isolator installed adjacent to condenser by others
checkpoint-status | 1a89f0b0-27e4-486a-b8e1-adcf613654af |  | checkpoint | Power available
checkpoint-group | 1eb19af3-f7cb-4d02-b762-d78a1310478f |  | section | Condenser
checkpoint-status | f2d6cbb2-5ced-46b3-b49d-d617b801cd4c |  | checkpoint | Floor and Wall finishes complete. Tundish complete
checkpoint-status | a65772db-0a26-4ebc-b49a-ba82bcf5d841 |  | checkpoint | Correct Condenser installed
checkpoint-status | 6f9a5e65-33df-422e-87d7-140b5730ef94 |  | checkpoint | Condenser mounts installed
checkpoint-status | 1321c459-19d7-4773-8a37-e2a2c7d4c39f |  | checkpoint | Drain terminated to tundish
checkpoint-status | eddac3fa-1f57-4d9a-bbb2-59deccea2a0a |  | checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint-status | 0c4295dc-fccd-4e06-bd4e-7eecd2f87edf |  | checkpoint | System evacuated
checkpoint-status | 2d4e044b-1e7f-43fd-999c-88014409a5bc |  | checkpoint | Additional refrigerant charge
checkpoint-status | e080f343-2ea5-4822-823f-649a5ea7b404 |  | checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
checkpoint-group | bff48819-a674-4d71-84e3-a2459ebf355d |  | section | Handover
checkpoint-status | b9dcaecb-3b86-4835-a5d8-779c51937fbd |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | e73ebca6-71b7-4291-bbd1-937dc5ed7364 |  | checklist | TEF |  |  |  |  | Yes | TEF | 5cd190c3-b4b5-433e-b439-6d71889f5d7e
checkpoint-group | 1c4b5527-23f2-4bee-9680-a30fc64dbb6f |  | section | General
checkpoint-status | a4ad8dec-1149-4c2b-97e8-16eb774ee77b |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 75e0ced0-3fd2-42de-b1cc-77f4662029c6 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | da5bfb20-3b37-4405-8858-0371a5570716 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | 85004656-520d-4840-a452-5f3daaaaf5e8 |  | checkpoint | Correct Fan Installed
checkpoint-status | 4fbe19fb-ebac-4ca3-9535-8164f77f09f6 |  | checkpoint | Fan installed for correct direction of Air Flow
checkpoint-status | 1c282559-c652-487c-a4a0-425a03aae2fa |  | checkpoint | Anti Vibration Mounts Installed
checkpoint-status | 9f79f76f-cd06-4a89-9c61-276b04d9f89d |  | checkpoint | Access Panel Marked Out
checkpoint-group | 0d26d76b-ecaa-434d-a141-2958ad4f218e |  | section | Ductwork
checkpoint-status | 4199cfdb-8d7e-46c6-8534-906f75238d8e |  | checkpoint | Flex Duct installed with clearance from other services
checkpoint-status | 43919503-88f3-4009-8b27-a029cbd844b2 |  | checkpoint | Flex duct adequately supported (Gutter Guard)
checkpoint-status | 8e902d8c-fda3-4d8e-b7b0-2e4c3b832502 |  | checkpoint | Plenum Box sealed to wall
checkpoint-status | c4b08616-3731-42b3-93c5-b5872d0a1120 |  | checkpoint | Grille installed
checkpoint-status | 5abd2e38-f1da-4dfc-97f5-0aa484dead5e |  | checkpoint | Louvre installed
checkpoint-status | ea393700-162e-4a87-9d05-ff13cd2feb2c |  | checkpoint | Access Panel installed (by others)
checkpoint-group | c4503899-8f5d-4125-909e-05ac622faef6 |  | section | Electrical
checkpoint-status | 0cfa360f-579d-45a6-8a2c-305d9318188f |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-status | ff732527-5d62-4abc-890c-0ce4346d8c87 |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-group | 79f9a755-3ed3-47f3-a5e8-985f2e7cfbe1 |  | section | Handover
checkpoint-status | 0f4ad260-be94-40fd-8ac9-4a3cee029459 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | 1adbe6fc-2471-41d9-8360-a6a61e3ca9e9 |  | checklist | Bathroom / Laundry duct and fans |  |  |  |  | Yes | Bathroom / Laundry duct and fans | 5d6b9cb2-9355-4c82-ac30-cac7f004aa98
checkpoint-group | d6c9df05-4714-4106-aec4-a4548c1fbcc1 |  | section | General
checkpoint-status | 02921daa-a9ce-4456-ae8b-ee1d4d7d9103 |  | checkpoint | PVC Duct work run is correctly located and has adequate clearance from other services
checkpoint-status | 3a9b04b0-de0a-48a9-9679-4be2190b6593 |  | checkpoint | Duct work joints are screwed and sealed with foil tape
checkpoint-status | 1d60b6f9-f14a-4030-a7d6-c1adbc16c7ef |  | checkpoint | Duct work is sealed to window head
checkpoint-status | f63852e6-a9e1-437a-995f-6e034c90ac86 |  | checkpoint | Flex duct in place to connect to header box fan
checkpoint-group | 95a815be-36c2-4883-b9fd-cede321a6051 |  | section | Electrical
checkpoint-status | b357f907-69be-492c-b4ce-02971b11dabe |  | checkpoint | 4 pin plug supplied by electrical trade for Bathroom fan
checkpoint-status | b8524ed3-ab79-40f3-af0d-2e28bf905d47 |  | checkpoint | 4 pin plug supplied by electrical trade for Laundry fan
checkpoint-group | 04e289c6-ba33-4908-b11f-cb241a769d32 |  | section | Fans
checkpoint-status | 8d48abf1-63f4-4a6d-9993-63efe2bfc4cf |  | checkpoint | Bathroom fan fitted and connected
checkpoint-status | d539248d-5223-423c-8d80-347021f65f37 |  | checkpoint | Laundry fan fitted and connected
checklist-flat | 491994df-0b2c-44a3-9220-01589347f0ec |  | checklist | Stair Pressuration Relief Dampers ITP |  |  |  |  | Yes | Stair Pressuration Relief Dampers ITP | 5fe2a721-929e-4ac5-9557-9e1b0503d009
checkpoint-status | 05ece65e-0386-4744-959c-d9538d947217 |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 9094a69f-bda2-492f-b146-cf938d3ec145 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | bdc2933e-6da6-4eb0-a033-85d59dcbaf9c |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | d9839447-84f3-4183-9409-ff2e44bdc950 |  | checkpoint | Damper Installed
checkpoint-status | e6033a81-60ad-42c3-b165-47d8352bee53 |  | checkpoint | Electrical roughin
checkpoint-status | 213e3d24-86ca-4bd0-99e7-a3b302ce8670 |  | checkpoint | Electrical fitted off for damper motor
checkpoint-status | 43486968-f439-4896-ac1d-256770d0ab0f |  | checkpoint | Damper operates automatically when fire trip operated
checkpoint-status | 0f546c48-9ba4-413a-92de-59b49da62516 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-flat | 6333345d-d3a6-48b0-be9c-6bcb221be63f |  | checklist | Stair Press/Relief Sensors ITP |  |  |  |  | Yes | Stair Press/Relief Sensors ITP | 69ba9f43-b1bb-4563-942d-490ff20839b3
checkpoint-status | 4a3b5925-3bdf-4144-9eed-d47339c3980f |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 2e32b7e4-9d92-41e3-b5d3-2d658d2c589c |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 529a7bbc-23ee-4541-be20-b6e2512093cf |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | d98c3b65-42a8-4c6d-a71b-cb3d0dedebfd |  | checkpoint | Sensor Installed
checkpoint-status | 1d035a8d-88bf-4d44-aecb-6b85cbf002e6 |  | checkpoint | Sensor set to correct unit of mesurement (pascals)
checkpoint-status | bf34994a-0f0f-402b-b7bd-f339b1a57e3e |  | checkpoint | Electrical roughed in
checkpoint-status | fd3ea81f-773c-4682-b8fc-34d47f5191dc |  | checkpoint | Electrical fit off - terminations complete
checkpoint-status | 1f4c7f1b-0029-43c0-b241-d6ba4a624b96 |  | checkpoint | Fire sealing correct and complete
checkpoint-status | 348297af-0204-4590-84bc-c59d18f45ae6 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-flat | 6fbcb006-28d0-4154-a9a0-280c41805640 |  | checklist | Stair Pressuration Grilles ITP |  |  |  |  | Yes | Stair Pressuration Grilles ITP | 6c682c17-818e-42df-b699-442406d3ac97
checkpoint-status | 9e8f09e1-1546-4544-b2cd-cb4711ca86e0 |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 9c7e81b2-d5ca-4eed-9d5c-6b4ff024f250 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 3e71da2c-9540-4c72-9a04-08dba98953b9 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | e8bb2124-f6b7-4927-878d-56b3bdba780a |  | checkpoint | Correct size grille installed (with OBD)
checkpoint-status | b9eb2677-21f0-4b98-b3a9-61472267779d |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | b401f40b-4e05-4d28-b387-3979e208b9e9 |  | checklist | Terrace House LG ITP |  |  |  |  | Yes | Terrace House LG ITP | 71ef2212-0f5b-4bcf-86cf-b1f97de22a67
checkpoint-group | 5432dbb0-ae5c-4a9c-90ee-5bfccd72bf88 |  | section | General
checkpoint-status | 5fea4081-610e-4fbd-bb02-3175b6067647 |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 955f4cc0-ef57-42d2-97e1-8eee0440bb24 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | 902d0cd3-1f62-481a-8aca-5f26dff497f1 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-group | 00e9053a-2801-4ccc-a145-85e39453c892 |  | section | Pipework
checkpoint-status | 03cde728-75b5-492f-a8cb-8b835e0de16a |  | checkpoint | Pipework roughin complete
checkpoint-status | 18b8ecda-3949-4e26-948c-86f1218b6ba7 |  | checkpoint | Drain roughin - Pressure Pipe - Green Glue
checkpoint-status | 4f04d7a6-4a86-4683-86cd-1246ff40d9a1 |  | checkpoint | Drain Test - min 1L
checkpoint-group | da4834bb-d708-41d7-8d23-e29c4a0b6217 |  | section | Fan Coil Unit
checkpoint-status | e216d62d-06d9-48aa-a5f8-be4181715319 |  | checkpoint | Correct Fan Coil Installed with Anti Vibration mounts
checkpoint-status | dfc59a50-57d9-4caa-bd7a-25c75db2a50b |  | checkpoint | Filter installed
checkpoint-status | bb683b46-0d1b-4e40-81cd-4a5c4227c011 |  | checkpoint | Drain terminated to tundish
checkpoint-group | c0baa82d-ab3c-4a4a-a825-c60ff1699753 |  | section | Electrical
checkpoint-status | 613b951f-40de-4f1b-9f10-1d2199cd11a2 |  | checkpoint | Electrical interconnect roughed in
checkpoint-status | 5ff37b44-9942-49f8-85d3-539ed9548006 |  | checkpoint | Wall Controller roughed in
checkpoint-status | 52065f43-05b9-4d82-bf5e-1e3b2143be21 |  | checkpoint | Fan coil terminations complete
checklist-flat | 204fbca8-515e-482a-ad6e-5ecde0d91912 |  | checklist | Fire Damper |  |  |  |  | Yes | Fire Damper | 9f78292a-aa3c-4957-82b8-85d7aa9e7b3b
checkpoint-status | 027d0264-b151-41ff-a026-769269013abc |  | checkpoint | Penetration through wall is correct size and ready for installation
checkpoint-status | 8177261d-1603-4046-a912-b912fdd818ab |  | checkpoint | FD sleeve fitted to wall
checkpoint-status | 50d796da-37e7-4dac-94e8-c8a6f12f4f05 |  | checkpoint | Fire Damper label filled out and located where visible from access panel
checkpoint-status | 0529f3fb-f9f9-409c-a773-2ffbd0d80284 |  | checkpoint | Access panel marked out
checkpoint-status | 288826a5-b5ad-4c7b-a907-8101e2b2bc47 |  | checkpoint | Access panel installed by others
checklist-flat | b50e3a93-6305-443f-b457-d9779d8721c3 |  | checklist | Condensor Unit |  |  |  |  | Yes | Condensor Unit | b39149cf-b879-4ca1-826f-131edca2c2d9
checkpoint-status | ae6308bf-939c-47f5-a8da-db4d708f3645 |  | checkpoint | Floor and Wall finishes complete. Tundish complete
checkpoint-status | b8d03838-23d7-4527-b689-d60d1ff0f4a9 |  | checkpoint | Correct Condenser installed
checkpoint-status | ccd4a144-c00b-4799-8fce-42ba20c9b960 |  | checkpoint | Condenser mounts installed
checkpoint-status | 2cc57a5e-f413-445f-84ff-65f43f7416d6 |  | checkpoint | Drain terminated to tundish
checkpoint-status | 635fe356-1f49-4ab3-8fa9-f9ca6ea1d337 |  | checkpoint | Electrical power supply roughed in by others
checkpoint-status | a010cc00-80f2-4e99-8216-2f73850cd5ee |  | checkpoint | Isolator installed adjacent to condenserby others
checkpoint-status | 79c27e0d-64b2-4396-a45a-e784777953db |  | checkpoint | Power Available
checkpoint-status | fe08f1ed-ab08-4a91-811d-f09f51f87882 |  | checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint-status | b981d34a-6dd3-4fc8-a1f9-fd9eb82b3f84 |  | checkpoint | System evacuated
checkpoint-status | 85b0df11-8835-4106-ab17-0580137e4a58 |  | checkpoint | Additional refrigerant charge
checkpoint-status | 2ea74463-18c6-4deb-ba54-ee5ee1855f5c |  | checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
checkpoint-status | bac30fa8-7d42-42fa-aaa9-c27c0a343de8 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | 2a39225e-4d55-4143-bdb7-66704e55106a |  | checklist | Roof Mounted Garbage Exhaust Fan |  |  |  |  | Yes | Roof Mounted Garbage Exhaust Fan | ba24353e-cba9-4910-ac07-b1dd19993b85
checkpoint-group | fb802543-d9eb-4246-a3fd-2335b35e5c02 |  | section | General
checkpoint-status | 15693613-66ac-4ac7-97bd-cebe6f9e40f1 |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 09633647-b32a-4d97-87ec-adde419a89db |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | f085e18a-7c9f-429c-a789-8e61b15d3ed1 |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | 85258cc6-1259-4826-b2a6-e3107644ff5c |  | checkpoint | Correct Fan Installed
checkpoint-group | 029bbb92-8473-4254-8f50-6c6ed1029038 |  | section | Ductwork
checkpoint-status | 05791c47-b183-42d7-81d3-a7a6618be55a |  | checkpoint | Dropper installed in shaft and sealed to hob
checkpoint-status | 9e4005f4-82f8-4b5a-8966-a5b468db8b35 |  | checkpoint | Fan sealed to duct with foam tape
checkpoint-status | f050cf97-fade-412f-9b64-87cddb7379f8 |  | checkpoint | Overflashing installed
checkpoint-status | b125cd90-e062-49c6-ab68-a89bf03d40cc |  | checkpoint | Fan secured to duct with a minimum of 4 screws
checkpoint-group | 6f73ebd1-2cc3-43b3-9789-0cc4d04ff3be |  | section | Electrical
checkpoint-status | e873d06a-3e8b-4596-9cec-7be233f05e4f |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-status | 88ae5939-d8ea-433d-ba8b-63319b09af20 |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-group | 98cfdab7-1973-45f5-9cdb-8cfd76cc8361 |  | section | Handover
checkpoint-status | e70da40b-835d-45e2-b418-0ea5a03230b1 |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-flat | 5dd80a6c-c5a2-4fca-8f8c-c279f4e77834 |  | checklist | Rangehood duct |  |  |  |  | Yes | Rangehood duct | c1413854-347a-4a43-bd25-d773adcf919b
checkpoint-status | 69687fee-12d9-421d-b4a9-7b331fb4fee1 |  | checkpoint | PVC Duct work run is correctly located and has adequate clearance from other services
checkpoint-status | eafa9b3e-9185-4499-bff7-df034a9f2035 |  | checkpoint | Duct work joints are screwed and sealed with foil tape
checkpoint-status | c8353e98-56fb-4955-8805-8efa12bd5455 |  | checkpoint | Duct work is sealed to window head
checkpoint-status | 0372c09b-30f9-4f9e-a06e-4330268b7bcc |  | checkpoint | Flex duct in place to connect to Rangehood
checklist-sectioned | a73307bd-f65a-4b6b-96ec-03e491e30de0 |  | checklist | Stair Pressuration Fan (SPF) ITP |  |  |  |  | Yes | Stair Pressuration Fan (SPF) ITP | ca0eee74-0e6e-4534-871e-4bce9e9a10e2
checkpoint-group | cf4e26ce-f9c4-4997-848d-1515a0571d89 |  | section | General
checkpoint-status | 6ebe6ebf-4634-4ced-8564-639d5027e3be |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | c16dfb31-4066-47dc-8168-f76bfae5735b |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | f1ecefb3-30e7-43b6-8b04-7f49005007ee |  | checkpoint | Location Correct As per Plan/Drawing
checkpoint-status | b96db32e-82ef-41ec-bab0-16fc935639b5 |  | checkpoint | Correct Fan Installed
checkpoint-status | dedbac52-39bd-4d6b-8109-daa3a7402142 |  | checkpoint | Fan installed for correct direction of Air Flow
checkpoint-status | 23127294-28fc-4fac-9389-81050f27559b |  | checkpoint | Anti Vibration Mounts Installed
checkpoint-group | ef0cfc4d-41e9-4c79-81af-89c87dc7481e |  | section | Ductwork
checkpoint-status | e37a7e17-eca0-4ffb-a903-ef6114bd696e |  | checkpoint | Attenuators Installed
checkpoint-status | 52459216-5496-4bcf-bf7a-655fc9075a13 |  | checkpoint | Flex connection to duct work
checkpoint-status | 65a218d1-97eb-4376-9954-acf411140c50 |  | checkpoint | Duct work installed with clearance from other services
checkpoint-status | e06ee9f7-6b18-4ec6-b823-4d1c0cd7bb29 |  | checkpoint | Flex connection has sun/weather protection and TDF joints have flange covers and are sealed
checkpoint-status | 0eeeb3f0-d149-4e6b-9999-3956ef3ff4c3 |  | checkpoint | Duct work adequately supported
checkpoint-status | 7d808533-ad52-4b79-bd56-fed6a943741a |  | checkpoint | Duct work sealed to plenum
checkpoint-status | 02a0d79b-35c7-4b56-ae3f-031134340d99 |  | checkpoint | Provision for Access
checkpoint-group | 7ca0928c-fd56-42dd-a976-d3bcb9ee7702 |  | section | Electrical
checkpoint-status | 92dd7c2b-87f6-4ee1-bc06-6e02c1b2670a |  | checkpoint | VSD installed
checkpoint-status | 4f623820-9673-43ac-92c0-6cda96e61f38 |  | checkpoint | VSD programmed
checkpoint-status | 19dbaf1b-e60d-41a7-8db6-ce7e35dfe032 |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-status | 3dceb102-89f0-4f53-84dd-b92640991b2c |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-status | 7134da97-fdd0-490b-8422-6c4dd653121f |  | checkpoint | Lock Fitted to Isolator
checkpoint-group | 5847f3f7-207b-4eaf-a7bb-04154e647702 |  | section | Handover
checkpoint-status | 0a5bfd24-fd02-40a9-ae50-b43b67db2c7b |  | checkpoint | Handover - Work completed as per specification, checked and accepted
checklist-sectioned | d822eb49-5a12-4c73-b785-7505f1194ca8 |  | checklist | Car Park Supply/Exhaust Fan ITP |  |  |  |  | Yes | Car Park Supply/Exhaust Fan ITP | e2ff799f-952e-4dab-a47f-487986b4ba62
checkpoint-group | 23d4aeff-8f3c-48af-a220-f1f304691c39 |  | section | General
checkpoint-status | 31bd3680-da18-4c62-96b2-0da3ff8e3eaa |  | checkpoint | Area ready and accessible for work - take picture if required
checkpoint-status | 99496a59-a10e-4278-965a-0375e407fd37 |  | checkpoint | Inspect - Materials free from Damage
checkpoint-status | dfeb379f-7819-4c5b-9f48-33a0a1f8cc5a |  | checkpoint | Location Correct As per Plan/Drawing (Take photo)
checkpoint-status | e96e42cb-951c-48d7-89d7-342e2d5e1edf |  | checkpoint | Correct Fan Installed
checkpoint-status | 76fbab3a-66b7-4ffd-85ef-6be5d3f1b805 |  | checkpoint | Fan installed for correct direction of Air Flow
checkpoint-status | 9f99bf2b-6ba4-4714-b47e-ca7a79f8d241 |  | checkpoint | Anti Vibration Mounts Installed
checkpoint-group | 59aea593-a0cd-434e-85b6-b5a75d10ec03 |  | section | Ductwork
checkpoint-status | f29dac7c-11c4-44d2-b3e4-e9fa37e4c467 |  | checkpoint | Attenuators Installed
checkpoint-status | a2037ea0-4107-47f1-86fa-0735bc06745d |  | checkpoint | Flex connection to duct work
checkpoint-status | 6b89d2dd-6fdf-4064-954b-2d81440b3bd9 |  | checkpoint | Duct work installed with clearance from other services
checkpoint-status | 5158c68e-48b9-46dc-8915-f5e7810e73d3 |  | checkpoint | Duct work adequately supported
checkpoint-status | 28323640-f697-4722-9dcf-8e38c8f55bdc |  | checkpoint | Duct work sealed to plenum
checkpoint-status | e19d82c5-9562-474a-b93a-4a0af6817783 |  | checkpoint | Provision for Access
checkpoint-group | da42cde1-b0c0-4cb9-b895-258bd0900d3d |  | section | Electrical
checkpoint-status | ced39c0e-7922-46a6-91af-4576e8b6a252 |  | checkpoint | VSD installed
checkpoint-status | a42cb84d-07e1-423c-9360-725f6fb44937 |  | checkpoint | VSD programmed
checkpoint-status | 2f25a81f-2fb9-4924-b6d6-e8e7ff376929 |  | checkpoint | Electrical terminations - all terminations complete
checkpoint-status | 9bbff5a3-9207-4f56-9b03-8debf9a19fe4 |  | checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint-group | fa0c6980-8cae-4524-b4e9-a940907d9285 |  | section | Handover
checkpoint-status | 8c2efe7f-5dde-4bc5-a3de-d23b721042f9 |  | checkpoint | Handover - Work completed as per specification, checked and accepted