## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
| FD Photos | Level | FD# | FD Installation Photos Checklist | FD Installation Checklist
|  | Level B | MFSD-B-1
MFSD-B-2
MFSD-B-3
MFSD-B-4
MFSD-B-5
MFSD-B-7
MFSD-B-8
MFSD-B-9
MFSD-B-10

## Checklists
type | name | values
checklist-flat | FD Installation Checklist
checkpoint | FD Dimensions
Drawing #
label | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | Max Penetration = (W+F) x (H+F)
label | F= Side of the angle against Fire Wall (mm)
label | AS.1682.2:2015
text | FD Size (W X H):
text | Flange Size (F):
text | Minimum Peno Size (W X H):
text | Maximum Peno Size (W X H):
text | Current Peno Size (W x H)
checkpoint | FD fully open; blades free to close and latch
checkpoint | FD orientation and air flow direction is correct
checkpoint | FD wholly within wall/ Slab; case is square
checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint | Packing/expansion metal installed around casing
checkpoint | Opening in fire rated structure is correct
checkpoint | FD Flanges attached correctly
checkpoint | FD # corresponds to the one detailed on drawing
checkpoint | FD location corresponds to the one detailed on drawing
checkpoint | FD accessible for maintenance and service purposes
checkpoint | FD Installer Label complete
checkpoint | Fusible Link Fitted
checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint | Installation is approved
checkpoint | Corrective actions have been undertaken
checklist-flat | FD Installation Photos Checklist
checkpoint | Penetration Width
checkpoint | Penetration Height
checkpoint | Left and/or Rigth Gap
checkpoint | Top and/or Bottom Gap
checkpoint | FD c/w Retention Angles
checkpoint | FD Open
checkpoint | FD Close
checkpoint | FD Break Away Joint
checkpoint | FD with AP
checkpoint | Gaps Around FD Sealed
checkpoint | Sticker