## page 1
ITP - BONDING
Project Name : HOMAI
Project No. 43032
Project Document No. & Revision: DNR-43032-NIMT-ITP-001
Line: |  |  | North Island Main Trunk (NIMT) |  |  |  | Location/Area |  | HOMAI STATION
Wire Run Numbers |  |  | N/A
No. | Inspection & Test Activity |  |  | Application Std. & Acceptance Criteria* |  | Timing or |  | Records & Remarks |  | Comments
[6 empty] | Frequency** |  | Downer | Alpha Rail
1 | OH &S
1.1 | The following document is to be submitted for review/approval: Safe Work Method Statement (SWMS) |  |  | AS/NZS ISO 480-1-2001 & |  | Prior to |  | R | R
project OH&S Management Plan commencement
of work
2 | ENVIRONMENTAL
2.1 | Environmental: Environmental Control Plan |  |  | AS/NZS ISO 14001-2000. |  | Continuous |  | R | R
ProjectEnvironmental Management
Plan & Associated Sub-Plans.
3 | MATERIAL RECEIPT
3.1 | All major product items delivered to site shall be : Inspected on receipt then stored in designated area(s) |  |  | Construction Management Plan. |  | On receipt & |  | R | W
Continuous
4 | BONDING INSTALLATION
4.1 | Balustrade Guard Conductor to PET Equpotential Earth Bar 35 mm2 Cu cable bonds |  |  | IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts |  | PET Cabinet |  | R | X
Bonds
4.2 | Girder to Girder Bonds 50 mm2 Cu cable bonds |  |  | IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts |  | Girder Bonds |  | R | X
4.3 | Balustrade Guard Conductor to Balustrade Guard Conductor Bond 35 mm2 Cu cable bonds |  |  | IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts |  | Ballustrades |  | R | X
Guard Conductor
Bonds
4.4 | Connections & Terminations |  |  | AKL Basic Design Drawings |  | At Procurement |  | R | X
5 | BONDING CONTINUITY TESTS
5.1 | Ensure correct Contnuity tester is used. DLRO (Digital Low Resistance Ohmmeter). |  |  | E-SP-AE-61318 AEA Earthing and Bonding |  | Prior to test |  | R | R
E-ST-AE-0101 AEA Earthing and Bonding Design Standards
5.2 | Ensure testing equipment is calibrated for use with photo evidence. |  |  | E-SP-AE-61318 AEA Earthing and Bonding |  | Prior to test |  | R | R
E-ST-AE-0101 AEA Earthing and Bonding Design Standards
5.3 | Tests shall be conduted at 10 amps and readings should be less than 0.5 ohms. |  |  | ≤ 0.5 ohms |  | After Bonding |  | R | R
AS/NZS 3000:2007
5.4 | Record Test results on ITR Bonding testing sheet. |  |  | DNR-43032-NIMT-CHK-001-Rev0 - |  | After Bonding |  | R | R | Test Failed.
|  |  |  | Homai Bonding Check Sheet | [5 empty] | Need to
retest once
mortar has
cured
6 | Insulation Resistance Tests
6.1 | Insulation Resistance test between bridge screen and concrete barrier at 1000V DC to provied result greater than 1M ohm. |  |  | BECA-4323-10-HOMAI-RPT-001 |  | After Installation |  | W | R
6.2 | Ensure testing equipment is calibrated for use with photo evidence. |  |  | E-SP-AE-61318 AEA Earthing and Bonding |  | Prior to test |  | W | R
E-ST-AE-0101 AEA Earthing and Bonding Design Standards
6.3 | Record Test results on ITR Bonding testing sheet. |  |  | KR-43029-NAL-ITR-005-Rev0 - |  | After Bonding |  | R | R
OLE Bonding Test Sheet
KR-43029-NAL-ITR-028-Rev0 -
OLE Bonding Check Sheet
6.4 | Record Test results on ITR Bonding testing sheet. |  |  | DNR-43032-NIMT-CHK-002-Rev0 - |  | After Bonding |  | R | R
Homai IR Check Sheet
7 | AS CONSTRUCTED RECORDS
7.1 | Relevant RFI(s). |  |  | All RFIs closed |  |  |  | R | H
7.2 | Snags |  |  | Snags to be rectified/addressed with evidence to be sent to engineer for confirmation to allow for close out
7.3 | Record on Bonding Plans. |  |  | IFC Bonding Plans |  | After Installation |  | W | W
7.4 | COC issued no more than 20 days after works are completed. |  |  | AS/NZS 3000:2007 |  | After Installation |  | H | H
7.5 | ROI Issued no more than 20 working days after works completed. |  |  | AS/NZS 3000:2007 |  | After Installation
7.6 | EAC part 1&2 signed 20 working days after works completed. |  |  | E-ST-AL-0183-FO EAC Certificate |  | After Installation
Type: H - Hold Point: W - Witness Point: R - Review/Accept: X - Self-Inspection Note: * - Unless otherwise specified, every item, batch or section shall be checked. Note ** - Applicable Standard & Acceptance Criteria always includes the relevant approved drawing, client specifications, checklists and manufacturers instructions which must be complied with.
Prepared by: |  | Alan Twine |  | Approved by: |  | Tab Kilisimasi |  |  | Distributed | Danny Cox
Works completed satisfactorily in accordance with relevant Sandards & Specifications as indicated above
Signed on behalf of Installer : Alpha Rail
Name: |  | Alan Twine
Position: |  | Project Engineer
Sign: |  |  |  | Date: | 25/01/2025